06/14/2023 | Alternative | Routine/Scheduled | 093-07-0102 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | Dec 30 1899 4:31PM
10/05/2023 | Alternative | Initial Visit |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 RT |  |  | Pressure | Drip | Not Applicable |  | [] | [] | [18 empty] | Start up | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 12:00 AM
01/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/09/2023 |  | Routine/Scheduled | 19-142-0045 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Trash Tank - normal level Aeration tank - normal level - mixing present - aspirator serviced. Clarifier - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | Jan 1 1900 1:00PM
02/20/2023 |  | RoutineScheduled | 099-17-0072 SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for routine inspection. System was in high level due to panel losing settings reprogrammed panel. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
04/20/2023 |  | Reportable Incident |  | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | [18 empty] | COSS - Maintenance - GMP2018-02 Replaced structurally damaged plastic DBox with new concrete DBox - Spliced to existing conveyance line Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/24/2023 | 06:45 AM
06/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/13/2023 |  | Routine/Scheduled | 133 05 1208 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 10:00 AM
05/19/2023 |  | RoutineScheduled | 177-14-0056-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Bad enabler float in discharge pump tank, replaced. Recirc tank needs pump out due to solids. Spongy areas in drip field need to be investigated, Drip rate little higher than last year might be bad emitters (customer said they only show after rain). Will send proposal for pumping recirc tank and to investigate spongy areas. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
10/03/2023 | Alternative | RoutineScheduled | 07-142-0065 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Recirculation Pump","Distribution Pump Operation"] | ["Attached Growth Medium","Distribution Pump Operation","Recirculation Pump","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/26/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NO | [17 empty] | Disc filter cleaned, drip field flushed. System appears to be operating normally. Risers were sealed/replaced in April. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/26/2023 | Dec 30 1899 11:58AM
04/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/09/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Audible alarm not working and panel has alot of corrosion and should be replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/18/2023 | 04:10 AM
04/13/2023 |  | Pump-Out Only | 02-0381A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex | [8 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | Jan 1 1900 11:43AM
10/16/2023 | Alternative | RoutineScheduled Component Maintenance | 061-19-056 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Bio Barrier | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Level Sensor Operation"] | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
07/10/2023 | Alternative | RoutineScheduled Component Maintenance | 061-16-250 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | Musty | Clear | 7.980000 |  |  |  |  | 07/10/2023 | Pump Chamber | 10.000000 |  |  | 7.000000 | 43.100000 |  | Will be sent separately | Inspected | Bi-weekly inspection and routine effluent sampling. BOD and TSS sample results were excellent. Nitrogen reduction level not hit due to low influent BOD. Soil may be reducing it further, but no easy way to measure in the field. D.O. in the drip pump tank measured .20 mg/L at 22.9 * C. Odor was faintly musty. Nothing visible for settleable solids field test. In the past 19 days, the system pumped an average of 1,120.8 gals/day at 425.9 gals/dose (avg.) for a total of 21,297 gallons. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:19 PM
04/14/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | Orenco Advantex | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/05/2023 | Alternative |  | 150-16-0117 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | 12:00 AM
10/19/2023 | Alternative | RoutineScheduled | 121-STS-12748 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [8 empty] | 10/19/2023 | [7 empty] | Attached to this report |  | - upon arrival alarm system was on silent, adjusted air line and alarm sounded - everything appears functional at this time, more work may be needed if problems occur | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | 12:00 AM
07/26/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 12:00 AM
03/09/2023 |  | RoutineScheduled | 101-12-0027 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
04/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/15/2023 | Alternative | RoutineScheduled Component Maintenance | 099-08-0068-ST | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. A lot of hard grease is accumulating, system will need pump out next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0467-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | Worm casings are starting to cause bridging on the Advantex sheets. We recommend scraping the sheets & pumping the tank afterwards. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
04/10/2023 |  | Routine/Scheduled |  | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. BioFilter - peatmoss in fair condition - raked/ turned. Pump Basin - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/11/2023 | 06:30 AM
01/19/2023 |  | RoutineScheduled | 179-13-0285-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Please cut back the bushes around the Advantex unit by at least 24" & maintain them, so the system remains accessible for our technicians. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
04/25/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1875 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance | 193-STS-92916 | Westmoreland | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Three Rivers | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Disinfection" ,"Recirculation Pump" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Disinfection" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | A drain has been installed to move effluent that was in the dispersal area out of the drip field. Nonetheless, water with an oily sheen is surfacing at the end of the drain pipe. We recommend contacting the AOSE for further corrective action. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/03/2023 | 05:43 AM
04/17/2023 |  | Routine/Scheduled | 550-STS-6875 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | Jan 1 1900 11:05AM
01/27/2023 |  | RoutineScheduled | SWP-03-775 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for rountine inspection. Pump tank needs to be pumped out due to sludge levels. Timer settings in panel were set to 2 min off and 45 min on allowing to much waste water to pumped to the drainfield. Padsite is struggling but not failing at this point. readjusted timer settings to proper dose of 26 gallons. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
08/01/2023 | Alternative | Reportable Incident |  | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Blue Ridge | James Lee Miller III | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable | 150.000000 | ["Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Control Operation","Distribution Pump Operation","Effluent Screens"] | YES | [17 empty] | Two floats were replaced for the discharge pump system. An internal splice box was installed for making power connections to the floats and discharge pump. The union, shut off valve, and check valve were replaced on the forcemain in the pump chamber | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/30/2023 | 07:58 AM
04/17/2023 | Alternative | RoutineScheduled | 061-16-250 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. In the past 19 days, the system pumped an average of 1,120.2 gals/day at 409.3 gals/cycle (avg) for a total of 21,285 gallons. Effluent clarity looking better. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
07/31/2023 | Alternative |  | 08-192-128 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/31/2023 |  | 10.800000 |  |  | 11.400000 |  |  | Will be sent separately |  | BOD: 10.8 TSS: 11.4 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/31/2023 | 12:00 AM
09/25/2023 | Alternative | Reportable Incident Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced (2) 3" Brass check valves. Replaced (2) blue and (1) yellow control floats. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/16/2023 | Dec 30 1899 12:58PM
04/29/2023 |  | RoutineScheduled | 101-18-0314 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/04/2023 | 12:00 AM
03/27/2023 |  | RoutineScheduled | 08-184-5006 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Disinfection","BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation","Disinfection","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/27/2023 | 12:00 AM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
04/05/2023 |  | RoutineScheduled | SWP-02-230 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. RECIRC: HL 5, LL 23, OVERRIDE 2408. DISCHARGE: HL 12, OVERRIDE 11. Sheets were very dirty on the fence side, was hard to clean them. removed a couple sheets to check bottom of unit and to check length of sheets, sheets starting to stretch causing unit to accumulate sludge on fence side. Cleaned sheets and flush unit good, sheets might need cutting or replacing next year with new style sheets also recommend installing Gast struts then. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
11/06/2023 | Alternative | Routine/Scheduled | 151-15-0035 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3000 | EcoPod |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 75.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | 01:35 PM
08/23/2023 | Alternative | RoutineScheduled | 115-07-0522 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 12000 | Dual Biomicrobics Fast 2.5 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Level Sensor Operation","Control Operation","Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Effluent Screens","Level Sensor Operation","Control Operation","Auxiliary Filter","BlowerCompressorAerator Operation"] | YES |  |  | 7.300000 | 7.500000 | [12 empty] | Inspected | Septic Tank #1 Sludge levels- 1-2" scum and 12-20" sludge trace, septic tank #2 minimal scum and 12" sludge - Fast treatment unit has good Aeration Fast #1 8-12" sludge trace and Fast #2 6"-7" sludge trace. The system tanks were pumped 12 months ago. Cleaned blower airfilters, Good Aeration observed from both Blowers, cleaned all the probes. Took Ph and Do Readings. Cleaned both Effluent screens. -TSS#1 800 #2 600 - Effluent meter reading 6906203 vs 6814689 vs 6672663 98 days 91,514 galloin or about 933 gallons per days. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | 09:30 AM
09/21/2023 | Alternative | RoutineScheduled | 14-120-0182A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 2250 | 1250 | 1000 | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | YES | Sulphitic | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/21/2023 | 12:00 AM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
04/06/2023 | Alternative | RoutineScheduled | 104-07-0142 | Amherst | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 500 | Best 1 |  | Gravity | Gravity | Trenches | Not Applicable | 300.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Auxiliary Filter"] | [18 empty] | Client was informed septic tank needed pumping. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/23/2023 | 01:00 PM
03/14/2023 |  | Routine/Scheduled | 234-16-361 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | Jan 1 1900 4:30PM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/14/2023 | Alternative | RoutineScheduled | 121-STS-13308 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | 1.000000 | 1000 | Microfast | [6 empty] | [] | [] | NA | [16 empty] | Inspected | - recommend pretreatment unit/tank be pumped cleaned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | 12:00 AM
10/09/2023 | Alternative | RoutineScheduled | 177-STS-88914 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/08/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/31/2023 | Jan 1 1900 12:26PM
04/27/2023 |  | Reportable Incident |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesapeake | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Clearstream |  | Pump | Gravity | Pad | UV | 600.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | AOSS - Install - Repair - VDH Permit 234-22-061 Pumped existing septic tank empty for storage. Installed Clearstream DAC treatment unit. Installed 1000g concrete pump tank. Installed UV system in pump tank inlet. installed gravel pad/bed as permitted. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | Jan 1 1900 6:45AM
04/25/2023 |  | Reportable Incident |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | [18 empty] | COSS - Maintenance - GMP2018-02 Replaced failing DBox with new 8 port concrete DBox. Spliced to existing conveyance line. Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | 12:45 PM
05/15/2023 | Alternative | Routine/Scheduled | 147-03-0091 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced - bridging noted. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | Dec 30 1899 6:45AM
12/19/2023 | Alternative | RoutineScheduled | 10-120-0254AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 2.000000 | 2250 | Clearstream |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Attached Growth Medium"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Attached Growth Medium"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/29/2023 | 12:00 AM
08/21/2023 | Alternative | RoutineScheduled Component Maintenance | 175-04-0912 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 09/15/2023 | 02:41 PM
05/09/2023 | Alternative | Pump-Out Only | 18-160-0106 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000 | [7 empty] | [] | [] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
12/22/2023 | Alternative | RoutineScheduled | 109-08-0297 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Quanics |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | Returned to repair leaking pipe inside the treatment tank. Found the pipe was broken due to settling and dug up end of tank to replace the PVC and many fitting to get into the tank. New pressure gauge added and valve replaced as well. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/28/2023 | 09:30 AM
07/06/2023 | Alternative | RoutineScheduled | 108-05-0010 | Bath | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 1.000000 | 750 | Delta Environmental Products, DF |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | NA | [17 empty] | Filter checked and cleaned. GFI receptacle replaced. New blower installed. Control panels functioning properly. No apparent leaks in system or drain field area. Pump functioning properly. Lids properly secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/15/2023 | 09:45 AM
03/23/2023 | Alternative | RoutineScheduled | 151-07-0013 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Ecoflo |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/05/2023 | 12:00 AM
02/20/2023 |  | Initial Visit | 182-08-0300 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Auxiliary Filter","SludgeScum Accumulation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Auxiliary Filter","SludgeScum Accumulation","Dispersal System Operation"] | [18 empty] | replaced blower and cleared blockage in air pipe | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/16/2023 | 12:00 AM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
09/27/2023 | Alternative | RoutineScheduled Component Maintenance | 175-12-0287 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
10/03/2023 | Alternative | RoutineScheduled | 154-06-0687 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 12:00 AM
12/11/2023 | Alternative | RoutineScheduled Component Maintenance | 182-11-0070 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
01/23/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/16/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | 2 AIR RELEASE VALVES ARE BROKEN AND 7 BUCKETS AND LIDS ARE ALSO BROKEN | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
12/15/2023 | Alternative | RoutineScheduled | 127-STS-32908 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/25/2023 | Alternative | RoutineScheduled | 15-13-0160 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 100 |  |  | Pump |  |  |  |  | ["None"] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | 12:00 AM
11/08/2023 | Alternative | RoutineScheduled Component Maintenance | 107-03-0340 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 11/08/2023 |  | 2.000000 | [5 empty] | Will be sent separately | Inspected | Blower squeal may be a issue soon please make sure it is running constant. If you want this replaced in the meantime let us know | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
12/20/2023 | Alternative | Routine/Scheduled | 08-120-0493A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component Normal level Heavy sludge and solids Recommend pumping No signs of infiltration Discharge/Pump Tank Condition of above Component Notes for above Component Normal level 7 in of suspended solids All plumbing intact and pump moving water properly No signs of infiltration Aeration Condition of above Component Notes for above Component Normal level 4 in of suspended solids No signs of infiltration Air Pump/Blower Condition of above Component Notes for above Component 120 volts coming in Air Pressure sensor intact and functional Concrete Dog box is cracking and deteriorated Control Panel Condition of above Component Notes for above Component 120 volts coming in All visual and audible alarms functional Pump pulled 9.9 amps All components working as should Distribution Box Condition of above Component Notes for above Component Normal level 6 lines all intact and taking water properly Drain Field Condition of above Component Notes for above Component No signs of surfacing Repairs 12/27: -Installation of 6 speed balances in the distribution box | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | Dec 30 1899 8:34AM
12/04/2023 | Alternative | RoutineScheduled Component Maintenance | SP-05-517 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"SludgeScum Accumulation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Pumping of the septic/ATU tank is scheduled for Wednesday, December 20. Please advise the gate that Marshall?s Septic Tank Cleaning Service will be coming to your house that morning. As noted on last year?s report, roots are growing in at the base of the risers on both tanks. Please let us know if you get alarms during periods of heavy rain, | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
11/24/2023 | Alternative | Routine/Scheduled | -STS-43152 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/24/2023 | Dec 30 1899 4:00PM
11/06/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.140000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | 11:00 PM
09/27/2023 | Alternative | RoutineScheduled Component Maintenance | 099-12-0061-SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
09/27/2023 | Alternative |  | -STS-90528 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
09/13/2023 | Alternative | Routine/Scheduled | 149-05-131 | King & Queen | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [16 empty] | Pumped Out | Annual Maintenance: -Septic Tank 1: Normal level Heavy sludge and solids Cast iron sewer line -Septic Tank 2: Normal level 18 in of sludge less than 1 in of solids No riser on inlet side Pulled and cleaned filter on outlet side Riser on outlet has roots running through -Discharge/Pump Tank: Normal level 3 in of suspended solids Pulled and tested floats all functioning properly Riser has roots running through it -Peat Moss: Tipping bucket and dispersal trays are intact Peat moss completely saturated and broken down -Control Panel: 120 volts coming in Visual alarm is functioning but audible alarm is not Discharge pump pulled 7 amps The top portion of the panel is completely broken and smashed Alarm light is hanging out from the top 9/15 Pump out: -Trk 605 Arrived home and septic tank 6 inches deep one hose from the truck. Pumped 1000 gallons heavy solid heavy sludge. Cleared blockage in line had tenant flush toilets, clear water came out Jerry (owner) stopped by I had the tenant flush again so he could see water coming from both toilets. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | 03:41 PM
06/29/2023 | Alternative | Follow-Up | 550-STS-6912 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Installed a new Norweco UV unit. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/29/2023 | Dec 30 1899 12:00PM
03/08/2023 | Alternative |  | 101-18-0533 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Bucky | Black | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/14/2023 | Alternative | Routine/Scheduled | 150-14-0009 | King William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/14/2023 | 03:30 PM
12/26/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Puraflo |  |  | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles"] | ["Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
05/19/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced D80 compressor. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/15/2023 | Dec 30 1899 12:05PM
09/16/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 500 | Orenco Advantex AX20RT |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 14" of accumulated solids in septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. Cleared roots from treatment unit. Flushed treatment unit spray manifold. 1" of solids in recirculation portion of treatment unit. 10" of solids in discharge portion of treatment unit. Tested floats, pump and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/22/2023 | 07:03 PM
01/06/2023 |  | Routine/Scheduled | 234-16-360 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | Replaced UV Bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/06/2023 | Jan 1 1900 8:10AM
04/18/2023 | Alternative | Follow-Up | SHUN-BCZQQ8 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [20 empty] | 2.000000 |  | 1.000000 | [5 empty] | Took BOD and Fecal labs. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/18/2023 | Dec 30 1899 12:00PM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance | 139-05-0296 | Greene | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 10/31/2023 |  | 22.000000 | [5 empty] | Will be sent separately | Inspected | Replaced blower and blower panel Replaced tank lid | This AOSS should now return to normal function after having provided the above state routine maintenance | 12/06/2023 | 03:05 PM
08/15/2023 | Alternative | Routine/Scheduled |  | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | 06:45 AM
04/06/2023 |  | RoutineScheduled | 179-18-0012-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | New spin nozzle was installed in the Advantex module during this inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
03/24/2023 |  |  | 2014-143-0053 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
01/10/2023 |  |  |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/09/2023 | Alternative | Routine/Scheduled | 154-18-0007 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1060 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [17 empty] | Effluent filter cleaned. Manifold flushed. System appears to be operating normally. The nitrogen return line is apparently broken just outside the riser and is leaking into the tank at the tank riser connection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/09/2023 | 11:39 AM
09/26/2023 | Alternative | RoutineScheduled | 107-14-0130 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
07/07/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1200 |  |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Distribution Pump Operation","Attached Growth Medium"] | ["None"] | NO | [16 empty] | Pumped Out | System needs new peat moss in 3 pods/ also needs 1 new Pump and 1 check valve | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/09/2023 | Dec 30 1899 10:10AM
03/13/2023 |  | RoutineScheduled | 179-12-0098-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | None | Clear | [5 empty] | 03/13/2023 | Sample Chamber | [6 empty] | Will be sent separately | Inspected | Annual inspection. Effluent level was down close to the pump intake due to extra pump cycles from the timer float failed on - replaced the float switch. Since effluent level was so low, the pump was only run briefly to measure amp draw. In addition, the 5-yr BOD sample had to be collected from the splitter d-box. Added a lage dose of Root-Ex while the lid was open. Effluent had a blue-green tint to it. Advised occupants to back off on the toilet bowl sanitizer. Distribution panels in the peat tank were knocked completely out of position due to a high level condition. This caused almost all of the effluent to go to one side and pond to about 2" deep. Peat looked a little better after raking but still would only be considered to be in okay condition, not good. Peat is over 10 years old and is recommended to be replaced before it fails completely. Plugged alarm horn back in. Recommend removing a couple of fallen trees that are either on or close to the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
01/26/2023 |  | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Multiflo FTB |  | Gravity | Gravity | Trenches |  | 750.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | 09:18 AM
02/06/2023 |  |  | 177-STS-87521 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
10/04/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-19461 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | Septic | Black | 5.500000 | 1.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/05/2023 | 12:00 AM
04/18/2023 | Alternative | Initial Visit | 097-STS-96191 | King & Queen | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Advanced Septic |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | SludgeScum Accumulation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Visit. Primary septic tank - recommend pumpout. Anua PuraSYS SBR - sludge return operating, mixing present - compressor serviced. Discharge pump - float sensors, pump and controls operating. DBox - Plastic - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/19/2023 | 09:30 AM
01/16/2023 |  | Routine/Scheduled | 228-13-0202 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | Jan 1 1900 9:20AM
01/24/2023 |  | RoutineScheduled | 96-120-474A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | [9 empty] | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Level Sensor Operation","Distribution Pump Operation"] |  | Septic | Black | 5.000000 |  | 4.000000 | [13 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/24/2023 | Jan 1 1900 11:30AM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | Best 1 | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was turned off and the blower connection to the air line had separated. It was connected and should return to proper function | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/19/2023 | Alternative | RoutineScheduled | 107-03-0548 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.400000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 09:30 AM
03/17/2023 |  | Routine/Scheduled | 234-18-156 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/17/2023 | Jan 1 1900 12:05PM
08/15/2023 | Alternative | Routine/Scheduled |  | Gloucester | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Biofilter - Peatmoss spent - heavy ponding. Pump Basin - float sensors, pump and controls operating. DBox - plastic intact. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/21/2023 | 06:30 AM
08/29/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-12"sludge 0"scum ( A lot of wipes/ informed owner) / Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Controls, pumps, floats and alarms are functioning properly/ Puraflo Peat was turned in all 6 modules and is in good condition at this time/ Counts: Pump1-021288 ETM-0023380/ Pump2-021228 ETM-0023878/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/15/2023 | Alternative | Routine/Scheduled | 2001-143-0383 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out. -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Recirculation pump has exceeded life expectancy. Recirculation pump plumbing has exceeded life expectancy. Recirculation floats have exceeded life expectancy. -RSV: Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. Discharge pump has exceeded life expectancy. Discharge pump plumbing has exceeded life expectancy. Discharge floats are not properly secured and have exceeded life expectancy. -Media Sheets: Cleaned media. Flushed and cleaned laterals. Flushed media module. Media has exceeded life expectancy. Media lid safety support struts have failed -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Control panel has exceeded life expectancy. -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 02:18 PM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance | 177-11-0124-SP | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001053 | Ed | Scott | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | UV |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Both the blower and the Salcor UV light are not working. We recommend installing a new blower and replacing the Salcor UV unit with a Norweco disinfection system since Salcor is no longer in business. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/03/2023 | 05:43 AM
04/20/2023 |  | Follow-Up | 234-16-209 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Meet with the pumping company and pumped out the septic tank and Clearstream tank. Installed a new UV unit (Norweco). Disconnected the pressure switch on the aerator and the UV power wire due to the pumping of the tanks. Raised the aerator off the ground. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/20/2023 | Jan 1 1900 12:00PM
09/25/2023 | Alternative | RoutineScheduled | 151-10-0133 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/04/2023 | Alternative | RoutineScheduled Component Maintenance | 175-18-0067 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | UV |  | ["Disinfection" ,"SludgeScum Accumulation"] | ["Disinfection"] | NA | Musty | Clear | 7.200000 | 22.600000 | [11 empty] | Will be sent separately | Inspected | Microfast needs pumping. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 12/18/2023 | 08:36 AM
03/14/2023 |  | Routine/Scheduled | 08-172-0028A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | EcoPod |  | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [17 empty] | Replaced spin filter, flushed drip field, and reset pressure. The system appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | Jan 1 1900 7:24AM
02/28/2023 |  | RoutineScheduled | 11-152-100 | Lee | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Pump | Pressure | Drip | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens","Dispersal System Operation","Control Operation","Auxiliary Filter","Recirculation Pump","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/28/2023 | 12:00 AM
02/10/2023 |  | RoutineScheduled | SWT 96-580 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Hoot | none | Pump | Gravity | Drip | Not Applicable |  | ["Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation"] | ["Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
03/29/2023 |  | Routine/Scheduled | 234-14-258 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | Jan 1 1900 2:00PM
10/04/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 10/04/2023 | Sample Chamber | 5.000000 | [5 empty] | Attached to this report |  | Septic Tank-3"sludge 0"scum/ Microfast-0"sludge/ Pump Tank-0"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-158 ETM-6h 37m/ Pump2-155 ETM-6h 30m On-2m 45s Off-6h/ Peak Off-4h 48m/ Peak-5/ High-5/ Pumps: Zoeller E-165 (230 volts) No breakout or spongy areas on the LPD Pad area and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2024 | 12:23 PM
09/15/2023 | Alternative | Routine/Scheduled | 06-160-0081 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/15/2023 | 02:30 PM
09/18/2023 | Alternative | Routine/Scheduled | 2005-143-0222 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1250 | Clearstream ATU |  | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [17 empty] | Air filter changed. System checked. System appears to be operating normally. Etm 361.58, ct 70929 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/18/2023 | 09:00 AM
02/07/2023 | Alternative | Reportable Incident | 119-STS-106011 | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | COSS - Maintenance - GMP2018-02 Replaced distribution box with new 8 port concrete DBox Spliced to existing conveyance line Spliced to existing header lines. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/09/2023 | 06:30 AM
10/05/2023 | Alternative | Routine/Scheduled | 19-142-0146 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 100.000000 | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [17 empty] | Effluent filter cleaned. Manifold flushed. No overrides for the last 30 days. Changed recirc off time from 17 to 20 minutes. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | Dec 30 1899 8:24AM
01/30/2023 |  | RoutineScheduled | 14-183-006 | Russell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | 12:00 AM
12/07/2023 | Alternative | RoutineScheduled | VAG401991 | Augusta | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None |  | 7.620000 |  |  | 1.900000 |  | 12/07/2023 |  | 4.000000 |  |  | 7.300000 | [5 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/12/2024 | 04:00 PM
07/26/2023 | Alternative |  | 195-Discharge-15326 Greenway Rd. | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/26/2023 |  | 3.760000 | [5 empty] | Will be sent separately |  | BOD: 3.76 TSS: BDL | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/26/2023 | 12:00 AM
04/07/2023 |  | Routine/Scheduled |  | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level Processing Tank - RSV, recirc pump & effluent screen serviced. Media Filter - media drapes and spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | 08:45 AM
04/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Whitewater ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | Dec 30 1899 11:24AM
04/20/2023 |  | Routine/Scheduled | 085-STS-32325 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/20/2023 | Jan 1 1900 10:01AM
03/07/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 03/07/2023 |  | 17.000000 | [5 empty] | Will be sent separately | Inspected | Filler clog, wipes and hygiene products | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
04/03/2023 |  | RoutineScheduled | 19-137-0058 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1500 | Advantex |  | Gravity | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 12:00 AM
11/08/2023 | Alternative | Routine/Scheduled | 06-160-0023 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable | 141.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/08/2023 | 02:00 PM
10/27/2023 | Alternative | Routine/Scheduled | 228-04-1156 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Ecoflo |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Replaced peat moss | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/27/2023 | Dec 30 1899 10:00AM
07/19/2023 | Alternative | RoutineScheduled Component Maintenance | 179-07-0105-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Recirculation Pump" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | The Tri-Check Valve in the Pump Tank is leaking. We recommend installing a new gasket. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
03/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | UV |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
05/11/2023 | Alternative | Routine/Scheduled | -STS-5287 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | System flooded - property owner routinely has large amounts of people at residence during spring to summer ... | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/25/2023 | Dec 30 1899 11:00AM
04/27/2023 |  | Follow-Up | 175-17-0164 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [7 empty] | 04/27/2023 |  | 2.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/10/2023 | 05:56 AM
06/14/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Gravity | Drip | Not Applicable | 450.000000 | ["None"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | 12:00 AM
01/31/2023 |  | RoutineScheduled | 177-17-0061-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Annual inspection and cleaning completed. Reset all "R" counts to zero. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
01/05/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic/ Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 01/05/2023 | Sample Chamber | 15.000000 | [5 empty] | Attached to this report |  | Septic-3"sludge 3"scum/ Microfast-4"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working properly/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/26/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Pad | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/28/2023 | Dec 30 1899 11:00AM
04/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/28/2023 | Alternative | Reportable Incident | SWP-05-188 | Spotsylvania | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | Attached Growth Medium | Attached Growth Medium | NO | [17 empty] | Removal of spent peatmoss biofilter for Old Dominion Onsite - Contract job with VacTruck for removal. Old Dominion Onsite is Service Provider - | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/29/2023 | 06:45 AM
09/21/2023 | Alternative | RoutineScheduled | 043-14-0142 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | MicroFast | Pump | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","SludgeScum Accumulation","Level Sensor Operation"] | NA | [17 empty] | 4' liquid depth, 2" of scum, 10" of sludge, 3" of sludge of fast side. Pump Tank is clean. Pump, blower, alarm al working. Field Dry. Audio alarm unhooked. I hooked it back up. 4015 Doses, 1752 Veto, 192:12:39 hrs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/02/2023 | 12:30 PM
07/25/2023 | Alternative |  | 17-195-160-SP | Washington | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/25/2023 |  | 5.660000 |  |  | 2.700000 |  |  | Will be sent separately |  | BOD: 5.66 TSS: 2.70 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/25/2023 | 12:00 AM
01/12/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Air pre-filter cleaned as preventative maintenance. Aeration is minimal again. Manifold needs to be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
12/19/2023 | Alternative | RoutineScheduled | 107-13-0223 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 10:15 AM
09/22/2023 | Alternative | RoutineScheduled | 175-07-0149 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank | Delta DF-50 ATU to Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Septic Tank-8"sludge 1"scum/ ATU-6"sludge 0"scum/ Pump Tank-5"sludge ( Needs Pump out)Controls, pump, floats and alarms are functioning properly/ Blower air filter cleaned and blower is working properly/ Counts: Pump-20628 ETM-15h/ High level-338/ Watermeter-1,511,920/ No breakout or spongy areas on the drip field and is dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/06/2023 |  | Follow-Up | 061-STS-25944 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/31/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/31/2023 | 12:00 AM
12/18/2023 | Alternative | Routine/Scheduled | 157-15-0065 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Trash Tank Condition of above Component Notes for above Component Found at normal level, 11in of sludge and less than 1in of solids. Discharge/Pump Tank Condition of above Component Notes for above Component Found at normal level, pump side found 1in of sludge. Uv side found 10in of sludge. Pulled and cleaned uv and housing. Uv working as it should Tested transducer and pump all working as they should Aeration Condition of above Component Notes for above Component Found at normal level, 4in of sludge and less than 1in of solids. Could hear and see treatment working properly. Air Pump/Blower Condition of above Component Notes for above Component Pulled and cleaned air filter. Tested air pressure sensor. Control panel working properly. Air blower pulled 3.3 amps. Control Panel Condition of above Component Notes for above Component 12 volts audio and visual alarms working as they should. Pump pulled 5 amps. Uv panel 120 volts audio and visual alarms working as they should LPD Condition of above Component Notes for above Component Exersized all valves. Found no surfacing in drainfield area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | 02:14 PM
01/10/2023 |  | Routine/Scheduled | 234-17-0040 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | Replaced diffuser and UV ballast | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | Jan 1 1900 10:20AM
11/13/2023 | Alternative | Routine/Scheduled | 157-16-0105 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Normal Level 15" of sludge and 1" of solids No signs of infiltration -Discharge/Pump Tank: Normal Level Less than 1"of suspended solids All floats and pump are functioning properly however they are Aged Pulled and clean pump screen Uv panel is functioning properly and bulb is functioning properly However bulb is aged -Aeration: Normal Level Less than 1"of suspended solids Pulled and cleaned diffuser and weir However diffuser is 75% clogged Signs of leaks through risers -Air Pump/Blower: 120v Pulled and cleaned air filter Pulling .8amps -Control Panel: 120v to each breaker Pump pulled 8.88amps All audible and visual alarms are functioning properly Timer functioning properly -LPD: No signs of surfacing Repairs and pumping to be made on 11/15 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | 02:50 PM
10/22/2023 | Alternative | RoutineScheduled | SD-02-374 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | microfast |  | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | YES | None | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/19/2023 | 08:00 AM
07/22/2023 | Alternative | Follow-Up Component Maintenance | 179-11-0025-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced distribution box with above grade monster distribution box. Replaced headers 1-5 close to distribution box and line 6 just before drain line. Applied root kill to all lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 07:01 AM
01/26/2023 | Alternative | Reportable Incident | 073-STS-105173 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | COSS - Maintenance - GMP2018-02 Primary septic tank pumped down for repair. Installed access riser on septic tank. Installed cannister style effluent screen in outlet of septic tank Installed new 8 port concrete distribution box. Spliced to existing conveyance line Spliced to existing header lines. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/30/2023 | 08:45 AM
07/20/2023 | Alternative | Reportable Incident | 166-15-133 | Northumberland | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Pad | UV | 450.000000 | ["Control Operation","Disinfection","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Visit - Requested Second Opinion of treatment System - previous service provider equals Obsidian Trash Tank - inlet T clogged - 28" of sludge - requires pumpout. Aeration Tank - normal level - 5" suspended solids - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating - control panel door fractured . audio visual alarm not working - recommend panel replacement. Obsidian UV has failed - Bulb has bun marks, panel corroded - do not believe that system has had required service in a while. - Recommend replacing UV system with "other" manufacturer. LPP Field walked - no indications of surfacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/24/2023 | 07:30 AM
04/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/02/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
03/24/2023 |  | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Installed UV Bulb & chord. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/31/2023 | Jan 1 1900 12:26PM
11/07/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 12:00 AM
03/28/2023 | Alternative | RoutineScheduled | 154-08-0079 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | MicroFast |  | Gravity | Pressure | Discharge | Chlorination | 500.000000 | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Dispersal System Operation","Disinfection","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 12:00 AM
04/03/2023 |  | RoutineScheduled | 177-15-0222-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Disinfection" ,"Effluent Screens"] | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Disinfection" ,"Effluent Screens"] | YES | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Spinners were barely spraying due to clogged pump intake plus dirty manifold pipe, cleaned both and system started working good. Cleaned both pump housings due to scum layer. Both tanks need pump out due to solids. quality of treatment was still good after clogged pump intake and sheets bridging. Will send proposal for pump out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
01/18/2023 |  | Routine/Scheduled | 053-STS-10124 | Dinwiddie | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/18/2023 | Jan 1 1900 3:29PM
06/27/2023 | Alternative | Reportable Incident | 147-11-0036 | James City | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Pressure | Drip |  | 450.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation"] | None | [18 empty] | System in alarm - all tanks high level - absorption mound is saturated and surfacing - offered pumpout of tanks - homeowner declined. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/28/2023 | Dec 30 1899 10:30AM
01/10/2023 | Alternative | Routine/Scheduled | 550-STS-6343 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The timer is set to 7 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | Dec 30 1899 1:00PM
03/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/21/2023 | Alternative | Routine/Scheduled |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [29 empty] | Maintenance and Inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/22/2023 | 03:52 PM
03/07/2023 |  | RoutineScheduled | 133 04 1026 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | BioWheel |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | Monthly Report. Total flow for month of February 2023 - 49,407 gallons. Average daily flow - 1,495 gallons. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/08/2023 | 07:03 PM
10/24/2023 | Alternative | RoutineScheduled Component Maintenance | 182-02-0693 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Primary tank pumped FIlter cap replaced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
07/13/2023 | Alternative | RoutineScheduled | SD-04-190 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | septic | ATU | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | YES | Musty | Clear | [15 empty] | No Discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/17/2023 | 07:45 AM
03/24/2023 | Alternative | RoutineScheduled | 09-183-029 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/24/2023 | 12:00 AM
09/05/2023 | Alternative | Pump-Out Only | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | YES | [16 empty] | Pumped Out | Advantex tank pumped out | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/09/2023 | Dec 30 1899 4:00PM
05/10/2023 |  |  | 033-12-0003-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
11/14/2023 | Alternative | Routine/Scheduled | 2009-143-0091 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Hoot |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/14/2023 | 01:36 PM
04/06/2023 |  |  | 2006-143-0033 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 2000 | 1000 | 1000 | Pump | Pressure | Pad | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Pungent | Discolored | 7.000000 |  | 6.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/06/2023 | 11:00 AM
04/18/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
01/02/2023 |  | RoutineScheduled | VAG408306 | Highland | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | EcoFlo Peatmoss | Gravity | Gravity | Discharge | Chlorination |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | [17 empty] | The system did not need to be pumped. The peat moss was removed and replaced in the treatment tank. The lids were secured. | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 01/25/2023 | 04:25 PM
07/31/2023 | Alternative | RoutineScheduled Component Maintenance | 177-07-0449-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
09/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-6"sludge 0"scum/ Microfast ATU-1"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-180 ETM-13h 41m/ Pump2-177 ETM-13h 28m On-4m 41s Off-12h Peak off-9h 36m / Peak-10/ High-10/ No breakout or spongy areas on the drainfield and dosing correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/15/2023 |  | Routine/Scheduled | 234-13-388 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | Jan 1 1900 2:50PM
06/16/2023 | Alternative | Follow-Up Component Maintenance | SWP-04-630 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced Advantex sheets with new style upgrade kit. Resealed recirc inlet riser. Sealed root penetration on pump tank outlet riser. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
02/28/2023 |  | RoutineScheduled | {FIPSCode}-STS-8940 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/28/2023 | 12:00 AM
01/16/2023 |  | Routine/Scheduled | 06-160-0100 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | 02:00 PM
06/01/2023 | Alternative | RoutineScheduled | 16-160-0091 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 | 2500 | Microfast |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | [16 empty] | Inspected | - pump tank and pretreatment tanks need to be pumped/cleaned | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/08/2023 | 12:00 AM
07/05/2023 | Alternative | Reportable Incident Component Maintenance | SP-04-384 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to failed pump. Installed new pump, check valve and plumbed pump up into the riser to meet code. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
03/17/2023 |  | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [6 empty] | ["Control Operation","Dispersal System Operation"] | ["Control Operation","Dispersal System Operation"] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/30/2023 | 12:37 PM
04/07/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
02/15/2023 |  | RoutineScheduled | WWRT-9E2QUT | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NO | [7 empty] | 02/15/2023 | Sample Chamber | 5.000000 | [7 empty] | Septic-0"sludge 0"scum/ EZ-Treat-0"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Recirc. Pump intake cleaned/ Controls, pumps, floats and alarms functioning properly/ Counts: Discharge Pump CC-146 ETM-15h 28m/ EZ-Treat Pump-0015601/ ETM-0078742 On-2.5m Off-14m/ High-3 / EZ-Treat media in very good condition/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/20/2023 |  | Routine/Scheduled | 04-172-0451A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump, Effluent screen serviced. Treatment Module - media drapes, spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/21/2023 | Jan 1 1900 7:30AM
09/08/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-4382 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | Dec 30 1899 8:35AM
11/13/2023 | Alternative | RoutineScheduled Component Maintenance | 179-14-0189-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
02/20/2023 |  | RoutineScheduled | 179-11-0088-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | Roots are growing through all of the fittings of the Fralo Montster Box. We recommend excavating by machine and replacing fittings and/or the Monster Box as necessary to remove roots, reseal fittings, and ensure effluent is not leaking out of the box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
05/19/2023 |  | Routine/Scheduled | 228-16-0418 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | Jan 1 1900 11:25AM
11/16/2023 | Alternative | Reportable Incident |  | Buckingham | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 2.000000 | 2250 | Delta Whitewater Model DF |  | Pump | Gravity | Discharge | Chlorination | 600.000000 | ["Distribution Pump Operation","SludgeScum Accumulation","Septic Tank Baffles","BlowerCompressorAerator Operation","Level Sensor Operation","Other"] | ["Distribution Pump Operation"] | NO | [16 empty] | Pumped Out |  | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/16/2023 | Dec 30 1899 11:00AM
06/15/2023 |  | RoutineScheduled | 16-142-0332 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1000 | EZ Treat |  | Pump | Pressure | Drip |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/15/2023 | 12:00 AM
12/14/2023 | Alternative | RoutineScheduled Component Maintenance | SD-04-516 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 02:30 PM
05/05/2023 | Alternative | Routine/Scheduled | 149-STS-10628 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 1000 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/05/2023 | Dec 30 1899 1:00PM
01/14/2023 |  |  |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [15 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | 12:00 AM
06/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | 11:17 AM
10/16/2023 | Alternative | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Disinfection"] | ["Disinfection"] | [18 empty] | Service call only: Found the UV-Light Bulb was blown. Replaced and tested/ UV-Light now functioning properly. Counts: Watermeter-022320.19/ Pump-4221 ETM-746h 53m. Noted: Microfast media is clogged and is in need of a chemical cleaning. Owner was informed and is checking with other companies. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/10/2023 | Alternative | Reportable Incident | 115-STS-102164 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Fuji |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | AOSS - Install - VDH permit 157-23-0039 Pumped septic tank empty, crushed and removed. Installed new FujiClean CEN5 ATU and pump tank. Installed new absorption bed in accordance with permit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/25/2023 | 07:30 AM
01/11/2023 |  | RoutineScheduled | 181-15-0071 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The blower filter was cleaned. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/25/2023 | 04:45 PM
09/01/2023 | Alternative | Reportable Incident | 159-10-093 | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Installed an aerator rebuild kit. Replaced the UV bulb and replaced the UV ballast. The timer is set to 5 minutes every 1 hour. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/01/2023 | 01:30 PM
03/02/2023 |  | RoutineScheduled | 153-STS-20384 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["Disinfection","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Disinfection"] | [8 empty] | 03/02/2023 | Sample Chamber | 19.000000 |  | 5.000000 |  |  |  | Attached to this report |  | Septic-4"sludge 2"scum/ Microfast-2"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned but blower is below grade and requires to be raised 6"-8"/ UV-Light cord is short and requires longer cord to get full treatment and the ballast needs replacement/ Conduit is separated and needs to be reconnected to prevent water intrusion. Controls, pump, floats and alarms are functioning properly/ Counts: Pump-1010 ETM-137h On-8m 19s Off-2h 4m / Watermeter-004595.0/ High-22/ No breakout or spongy areas on the drip area and dosing properly. Returned on 5/2/2023 for repairs : Raised blower/ Replaced UV Cord/ Replaced UV Conduit/ Raised UV-Light Box. All repairs are complete. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/03/2023 |  | Reportable Incident | SWP-05-57 | King George | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Rappahannock | Assure Plumbing & Septic LLC | 1942001502 | Assure | LLC | 2.000000 | 1000 | 1000 | 1000 | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Septic | [16 empty] | Peat is almost completely failed. Advised owner to plan to replace within the year | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | 12:00 AM
11/01/2023 | Alternative | RoutineScheduled |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1150 | 1000 | 150 | Pump | Gravity | Mound | Not Applicable |  | [] | ["Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Disinfection","Auxiliary Filter","Attached Growth Medium","Control Operation"] | YES | Pungent | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | 12:00 AM
03/15/2023 |  | Initial Visit | 163-STS-338043 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 1.000000 |  |  |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles"] | YES | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/22/2023 | 03:20 PM
10/04/2023 | Alternative | RoutineScheduled | 193-STS-94372 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | peat check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
11/07/2023 | Alternative |  | 2018-143-0195 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | [9 empty] | [] | [] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/07/2023 | 12:00 AM
04/19/2023 | Alternative | Routine/Scheduled | 157-16-0085 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 2.5 minutes every 1.5 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/19/2023 | 02:00 PM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance | SP-04-904 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
07/26/2023 | Alternative |  | 191-STS-36019 | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/26/2023 |  | 2.090000 |  |  | 1.000000 |  |  | Will be sent separately |  | BOD: 2.09 TSS: 1.00 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/26/2023 | 12:00 AM
07/12/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/30/2023 | 12:00 AM
08/09/2023 | Alternative | Routine/Scheduled |  | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump basin - dosing - plastic - bulging noted - float sensors, pump and controls operating. Biofilter - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 08:45 AM
09/13/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
12/19/2023 | Alternative | RoutineScheduled | 075-STS-34208 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1000 | EZ Treat |  | Gravity | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/29/2023 | 12:00 AM
03/28/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower connection was repaired. System should return to normal operation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/16/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | A septic system inspection was done on a conventional gravity. The septic tank lid was dug up it was 16" under the ground. The tank was pumped out and inspected for any cracks or leaks and non were seen. The sewer line was camera snaked and was clear. We would recommend adding a riser and a filter on the outlet side of the tank to help stop solids from getting into the drain field. The 10 port concrete d-box was dug up it was 10" under the ground. Camera snaked all 7 header lines. Lines 1 and 6 are blocked with sludge. Line 2 was clear. Lines 3,4,5 and 7 the corrugated lines were full of dirt and looked like the corrugated lines were split. There were 2 small trees between the drain field lines 6 and 7 that should be removed. At time of inspection the septic system was not in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
07/20/2023 | Alternative | Routine/Scheduled | 093-STS-15037 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | Dec 30 1899 1:20PM
11/13/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | Dec 30 1899 10:55AM
02/27/2023 |  |  | SWP-05-270 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
01/09/2023 |  | Routine/Scheduled | 550-STS-6332 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | Jan 1 1900 11:00AM
08/14/2023 | Alternative | RoutineScheduled | C-122-15-0004 | Craig | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | King's Alternative Septic | 1942001094 | David | King | 1.000000 | 1500 | Bio Microbics Microfast 0.5 |  | Pump | Pressure | Drip | Not Applicable | 100.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | Replaced Effluent Filter, system is working correctly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/06/2023 | 12:00 AM
06/13/2023 | Alternative | Routine/Scheduled | 04-142-0074 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing tank - RSV, recirc pump and effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | Dec 30 1899 9:15AM
01/03/2023 |  |  | 101-07-0116 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Virginia Soils Inc, dba VSI Supply / AG Onsite | 1942001291 | Archie | Arnold | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/15/2023 | 12:00 AM
04/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Power surge last week tripped Microfast blower breaker. Breaker was reset and system should return to designed operation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/01/2023 | Alternative | RoutineScheduled | 175-98-0491 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | YES | [17 empty] | Septic Tank-10"sludge 3"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Recommend cleaning the septic filters twice a year/ Controls, pump, floats and alarms are functioning properly/ No breakout or spongy areas on the LPD drainfield area and is dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/27/2023 | Alternative | Follow-Up Component Maintenance | 099-10-0003-SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Chemically cleaned FAST unit. Both tanks pumped out by others. Bleached flushed drip tubing in attempt to improve rates, will re-check in 1-2 weeks. Replaced backer board on FAST panel. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
04/03/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
11/15/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-14310 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 7.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
12/06/2023 | Alternative | Routine/Scheduled | 103-STS-92659 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the filter in the septic tank (was stopped up). Changed the diffuser in the Clearstream and changed the filter in the aerator. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 01:30 PM
12/06/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/07/2023 | Dec 30 1899 11:15AM
01/05/2023 |  |  | 2005-143-0118 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Microfast | [6 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/03/2023 | 12:00 AM
08/29/2023 | Alternative | RoutineScheduled | 061-17-363 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | trash | Microfast | Gravity | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | 12:25 PM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/12/2023 | Alternative | RoutineScheduled | 08-142-0168 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | [] | ["Control Operation","Effluent Screens","Attached Growth Medium","Distribution Pump Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/05/2023 |  | RoutineScheduled | 12-184-5001 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation","BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/05/2023 | 12:00 AM
04/10/2023 |  | RoutineScheduled | VAG408015 | Rockbridge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MICROFAST |  | Gravity | Gravity | Discharge | Chlorination |  | ["None"] | ["None"] | NA | [17 empty] | SYSTEM DID NOT NEED TO BE PUMPED. BLOWER FILTER WAS CLEANED. CONTROLS OPERATING AS DESIGNED. EVAPORATION BED FUNCTIONING AS DESIGNED. THE APPROPRIATE AMOUNT OF TABLETS WERE IN THE FEEDER, NO ADDITION WAS MADE. NO DISCHARGE AT TIME OF VISIT. NO VISIBLE LEAKS IN CONVEYANCE LINES OR EVAPORATION BED. LIDS WERE SECURED. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/01/2023 | 09:40 PM
04/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/23/2023 |  |  | SP-03-249 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
09/25/2023 | Alternative | RoutineScheduled | 175-14-0042 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["Disinfection","BlowerCompressorAerator Operation"] | ["Disinfection","BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-4"sludge 4"scum/ Microfast-2"sludge 0"scum/ Pump Tank-3"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower is working properly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-43896 ETM-1831 On-5m 55s Off-1h 54m/ Override-253781/ High-162777/ Switch to Hand-49/ Watermeter-0196100/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/05/2023 | Alternative | Initial Visit | 800-STS-14219 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 4.000000 |  | 4.000000 | [5 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream (was stopped up). Changed the diffuser in the Clearstream and changed the filter in the aerator. The UV is working. The timer is set to 1 minute every 2 hours. Took BOD and Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/05/2023 | Dec 30 1899 12:00PM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 3.000000 | 1250 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 4:40PM
12/05/2023 | Alternative | RoutineScheduled Component Maintenance | 015-STS-336642 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Pumped primary tank Replaced recirc pump was clogged from hair and solids | This AOSS should now return to normal function after having provided the above state routine maintenance | 01/15/2024 | 10:39 AM
07/18/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-92157 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Control Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation"] | NA | None | Clear | [5 empty] | 07/18/2023 |  | 8.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Bad enabler float for discharge, replaced. RECIRC: HL 1, LL 17, OVERRIDE 40. DISCHARGE: HL 15, ETM OM, PEAK 19, ETM 1OH0M. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:19 PM
06/14/2023 | Alternative | RoutineScheduled | 2005-143-0301 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
01/02/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1500 | Septic | pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/18/2023 | Alternative | Routine/Scheduled | 18-172-0338A | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/18/2023 | Dec 30 1899 12:11PM
11/29/2023 | Alternative | RoutineScheduled Component Maintenance | 175-15-0218 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Clearstream | none | Pump | Gravity |  | UV |  | ["Disinfection" ,"Dispersal System Operation"] | ["Disinfection" ,"Dispersal System Operation"] | NA | Musty | Clear | 7.600000 | 9.200000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 12/06/2023 | 09:34 AM
11/15/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | Dec 30 1899 10:33AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance | 177-14-0259-SR | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 2.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Couple flower bushes planted on pad, advised customer to remove them before they grow root inside pipes. Customer said she will take care of it. Recirc tank will need pump out next year. HL 19, LL 73, OVERRIDE 87. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
03/21/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation"] | ["Effluent Screens" ,"Level Sensor Operation"] | YES | [15 empty] | Will be sent separately | Inspected | Needs contactor in control panel replaced & 3 control floats. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/15/2023 | 07:20 PM
03/31/2023 |  | RoutineScheduled | 14-183-127 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 3 Chlorine 7 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/31/2023 | 12:00 AM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
06/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/26/2023 | Alternative |  | {FIPSCode}-STS-23599 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/26/2023 |  | 6.470000 |  |  | 4.900000 |  |  | Will be sent separately |  | BOD: 6.47 TSS: 4.90 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
07/11/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Norweco Singulair ATU |  | Pump | Pressure | Drip |  | 600.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | 10:03 AM
09/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/19/2023 | Alternative | RoutineScheduled Component Maintenance | 175-15-0006 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
07/31/2023 | Alternative |  |  | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 12:00 AM
08/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","Level Sensor Operation"] | ["Attached Growth Medium","Level Sensor Operation"] | YES | [17 empty] | Septic Tank-4"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Timer enable float was faulty and replaced during inspection/ Controls, pumps, floats and alarms are now functioning properly/ Turned Puraflo Peat and peat is in good condition/ No breakout or spongy areas on the Puraflo Pad Site Area. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
10/18/2023 | Alternative | Follow-Up | 800-STS-13899 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [20 empty] | 14.000000 | [7 empty] | Took initial BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | Dec 30 1899 10:00AM
09/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/05/2023 | Alternative | Reportable Incident | SWP-03-599 | Spotsylvania | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2000 | Puraflow - 4 Pods |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","Distribution Pump Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [14 empty] | Pumped Out | Pumped septic tank - 8/30 Pumped Pump station tank - 10/5 to accommodate the repair Replace inop effluent pump Conduct draw down and adjust time dose for a 3 bed home | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/05/2023 | 02:00 PM
05/05/2023 | Alternative | Routine/Scheduled | 128-04-283 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump and effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - full - drainfield drains super slowly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | 08:45 AM
07/19/2023 | Alternative | RoutineScheduled | 151-14-0007 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/29/2023 |  | RoutineScheduled | 167-STS-17800 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 2 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/29/2023 | 12:00 AM
12/29/2023 | Alternative | RoutineScheduled | 02-163-0374 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Advantex AX20 |  | Pump |  |  |  |  | [] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Auxiliary Filter"] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/29/2023 | 12:00 AM
11/21/2023 | Alternative |  | 08-197-A2 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/21/2023 |  | 21.900000 |  |  | 3.900000 |  |  | Will be sent separately |  | BOD: 21.9 TSS: 3.90 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/21/2023 | 12:00 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/12/2023 | Alternative | Routine/Scheduled | 166-13-021 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 4.000000 | 3600 | Clearstream |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 75.000000 | [11 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 05:22 PM
11/03/2023 | Alternative | RoutineScheduled | 019-STS-27296 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Drip |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | warranty claim - adjusted float switches to correct design changes by manufacturer- recirc pump 1 min on and 5.3 min off normal and 1 min on and 1.5 min off for overide level. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
02/21/2023 |  | RoutineScheduled | 2107-05-153 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  |  |  | NA |  |  | 6.900000 | 7.400000 | [11 empty] | Will be sent separately | Inspected | Note: No Discharge Sign | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/01/2023 | 02:21 PM
01/24/2023 |  | Routine/Scheduled | 550-STS-6595 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 01/24/2023 |  | 4.000000 |  | 26.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 9:20AM
11/06/2023 | Alternative | RoutineScheduled Component Maintenance | 179-14-0178-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
06/08/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | schedule pumping of Septic | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | 12:00 AM
10/16/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2024 | Dec 30 1899 11:55AM
04/26/2023 |  | Routine/Scheduled | 02-142-0207 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | NO | [17 empty] | Manifold flushed. System appears to be operating normally. Used water probe around risers found the risers on the septic tank leak at tank connection. These should be sealed. This should stop the overrides. Averaged 5 overrides per day. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | Jan 1 1900 10:30AM
12/28/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0085-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"Control Operation"] | ["Attached Growth Medium" ,"Septic Tank Baffles" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Distribution box was full of roots blocking 2 lines, removed roots. Recommended to customer to add Root-x but he said he will take trees near of d-box instead. System may most likely will need pump out next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 07:39 AM
08/28/2023 | Alternative | Routine/Scheduled | 800-06-0194 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | Dec 30 1899 9:00AM
04/14/2023 |  | Routine/Scheduled |  | Gloucester | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - riser damaged by lawncare operations - effluent screen serviced. BioFilter - peatmoss spent - requires replacing - heavy ponding present - PUmp Basin - float sensors, pump and controls operating. DBox - intact | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/17/2023 | 11:00 AM
08/07/2023 | Alternative | Routine/Scheduled | 234-18-360 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | Dec 30 1899 9:30AM
03/27/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/06/2023 | 12:00 AM
04/26/2023 | Alternative |  |  | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan |  |  | Chester | Mummau | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/22/2023 | Alternative | RoutineScheduled Component Maintenance | 182-95-0611 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Dispersal System Operation"] | ["Control Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Control breaker was tripped corrected | This AOSS should now return to normal function after having provided the above state routine maintenance | 10/13/2023 | 01:07 PM
09/20/2023 | Alternative | RoutineScheduled | 177-18-350-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Aquasafe |  | Pump | Gravity | Trenches | Not Applicable | 150.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/10/2023 | 11:50 AM
02/15/2023 | Alternative | Routine/Scheduled | 103-STS-96490 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Trenches | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [7 empty] | 02/15/2023 | Sample Chamber | [8 empty] | 180 day post install inspection - lab samples for BOD5, TSS & E-Coli obtained and transported to Envirocompliance laboratory, Ashland. Primary septic tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. U.V. System - bulb and housing serviced. Lab Samples Obtained - BOD5, TSS & E-Coliform Pump Tank - float sensors, pump and controls operating. Absorption Field - no indications of surfacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/16/2023 | 07:00 AM
10/07/2023 | Alternative | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 4.000000 | 8500 | EZ Treat |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Septic tank #1 - 7" of accumulated solids. Septic tank #2 - 8" of accumulated solids. Recirculation Tank - 8" of accumulated solids. Discharge Pump Tank - 0"of accumulated solids. Cleaned septic tank filter. Cleaned EZ Treat spray nozzles | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | 07:03 PM
04/20/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [5 empty] | 04/19/2023 |  | 14.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | Jan 1 1900 12:48PM
11/01/2023 | Alternative | RoutineScheduled Component Maintenance | SP-04-669 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation" ,"SludgeScum Accumulation"] | ["Dispersal System Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend pumping the septic/ATU tank due to scum and sludge accumulation in the tank. We also recommend cutting back and mowing around all edges for the drip dispersal area to prevent root intrusion into the dispersal system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
08/11/2023 | Alternative | Follow-Up Component Maintenance | 175-18-0324 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced UV bulb & cord. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
02/28/2023 |  | RoutineScheduled | 15-125-100 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/28/2023 | 12:00 AM
06/13/2023 |  | RoutineScheduled | 175-16-0011 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Water meter needs replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | 12:05 PM
02/14/2023 |  | RoutineScheduled | 179-17-0110-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
11/28/2023 | Alternative | RoutineScheduled Component Maintenance | 182-03-0319 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | raised filter housing and installed float tree unable to check sandfilter as it is buried | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/25/2023 | Alternative | Reportable Incident | 073-STS-102609 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 600.000000 | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | COSS - Repair - VDH Permit 136-23-0120 - GMP2018-02 Pumped and crushed / removed existing septic tank. Installed new Infiltrator IM1060 Poly tank Spliced to existing conveyance line and sewer line. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 01:00 PM
04/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/28/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | System not in EHD, missing address to attach. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/28/2023 | Dec 30 1899 8:56AM
03/06/2023 |  | RoutineScheduled | SWP-02-498 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 2-2 2-2 | 0-0 | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear |  |  | 7.000000 | [11 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/06/2023 | 09:00 AM
05/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 3.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air release valve on Zone 2 had come off. It was replaced and appears to be functioning as designed now. Valve box and air release valve will be replaced and area will be limed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/26/2023 | Alternative |  | 09-192-184 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 06/26/2023 |  | 10.600000 |  |  | 2.100000 |  |  | Will be sent separately |  | BOD: 10.6 TSS: 2.10 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/26/2023 | 12:00 AM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/23/2023 | Alternative | Reportable Incident | SD-06-13 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | Owner called about septic panel alarming, buzzer sounding with varying intensity. Owner admitted to running the pump manually to clear the alarm. It kept alarming so he shut off the control breaker. Panel was still indicating a high level alarm, but water was all the way down to the pump intake. Replaced the alarm float under warranty (contacts stuck shut) and tested other floats (timer and override). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
02/03/2023 |  | Routine/Scheduled | {FIPSCode}-STS-1317 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | Jan 1 1900 10:35AM
10/04/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | DeHaven's Backhoe Service Inc. | 1942001541 | Wayne | Edmonson | 2.000000 | 2500 | Septic tank |  | Pump | Pressure | Trenches | Not Applicable | 175.000000 | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/07/2023 | 10:00 AM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | 182-16-0295 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 09/26/2023 |  | 13.000000 | [5 empty] | Will be sent separately | Inspected | Gauge and oring replaced Lab sample normal | This AOSS should now return to normal function after having provided the above state routine maintenance | 10/13/2023 | 01:07 PM
09/30/2023 | Alternative | RoutineScheduled | 154-05-1089 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Randy's Complete Water & Wastewater Services | 1942001335 | Randy | Gray | 1.000000 | 1000 | Puroflo |  | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/02/2023 | 09:00 AM
08/25/2023 | Alternative | RoutineScheduled | 06-100-0093 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | ECOFLO |  | Pump |  | Pad |  | 450.000000 | [] | [] | YES | [17 empty] | SLUDGE JUDGE 4-5" FROM BOTTOM 1" FROM TOP EVERYTING IS WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | 01:45 PM
02/01/2023 |  | RoutineScheduled | {FIPSCode}-STS-18002 | Bland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Auxiliary Filter","Control Operation","Effluent Screens","Dispersal System Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/01/2023 | 12:00 AM
09/12/2023 | Alternative | Follow-Up |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [20 empty] | 3.000000 |  | 1.000000 | [5 empty] | Took 5 year BOD and Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | Dec 30 1899 10:45AM
04/05/2023 |  | Routine/Scheduled |  | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - recommend pumpout - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/06/2023 | Jan 1 1900 7:30AM
04/28/2023 |  | Pump-Out Only |  | James City | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 4.000000 | 9000 | None | None | Gravity | Pressure | Trenches | Not Applicable | 4000.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Pumped septic tanks for storage. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/01/2023 | Jan 1 1900 8:30AM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1500 |  |  | Pump | Gravity | Pad | Not Applicable | 750.000000 | ["None"] | ["None"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/15/2023 | Dec 30 1899 2:45PM
01/24/2023 |  | Routine/Scheduled | 550-STS-6547 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 3:39PM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance | 015-STS-337964 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | [7 empty] | 06/19/2023 |  | 7.000000 | [5 empty] | Will be sent separately | Inspected | Replaced Recirc Pump Repaired leaks in field Replaced lid on riser | This AOSS should now return to normal function after having provided the above state routine maintenance | 08/23/2023 | 06:57 AM
11/09/2023 | Alternative | RoutineScheduled | 14-100-0350 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 500 | AQUASAFE |  | Pump | Gravity |  | UV | 300.000000 | [] | [] | YES | [16 empty] | Pumped Out | SLUDGE JUDGE SEPTIC TANK REVEALED 11" FROM BOTTOM AND 1-2" FROM TOP-PUMPED SEPTIC REBUILD BLOWER EVERYTHING WORKING THE WAY IT SHOULD | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/08/2023 | 10:30 AM
03/01/2023 |  | RoutineScheduled | 179-13-0228-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity |  | Chlorination |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | No water coming from discharge to test. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 11/15/2023 | 02:02 PM
01/19/2023 |  | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Aquarobic Mini Plant | [8 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | 03:06 PM
12/09/2023 | Alternative | RoutineScheduled | 2116-06-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | Chlorination | 500.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.400000 |  |  | 1.600000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/12/2023 | 12:00 AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
01/27/2023 |  | Routine/Scheduled | 234-18-287 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/27/2023 | Jan 1 1900 1:45PM
06/02/2023 |  |  | 033-STS-89548 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
08/16/2023 | Alternative |  | 035-STS-37285 | Carroll | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 08/16/2023 |  | 4.340000 |  |  | 1.000000 |  |  | Will be sent separately |  | BOD: 4.34 TSS: 1.00 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/16/2023 | 12:00 AM
04/12/2023 |  | RoutineScheduled | 175-04-0857 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Effluent Screens"] | ["Control Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 04:23 AM
06/12/2023 | Alternative | RoutineScheduled | 003-STS-32844 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco | Norweco | Gravity | Gravity | Discharge | UV | 450.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES |  |  | 7.100000 |  |  |  |  | 06/12/2023 |  | 10.000000 |  |  | 30.500000 |  |  | Will be sent separately |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | 12:00 AM
12/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [7 empty] | 12/13/2023 |  | 112.000000 | [5 empty] | Will be sent separately | Inspected | Adjusted timers properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
01/31/2023 |  | RoutineScheduled | SWP-05-358 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
08/10/2023 | Alternative | Routine/Scheduled | 234-15-305 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | Dec 30 1899 9:10AM
05/03/2023 | Alternative | RoutineScheduled | 09-100-0599 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1250 | BIOCOIR |  | Pump | Gravity | Trenches | Not Applicable | 300.000000 | [] | [] | YES | [17 empty] | REPLACED FIBER AND N-53 SEWAGE PUMP | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/08/2023 | 11:20 AM
01/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
05/22/2023 |  | Reportable Incident | 177-06-0048-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | None | [14 empty] | Will be sent separately | Inspected | Repaired broken clean-out that was hit by a mower. Flushed mud and pvc chips from the sewer line. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
10/26/2023 | Alternative | RoutineScheduled Component Maintenance | 175-04-0420 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Whitewater ATU | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
05/10/2023 |  | RoutineScheduled | 015-STS-336065 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.710000 | 7.080000 |  |  |  | 05/10/2023 |  | 18.000000 |  |  | 6.200000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/31/2023 | 11:45 AM
04/25/2023 | Alternative | RoutineScheduled | 87-314 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | 12:00 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20503 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation"] | ["Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [5 empty] | 06/08/2023 |  | 248.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/07/2023 | 06:25 AM
12/28/2023 | Alternative | RoutineScheduled | 085-STS-31588 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Recirculation Pump","Distribution Pump Operation","Control Operation"] | ["Attached Growth Medium","Recirculation Pump","Distribution Pump Operation","Control Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/23/2023 | Alternative | RoutineScheduled | 115-93-0097 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Septic Tank | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | YES | [16 empty] | Inspected | Sludge level-1"scum layer on top(fat,oil,grease)-12" sludge in Septic tank - Cleaned effluent filter, Pump data meter reading- 36976 vs 33773=3,203 cycles and pump run time 1439.88 hours vs 1358.74 appears pump ran about 81 hrs total this year. Alarm operational. Turned peat in all 5 pods, peat is like new in all pods. Garter snake in a peat pod this year nested under middle pod. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
09/29/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1125 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/07/2023 | Alternative | RoutineScheduled Component Maintenance | 2107-05-153 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Dispersal System Operation"] |  | NA |  |  | 7.200000 | 7.300000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 12/01/2023 | 10:33 AM
05/12/2023 | Alternative | Routine/Scheduled | 800-STS-15525 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/12/2023 | Dec 30 1899 9:50AM
01/30/2023 |  | Routine/Scheduled | 07-172-0170A | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Delta Environmental Products, DF Series |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - normal level - no riser to grade. Aeration Tank - compressor failure - Replaced Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/31/2023 | Jan 1 1900 7:00AM
06/03/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 5.000000 |  | Clearstream | Clearstream | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump and floats were replaced. System appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/04/2023 | Alternative | Initial Visit | 700-17-0004 | Newport News | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Installed an aerator rebuild kit. The airline assembly is cracked - needs to be addressed and/or fixed. The alarm in the Clearstream is not hooked up (needs to be wired up) - needs to be addressed and/or fixed. The septic tank needs additional risers on it to be properly inspected in the future - also needs a 6" x 12" riser. It was raining at the time of service - could not check the drainfield or mound. The timer is set to 8 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/04/2023 | Dec 30 1899 1:30PM
04/14/2023 |  | Routine/Scheduled |  | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Aeration Tank - normal level - mixing present - compressor serviced. Pump Basin - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 10:30 AM
05/25/2023 | Alternative | Routine/Scheduled | 04-160-0479 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/25/2023 | 11:30 AM
10/19/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/19/2023 | Dec 30 1899 9:10AM
11/16/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Sandfilter, Recirculating |  | Pump | Gravity | Trenches |  | 450.000000 | None | None | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/22/2023 | 10:51 AM
06/26/2023 | Alternative | Routine/Scheduled |  | Loudoun | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Hydro-Action ATU |  | Pump | Gravity | Trenches |  | 600.000000 | ["BlowerCompressorAerator Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/21/2023 | 11:32 AM
07/18/2023 | Alternative | Routine/Scheduled | 234-17-437 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/18/2023 | Dec 30 1899 11:00AM
04/18/2023 |  | RoutineScheduled | 13-184-5003 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 1 Chlorine 7 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/18/2023 | 12:00 AM
01/18/2023 | Alternative | Routine/Scheduled | 136-07-0445 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Cleaned the filter in the Clearstream and cleaned the filter in the septic tank. Changed the diffuser in the Clearstream. Installed a rebuild kit on the aerator. Replaced the pump float, replaced the alarm float, and replaced the alarm light bulb. Installed a new pump (Liberty 280). Installed a splice box in the pump tank. Pumped out the septic tank, pumped out the pump tank, and pumped the sludge out of the Clearstream tank. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/18/2023 | 09:30 AM
01/24/2023 | Alternative | Routine/Scheduled | 151-04-043 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1500 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 75.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 03:32 PM
10/11/2023 | Alternative | RoutineScheduled Component Maintenance | 175-17-0218 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Disinfection" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Uv bulb was replaced while onsite. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
03/22/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
10/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
03/09/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/04/2023 |  | RoutineScheduled | 067-STS-38685 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | Modified Extended Aeration |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | YES | [17 empty] | Total flow to drain fields February 2023 - 117,430 gallons. Average 3,355 gallons per day. All aspects of the system are operational. Wasting of settled mixed liquor from the clarifier to the digester and decanting of supernatant from digester are occurring regularly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/06/2023 | 07:03 PM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0314-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
04/27/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 09:14 AM
11/06/2023 | Alternative | RoutineScheduled | 132-17-0013 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Aquasafe |  | Gravity | Gravity | Trenches | Not Applicable | 150.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/15/2023 | 11:05 AM
07/10/2023 | Alternative | RoutineScheduled | 041-STS-259463 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/03/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["Other"] | ["None"] | YES | [17 empty] | Needs 10 Hole Distribution Box and 5 Header Lines Replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/12/2023 | 12:00 AM
11/15/2023 | Alternative | RoutineScheduled | 2006-143-0063 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 7.000000 |  | Puraflo |  | Gravity | Gravity | Mound |  |  | [] | ["Attached Growth Medium","Level Sensor Operation","Control Operation","Distribution Pump Operation"] |  | Musty | Cloudy | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/15/2023 | 12:00 AM
05/12/2023 |  | RoutineScheduled | 132-15-0115 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | UV light is not functioning | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
02/27/2023 |  | RoutineScheduled | 179-STS-87475 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
01/31/2023 | Alternative | Pump-Out Only | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim |  | 2000 | [7 empty] | [] | [] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | Dec 30 1899 4:00PM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/06/2023 |  | Routine/Scheduled | 07-172-0325A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. Dbox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | Jan 1 1900 9:00AM
06/30/2023 | Alternative | Reportable Incident | 133-STS-92532 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Replaced UV bulb | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
01/31/2023 |  | RoutineScheduled |  | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
05/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Sand filter zone is not functioning as designed. Emitters not functioning as designed. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
10/10/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 8.040000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 03:45 PM
10/03/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:00 AM
04/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/05/2023 | Alternative | Reportable Incident | 147-09-0053 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Alarm Response - found compressor failed - blown diaphragms. Trash Tank - normal level - recommend pumpout of trash tank. Aeration Tank - normal level - compressor repaired - mixing present. Pump Tank - float sensors, pump and controls operating. Drip Field - headworks serviced. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/07/2023 | Dec 30 1899 7:15AM
11/21/2023 | Alternative |  | 07-113-164 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/21/2023 |  | 4.530000 |  |  | 1.000000 |  |  | Will be sent separately |  | BOD: 4.53 TSS: 1.00 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/21/2023 | 12:00 AM
09/28/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-03-222 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
09/28/2023 | Alternative | RoutineScheduled Component Maintenance | 182-18-0247 | Rockingham | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced pressure gauge Primary septic tank requires pumping | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/13/2023 | 01:07 PM
11/03/2023 | Alternative | RoutineScheduled Component Maintenance | 175-03-0824 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
10/06/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-88745 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Attached Growth Medium" ,"Control Operation" ,"Disinfection" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Control Operation" ,"Disinfection" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. UV bulb replaced. Vent on ax20 was not glued on, cleaned it and glue it in place. Signs of leak on pump tank riser, tested and no water comes in. RECIRC: HL-5, LL-25, OVERRIDE-29. DISCHARGE: HL-2, LL-25, OVERRIDE-16. "R" COUNTS BACK TO ZERO. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
01/11/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
11/29/2023 | Alternative | Routine/Scheduled | 800-STS-14052 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 1 minute every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/29/2023 | Dec 30 1899 11:45AM
08/03/2023 | Alternative | Follow-Up |  | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | UV | 450.000000 | ["Control Operation","Disinfection"] | ["Control Operation","Disinfection"] | N/A | [17 empty] | Follow-up Repair Installed new conduit and electrical wire as recommend during last service event. Replaced failed Salcor 3G UV system with new Norweco AT1500 UV System | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/07/2023 | 09:30 AM
07/17/2023 | Alternative | RoutineScheduled | 009-STS-24182 | Amherst | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Septic Tank | Norweco Singulair | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Norweco. Septic tank 1-2" scum and 16" sludge, Norweco treatment Unit under minimal scum and 6-8" light sludge. Pump tank sludge trace. Good aeration, Pulled and cleaned septic filter, added handle bar to grab and clean. Biofilter was clean. Pump good, aerator good- Float switches good, Alarm good, Alarm on Norweco good. reccomend to not use food dispoal in sink or to clean the septic tank filter more freaquantly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/30/2023 | 09:30 AM
02/10/2023 |  | Reportable Incident | 04-142-0424 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Replaced on/off float in the pump tank and replaced the Clearstream blower | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/13/2023 | 12:00 AM
03/09/2023 |  | RoutineScheduled | 08-197-A3 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Multiflo |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/09/2023 | 12:00 AM
02/07/2023 |  | Pump-Out Only | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/27/2023 | Jan 1 1900 11:30AM
07/13/2023 | Alternative | RoutineScheduled Component Maintenance | SD-04-460 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Pump disconnnect switch at pump tank was off, turned it back on. Pump tank has about 3" of sludge in it. Since pump does not appear to sitting on blocks, it is close to the point where it could pump sludge into the peat. Recommend pump-out. Brush is beginning to encroach a little on edges of drainfield. Recommend cleaning it up a lttle as a precaution. Effluent filter could stand to be cleaned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/18/2023 | 11:45 AM
06/29/2023 | Alternative | Routine/Scheduled | 800-STS-15023 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/29/2023 | Dec 30 1899 2:30PM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | 165-STS-335277 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 | 2500 | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"SludgeScum Accumulation"] | NA | [7 empty] | 09/26/2023 |  | 12.000000 | [5 empty] | Will be sent separately | Inspected | Power was off to system Repaired valve box lid Repaired return line Pumped primary tank Lab sample normal | This AOSS should now return to normal function after having provided the above state routine maintenance | 10/13/2023 | 01:07 PM
12/19/2023 | Alternative | Reportable Incident | 124-STS-2379 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Upon arrival, I found the control panel in alarm condition and system in high level. I put the control panel in TEST mode and confirmed that pumps and floats are functioning properly. I noted signs of surfacing on the dispersal field. While checking the discharge I noted continuous inflow from the vortex filter flush valve indicating that the dispersal field is hydraulically overloaded and back feeding into the system. I checked and confirmed vortex filter was clean. System will remain in alarm condition until the dispersal field dries up following recent rain events. System should correct itself after the field dries up. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/22/2023 | 08:33 AM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 182-07-0054 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | 2 risers installed on inlet of tanks | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
03/10/2023 |  | Initial Visit | 085-STS-33760 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit Trash Tank - normal level Aeration Tank - normal level - mixing present - aspirator serviced. Clarifier - effluent screen serviced. Pump Tank - demand dosed - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | Jan 1 1900 9:30AM
10/17/2023 | Alternative | Routine/Scheduled | 136-11-0090 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal level 3 in of sludge less than 1 in of solids Riser is showing signs of leaking -Recirculation Tank: High level due to discharge plumbing being broke 12 in of suspended solids Tested floats and pump all working as should Pulled and cleaned bio tube filter Vault intact All plumbing intact and pump properly moving water Riser is showing signs of leaking -RSV (Recirculating Splitter Valve): Normal level 3 in of sludge less than 1 in of solids Pulled and cleaned rsv took apart and cleaned internals Male slide broke when pulled replaced on site Otherwise all working properly Riser is showing signs of leaking -Discharge/Pump Tank: Was in alarm when we arrived on site due to pump plumbing broken 4 in of suspended solids Floats are properly working Installed plumbing kit on site Everything working as it should -Media Sheets: Brushed and flushed laterals Sprayed media sheets clean Flushed media module until water ran clear Everything properly working -Distribution Box: Normal level Lines balanced Box is deformed due to ground pressure Lid doesn't fit due to deformity -Drain Field: No signs of surfacing Drain field is halfway in the woods Repairs: -Installed plumbing kit in discharge -Also installed male slide on rsv | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/30/2023 | 10:16 AM
09/27/2023 | Alternative | Reportable Incident | 800-STS-14165 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Owner called due to an alarm. Replaced the UV ballast and replaced the UV light bulb. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/27/2023 | Dec 30 1899 12:00PM
06/06/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced damaged riser & electric box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
06/09/2023 | Alternative | Follow-Up | 150-07-024 | King William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 3.000000 | 2900 | septic tank | Delta Whitewater | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Cloudy |  |  | 20.000000 | [12 empty] | Delta Whitewater maintenance. Vent pipe broken, floats bad, repaired, Serviced aerator, DWW 20% SS. ST- 2" FOG, 3" sludge. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/12/2023 | 09:10 AM
05/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
09/15/2023 | Alternative | RoutineScheduled | 88-197-173 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.000000 | 7.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/03/2023 | 12:00 AM
11/07/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 12:00 AM
12/28/2023 | Alternative | Routine/Scheduled | 136-89-0309 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component Below Normal level due to pumping No filter or riser present Roots intruding lid Discharge/Pump Tank Condition of above Component Notes for above Component Below normal level due to pumping Tested floats and pump all working as should All plumbing intact and pump moving water properly No signs of infiltration Control Panel Condition of above Component Notes for above Component 120 volts coming in All visual and audible alarms functional Pump pulled 8.3 amps All components working as should LPD Condition of above Component Notes for above Component 12lines intact however only one is taking water others are clogged and full of rocks Jetting did not solve problem due to rocks blocking lines Arrived to Jet LPD Laterals Lines completely clogged Investigated Drain filed issues Cut out old gate valve and camered manifold line didn't see any damage to pipe or and obstructions. Installed new gate valve. Informed customer at this point we will need to send this to underground | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/03/2024 | 09:13 AM
11/30/2023 | Alternative | Routine/Scheduled | 136-13-0164 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level Has 3" of solids with 5" of sludge -Discharge/Pump Tank: At normal level Pump and floats working Has 2" of sludge -Aeration: At normal level Aeration working -Air Pump/Blower: Working properly Pulled and cleaned filter -Control Panel: Both panels working properly Discharge pulling 9.40amps Air pump pulling 3.39 -Distribution Box: At grade and at normal level -Drain Field: Showing no signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 03:55 PM
08/25/2023 | Alternative | RoutineScheduled Component Maintenance | 099-10-0043-SP | King George | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Alarm float stock close, replaced. Blower 3.90 amps. Wet area on bottom of drip field. 37 psi on return. HL-6952, SECONDARY COUNTS-679. Recommend to bleach flush field to attempt to improve gallons per minute may be that help to stop the bleeding of drip field. Will send proposal. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 09/01/2023 | 05:07 AM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-19051 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | MicroFast needs pumping. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 08/29/2023 | 03:58 AM
06/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/12/2023 | 02:06 PM
08/30/2023 | Alternative | Routine/Scheduled | 093-14-0106 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | Dec 30 1899 10:45AM
04/17/2023 |  | Routine/Scheduled |  | Frederick | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Pump | Gravity | Discharge | Chlorination | 600.000000 | ["BlowerCompressorAerator Operation","Disinfection"] |  | N/A | [18 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/28/2023 | 11:10 AM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Cloudy | 7.200000 | 23.100000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 10/16/2023 | Dec 30 1899 12:58PM
05/17/2023 |  | RoutineScheduled | 175-10-0330 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 4.000000 |  | Septic Tank #1 | Septic Tank #2 | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation"] | [] | YES |  |  | 6.900000 |  |  |  | Ecoli 816 MPN/100 mL | 05/17/2023 | Sample Chamber | 10.000000 |  |  | 8.000000 |  |  | Attached to this report |  | Septic Tank #1-18"sludge 6"scum/ Septic Tank #2-4"sludge 0"scum/ Advantex Recirc Tank-2"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ Pump out required on Septic Tank #1/ Recirc pump intake cleaned- Media in good condition/ Controls, pumps, floats and alarms functioning properly/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/14/2023 | Alternative | RoutineScheduled Component Maintenance | 177-12-0121-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
09/06/2023 | Alternative | Routine/Scheduled | 041-STS-257977 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Aqua Klear |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/06/2023 | Dec 30 1899 10:01AM
03/09/2023 |  | RoutineScheduled | 175-03-0966 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
05/19/2023 | Alternative | RoutineScheduled | 154-11-0194 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | MicroFast |  | Gravity | Gravity | Discharge | UV | 450.000000 | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Disinfection","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/28/2023 | 12:00 AM
07/27/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
09/12/2023 | Alternative | Routine/Scheduled | 095-STS-5979 | Williamsburg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: - Septic Tank: Found above normal level due to grade issues between septic tank and clearstream tank. 14in of sludge and less than 1in of solids. - Discharge/Pump Tank: Found at normal level, less than 1in of sludge and solids. Tested floats and pump all working as they should. - Aeration: Found at normal level, 3in of sludge and 3in ofsolids. Pulled and cleaned weir and diffuser. High level float working as it should. - Air Pump/Blower: Pulled and cleaned air filter. Air pressure sensor working as it should. - Control Panel: 120 volts audio and visual alarms working as they should. tested timer. Air pump pulled .57 amps Discharge pump pulled 8.4 amps. - Distribution Box: Found at normal level, 3 lines taking water and balanced. - Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | Dec 30 1899 12:58PM
10/03/2023 | Alternative | Initial Visit | 085-STS-34742 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 59.100000 | [7 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream. Changed the diffuser in the Clearstream. The timer is set to 8 minutes every 1 hour 15 minutes. Took initial BOD sample. NOTE - BOD sample was high - system should function properly after service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/03/2023 | Dec 30 1899 10:30AM
12/13/2023 | Alternative | RoutineScheduled | 04-197-A11 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 2 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/13/2023 | 12:00 AM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/25/2023 | Alternative | RoutineScheduled Component Maintenance | 179-09-0177-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Control Operation" ,"Septic Tank Baffles"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Control Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Biotube filter was black as if they have been taking antibiotics but treatment still clear. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
03/24/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/29/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
12/26/2023 | Alternative | RoutineScheduled | 11-184-5001 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
05/11/2023 | Alternative | Routine/Scheduled | 17-174-0051 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Biofilter - petamoss in good condition - raked / turned. Pump Basin - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/25/2023 | Dec 30 1899 11:15AM
05/11/2023 |  | RoutineScheduled | 133 07 0084 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Septic zone Under 1-3"in Scum & 12" Sludge, recirculation zone 6-8 in., Clear Effluent on top, discharge Pump tank 5" sludge, hosed off media, Cleaned Bio-filter, RSV, Brushed and Flushed Manifold, Flushed System until clear, System was pumped 3 years ago. Ran system in test mode, Alarm opperational, Alarm history is corrupt . All Floats opperational. System is operational. recirc pump 206.7hours 40,520 cycles, discharge pump 45.2hours and 834 cycles recorded. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Clearstream | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
05/12/2023 | Alternative | Reportable Incident Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation"] | ["Distribution Pump Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | High level alarm. Observed visual damage to pump motor starter and power supply wire - replaced both. Pump pulling high amps, replaced it with same model (Goulds WE1512HH). Observed corrosion on j-box terminal strip and connectors - replaced them. Pumped level down to normal level and put system back into operation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 06:43 AM
05/22/2023 | Alternative | Routine/Scheduled | 17-174-0185 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Aqua Klear |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/22/2023 | Dec 30 1899 10:00AM
05/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 2.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | ecopod needs pumped out. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
08/15/2023 | Alternative | RoutineScheduled | 136-07-0759 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001302 | Charles | Langford | 2.000000 | 1000 |  |  | Pump | Pressure |  |  |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/25/2023 | 12:00 AM
03/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/06/2023 |  | Routine/Scheduled | {FIPSCode}-STS-2004 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | Jan 1 1900 11:20AM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend keeping vehicles away from drainfield area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/15/2023 | Alternative | Routine/Scheduled | C14-180-0031 | Roanoke City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/15/2023 | Dec 30 1899 10:15AM
03/02/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Pad | UV |  | ["Control Operation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | new blower panel | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
01/16/2023 | Alternative | RoutineScheduled | 115-14-0300 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Septic Tank | Advantex AX20 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Distribution Pump Operation","Effluent Screens"] | NA | Musty | [15 empty] | Inspected | Sludge level 1-2" scum and 10" Sludge in Septic tank zone. 5" Sludge in Recirc tank, Clear Effluent on top. Owners added mulch this year to cover the system and looks good, Biofilter was very dirty and almost fully clogged, we cleaned and flushed the system. Pump is functional, alarm functional, Brushed Manifold, Cleaned RSV and Ran is test mode. System is fully operational at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | 05:30 PM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance | 179-10-0199-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Pressure | Drip | Not Applicable |  | ["SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend pumping the pump tank due to sludge accumulation in the tank. We also recommend installing two new air release valve housings. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
01/12/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 01/12/2023 |  | 20.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
03/02/2023 |  |  | 15-137-0106 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | EZ Treat | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Distribution Pump Operation","Control Operation","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/08/2023 | 12:00 AM
09/20/2023 | Alternative | RoutineScheduled | 115-98-0121 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Septic | Clearstream | Gravity | Gravity | Trenches | Not Applicable | 350.000000 | ["SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/20/2023 | 12:15 PM
05/12/2023 |  | RoutineScheduled |  | Page | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 | 2500 | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["SludgeScum Accumulation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 05/12/2023 |  | 55.000000 | [5 empty] | Will be sent separately | Inspected | Tanks pumped and installer level out transfer pipe Added media scrub to help with sludge on media | This AOSS should now return to normal function after having provided the above state routine maintenance | 06/21/2023 | 03:35 PM
11/02/2023 | Alternative | Follow-Up Component Maintenance | 113-STS-22131 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed new checkvalve & union in the pump tank. Replaced broken cleanout plug. Excavated by hand and resealed leaking pump tank riser. Continue to recommend removing leaf litter and dead grass from dispersal area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
01/27/2023 |  | RoutineScheduled |  | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Rappahannock-Rapidan | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/29/2023 | 01:20 AM
02/28/2023 |  |  | 085-STS-35367 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
05/13/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 2.000000 | 2000 | Orenco Advantex |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 10" of accumulated solids in septic tank. Cleaned septic tank filter. 12" of accumulated solids in septic tank located near treatment unit. Flushed treatment unit spray manifold. Tested floats, pump and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/29/2023 | 07:03 PM
07/06/2023 | Alternative | RoutineScheduled | 18-100-0472 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 08:35 AM
06/14/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-2622 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | Dec 30 1899 9:55AM
09/06/2023 | Alternative | Reportable Incident | 166-12-054 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. The timer is set to 8 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/06/2023 | 01:00 PM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance | SD-04-459 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Control Operation" ,"Distribution Pump Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Advised owners to add about 6" of topsoil at the end of the top trench because about the last 4" of the corrugated pipe is showing. Dirt should be blended in all directions to prevent ponding. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:19 PM
05/02/2023 |  | Follow-Up | 177-15-0222-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to disassemble components in recirc tank and assist pumper with proper pump out. Reassembled components in recirc tank and all tanks were refilled with a water truck. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/05/2023 | 07:56 AM
05/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/22/2023 | Alternative | RoutineScheduled | 171-05-0559 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | [16 empty] | Inspected | Septic tank 1" scum and 12 " sludge, Pump tank no scum and 5-6" sludge. Records 1115.22 hr vs 1073.49 hours equals 41.73 hours run time, and 80384 vs 79,290 cycles equals 1,094 cycles this past year. Opened up and turned all Peat in 4 pods which was looking ok for age. Water Draining, cleaned biofilter, reccomend to add proper riser to seal the septic tank access and provide lid and prevent rain water infiltration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
10/11/2023 | Alternative | RoutineScheduled | 04-197-A4 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | Musty | Clear | 5.500000 | 4.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
05/04/2023 | Alternative | Routine/Scheduled | 10-174-0057 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/04/2023 | Dec 30 1899 8:45AM
06/19/2023 | Alternative | RoutineScheduled | 175-09-0285 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-6"sludge 6"scum/ Microfast-6"sludge 0"scum/ Pump Tank-0" sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms function properly/ Counts: Pump-1521 ETM-43h 16m/ High-4 On-1m 42s Off-4h Dose 70 gal./ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/20/2023 | Alternative | Routine/Scheduled | 2017-143-0061 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Trash Tank - normal level Aeration Tank - normal level - mixing present - aspirator pulling high amperage and overheating !!! - replacement aspirator & controls ordered. Clarifier - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Drip Field - headworks serviced - found vacuum breaker broken and leaking. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | 12:30 PM
05/11/2023 | Alternative | RoutineScheduled | 181-08-0045 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The blower filter was cleaned. The controls were operating as designed. There were no visible leaks in the leech field. Trees had to be trimmed to be able to get to get to the tanks. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/06/2023 | 10:55 PM
04/11/2023 |  | RoutineScheduled | SWP-98-140 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | 4/6/23 Attempted to complete annual insepction, but system was in high level. Cleaned very dirty pump intake and backwash valves to restore proper flow rate. 4/11/23 Completed annual inspection. Pump intake already starting to clog again. Installed Simtech stainless steel pump screen. Reminded owner that control panel was very old and recommended to be proactively replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
09/28/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
04/04/2023 |  | RoutineScheduled | 175-04-0320 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Puraflo peat needs replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 12:48 PM
08/29/2023 | Alternative | RoutineScheduled Component Maintenance | 179-17-0475-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Norweco Singulair ATU | none | Gravity | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
03/20/2023 | Alternative | RoutineScheduled | 154-07-0108 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | MicroFast |  | Gravity | Gravity | Trenches | Not Applicable | 500.000000 | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 12:00 AM
05/23/2023 | Alternative | Reportable Incident | 073-STS-99820 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | COSS - Maintenance - GMP2018-02 Replaced existing dbox with new 8 port concrete DBox. Spliced to existing conveyance line. Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 09:30 AM
03/28/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"BlowerCompressorAerator Operation"] | ["Disinfection" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Microfast needs pumping. UV Bulb changed while on site. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/15/2023 | Jan 1 1900 7:20PM
07/21/2023 | Alternative | RoutineScheduled | 17-165-0027 | Northampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1250 | Septic Tank | Delta Envir. DF | Gravity | Pressure | Trenches | Not Applicable | 450.000000 | ["None"] | ["None"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | 11:00 AM
02/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/22/2023 | Alternative | RoutineScheduled | 99-142-0285 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/26/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Fast | Pump | Pressure | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | 3" of Scum, 6" of sludge in septic. 6" of loose in fast side. 0 in pump tank. run time 22:44:57 h 150 doses Leak in the header line at the field. It was repaired and verified on 2/2/25. return pressure at 35 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | 12:00 PM
03/30/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Rejected | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We continue to recommend moving the fence crossing the drip dispersal area to run outside of the entire drip field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
01/31/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | tank needs pumped out and a new uv light bulb and cord needs installed burnt out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
07/11/2023 | Alternative | Routine/Scheduled | 15-142-0227 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1250 | EcoPod |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | NO | [17 empty] | Air filter cleaned. System checked. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | Dec 30 1899 10:01AM
03/22/2023 |  | Routine/Scheduled | 2004-143-0288 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Puraflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/22/2023 | 12:56 PM
02/14/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
12/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 12/11/2023 | Sample Chamber | 6.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Distribution box was uncovered and the dialflows were adjusted | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
01/18/2023 |  | Routine/Scheduled | 041-STS-257820 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/18/2023 | Jan 1 1900 2:43PM
10/30/2023 | Alternative |  | 033-11-0017-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/27/2023 |  | Routine/Scheduled | 234-16-307 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/27/2023 | Jan 1 1900 12:10PM
01/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
11/08/2023 | Alternative | RoutineScheduled | 109-15-0058 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Aqua Klear |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] |  | Musty | [15 empty] | Inspected | Sludge levels-Trace scum layer, 6" Sludge in Septic tank - Treatmeant tank 24" sludge at dischagre -- Pump Tank 8-10" Sludge, cleaned air filter. Pump Run time 200hr1min vs 172hrs 47 min last year & 3086 vs 2637 cycles, High level 9 Secondary count 143 Power failure 37. Goulds effluent pump- Runs when called. Clear Effluent on top. cleaned air filter. Flushed system. Drip Drain field appears fine no leaks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
01/18/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/06/2023 | Alternative | RoutineScheduled | 171-99-0577 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1000 | AK500FF Aquaklear |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 04:30 PM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 2.000000 |  | Bio Barrier | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced blower panel | This AOSS should now return to normal function after having provided the above state routine maintenance | 08/23/2023 | 06:57 AM
01/03/2023 |  | Reportable Incident | 124-STS-2379 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 44.000000 |  | 6000.000000 | [5 empty] | Owner called due to smell from the tank and the septic tank sloshing - the filter in the Clearstream tank was stopped up. Serviced system. Checked the pump, panel, and floats (ok). Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the UV light bulb and replaced the UV ballast. The timer is set to 3 minutes every 1.5 hours. Took BOD and Fecal samples. NOTE : BOD and Fecal were high - system should function properly after service. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/03/2023 | Jan 1 1900 11:30AM
09/08/2023 | Alternative | Reportable Incident | 159-11-002 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | -Customer stated they had water standing in yard Found 1" of clear water standing in yard Opened system and found clear water pouring through risers Peat modules were flooded but the inspection port for Peat modules was at normal level Checked to see if well was running continuously and it was not. Couldn't find source of water Need to pump system out and turn pump off to rule out that waters not coming from system customer approved pumping. - Customer later stated that toilet was running for 5 days straight causing water to pool. Customer fixed it and water is no longer pooling | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | 08:49 AM
10/28/2023 | Alternative | RoutineScheduled | 109-10-0152 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 2.000000 | 3000 | EcoPod |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | 3rd Quarter 2023 inspection. Grease trap - First section - 1" crust, 13" of solids on bottom, Second section - 0" crust, 12" of solids on bottom. Septic Tank - skim crust, 14" of solids on bottom. EQ tank - 0" crust, 12" of solids on bottom. Denitrification tank- 0" crust, 0"of solids on bottom. Treatment Unit - 0" crust, 10" of solids on bottom. Clarifier - 1" crust, 16" of solids on bottom. Discharge tank - 0" crust, 10" of solids on bottom. Meter Reading - 314220 - 40,830 gallons since 7-15-2023. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/09/2023 | 07:03 PM
06/13/2023 |  | RoutineScheduled | 175-08-0324 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
04/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/07/2023 | Dec 30 1899 7:43AM
01/20/2023 |  | RoutineScheduled | 01-120-0529A | Chesterfield | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 3300 | 1000 | 1300 | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation","Control Operation"] | YES | None | Clear | 6.000000 |  | 6.000000 | [13 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | Jan 1 1900 1:30PM
01/06/2023 | Alternative | RoutineScheduled | SD-10-109 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity |  | Chlorination |  | ["Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | ["BlowerCompressorAerator Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | There was approximately 8" of standing water in the sand filter. As we have discussed previously, it may be advisable to install new sand. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
01/23/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
01/07/2023 |  | RoutineScheduled | 17-100-0156 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | AQUASAFE |  | Pump | Pressure | Mound | UV | 600.000000 | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | [17 empty] | Pumped Out | REPLACED BLOWER ALARM, PUMPED SEPTIC TANK AND REPLACED UV LIGHT UNIT | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/19/2023 | 12:20 PM
06/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
10/06/2023 | Alternative |  | 154-06-0160 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
04/11/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Recirculation Pump"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Ez Treat pump is bad and system is in alarm and full. Tank needs pumped out and pump replaced. The water meter for drip field is not operational and needs to be replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 12:48 PM
09/19/2023 | Alternative | RoutineScheduled | 181-10-0056 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 4.000000 | 4000 | Ecopod | Biomicrobics MicroFAST | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [7 empty] | 09/19/2023 | Pump Chamber | 13.100000 |  |  | 13.200000 |  |  |  |  | Checked and cleaned all filters. Pumps functioning properly. Panel boxes all functioning properly. System did not need to be pumped. No apparent leaks in system or drain field area. Lids were all properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/06/2023 | 10:05 AM
04/26/2023 |  | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 01:40 PM
05/03/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] |  | NA | Musty | Black | [13 empty] | Will be sent separately | Inspected | D80 compressor needs replacing. Delta ATU needs pumping | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | Dec 30 1899 12:05PM
02/10/2023 |  | Pump-Out Only | {FIPSCode}-STS-5438 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/10/2023 | Jan 1 1900 8:00AM
02/02/2023 |  | RoutineScheduled | 181-04-0129 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation"] | [] | NA | [17 empty] | The system did need to be pumped, however I have to wait until it needs to be dry to be able to pump this system. The blower filter was cleaned. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/25/2023 | 12:45 PM
06/20/2023 | Alternative | Routine/Scheduled | 196-12-146 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 5.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 04:20 PM
07/13/2023 | Alternative | Pump-Out Only | 136-17-0374 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Pumpout of Clearstream treatment system as recommended during last service visit. Refilled with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 06:45 AM
04/05/2023 |  | RoutineScheduled | 94-184-5003 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation","BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/05/2023 | 12:00 AM
03/30/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
06/02/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-88943 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Auxiliary Filter" ,"Attached Growth Medium"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
06/09/2023 | Alternative | Routine/Scheduled | 157-13-0162 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the buzzer. The Clearstream tank should be pumped and cleaned the septic tank needs to be pumped. The drainfield was dry - try and keep the grass cut down. The timer is set to 2 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/09/2023 | 10:30 AM
01/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
01/04/2023 |  | Routine/Scheduled | 228-03-0301 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/04/2023 | Jan 1 1900 11:25AM
08/30/2023 | Alternative | Routine/Scheduled |  | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX | None | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. PUmp Basin - float sensors, pump and controls operating. BioFilter - Peatmoss recently replaced - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | 09:30 AM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2024 | Dec 30 1899 5:34PM
08/24/2023 | Alternative | RoutineScheduled | 195-STS-26571 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | EZ TREAT |  | Pump | Pressure | Discharge | UV | 200.000000 | ["Attached Growth Medium","Disinfection","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Disinfection","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/24/2023 | 12:00 AM
12/20/2023 | Alternative | RoutineScheduled | 08-120-0097R | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chesterfield | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [18 empty] | Replaced Bacteria catalyst, and blower. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
08/30/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Microfast needs pumping. Needs UV bulb, chord & glass housing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 09/15/2023 | Dec 30 1899 2:41PM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance | 061-19-147 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
11/07/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | 12:35 PM
02/24/2023 |  | RoutineScheduled | 075-STS-34602 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/25/2023 | 12:00 AM
04/05/2023 |  | RoutineScheduled | 179-STS-89934 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. No water infiltrating at this time. damaged lid on pump tank (not to bad) still ok. DISCHARGE: HL 2, LL 12, OVERRIDE 1. RECIRC: HL 2, LL 13, OVERRIDE 12. "R" counts back to zero. 1 missing valve cover lid and 1 broken. will give price for replacing lid next visit (24" tuff -tite lid) | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
03/25/2023 |  | RoutineScheduled | 133 17 0347 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 2000 | EZ Treat |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | [18 empty] | First quarter 2023 inspection. Cleaned recirculation tank filter. Tested floats, pumps and alarm. Spray heads spraying very good. Restaurant is on a regular grease trap pump out schedule. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/07/2023 | 07:03 PM
05/11/2023 |  | RoutineScheduled |  | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | BioMicrobics Micro Fast to Drip |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Control Operation"] | ["Auxiliary Filter","Control Operation"] | NA | [16 empty] | Inspected | Initial inspection of exhisting system, Septic Tank ? scum-no access (Try to minimize Fat oil Grease antibiotic chemicals and cleaners input in the system), 12" sludge - does not need pumping this year, Fast side port Treatment 12" sludge, good aeration, cleaned air filter-Blower Alarm and Pump Alarm tested operational, Drainfield Unremarkable- owner cuts it over- System was pumped last month- Issue with short cycling, Found pump time sec to seconds instead of minutes and corrected the setting which is allowing the pump to function normally. Pump cycles 229 Pump run time 3hours and 30 min. High level 18, low level 20, override cycles 7, timer float events 6785, Pow failure 27, time in service 22378hrs 50 min | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/30/2023 | 09:30 AM
04/18/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | mow drainfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/22/2023 | 11:15 AM
04/05/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/17/2023 | Jan 1 1900 12:44PM
01/25/2023 |  | Routine/Scheduled | 228-16-0440 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/25/2023 | Jan 1 1900 11:10AM
03/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Clearstream | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
04/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | drain line from modules to pump chamber had broken. DSS repaired. System appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/23/2023 | Alternative | Pump-Out Only | 157-04-281 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Dispersal System Operation","Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Dispersal System Operation","Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Pumpout of AOSS as recommended during last service visit. Refilled aeration tank with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 09:00 AM
11/06/2023 | Alternative | RoutineScheduled | 145-03-0066 | Highland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | RetroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | YES | [17 empty] | The system did not need to be pumped. The spin filter and blower filter were both pulled and cleaned. The timer float was not functioning properly at the time of inspection so the float was replaced. The controls were operating as designed. There were no visible leaks in the drip field. The effluent was returning to the pump tank from the drip field so the drip field was operating as designed. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/27/2023 | 09:50 PM
03/22/2023 | Alternative |  | 150-17-0001 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | microfast | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
01/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
02/01/2023 |  | RoutineScheduled | 175-17-0008 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/13/2023 | 08:47 AM
07/13/2023 | Alternative | RoutineScheduled | 043-08-0109 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | septic | LPD | Pump | Pressure | Trenches |  |  | [] | ["Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | 0 scum, 2" sludge. Loose sediment in pump tank. pump and floats working everything is good | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 01:30 PM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/17/2023 |  |  | SWT-04-741 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
04/13/2023 |  | Pump-Out Only | 18-137-0074 | Goochland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | EcoPod |  | Pump | Pressure | Drip | Not Applicable |  | SludgeScum Accumulation | SludgeScum Accumulation | N/A | [16 empty] | Pumped Out | Septic tank pumped out and scum removed from top of treatment unit. Found the grinder pump in alarm, pump not working. Replaced pump. System should return to normal operation | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/05/2023 | Jan 1 1900 10:08AM
12/01/2023 | Alternative | Follow-Up Component Maintenance | SD-02-222 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank and pump tank pumped out by others prior to peat replacement. Degarded peat was removed by hand and new peat was installed. Degraded peat was disposed at Spotsylvania Refuse. Peat was purchased from Driller Services. Re-plumbed pump piping for easy access per code. Replaced bottom float. Added proper float tree. Replaced 8 dial-a-flows in 1st original distribution box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
10/25/2023 | Alternative | RoutineScheduled | 182-04-0268 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | [17 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/31/2023 | 12:00 AM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/16/2023 |  | RoutineScheduled | 109-08-0152 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | YES | [16 empty] | Inspected | Realestate inspection - Sludge level minimal, little usage since the system was pumped out. Very Clear Effluent. Owners added mulch to cover the system and looks good, Biofilter was cleaned. We tested the float switches and found one bad float switch. We returned on the 18th and replaced the bad float switch. we flushed the system and ran in test mode. Adjusted the float height based on company representative. Pumps are functional, alarm functional, Manifold clean, RSV clean and Ran is test mode. System is fully operational at this time. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/31/2022 | 09:30 AM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/02/2023 | Alternative | RoutineScheduled Component Maintenance | 175-08-0497 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Wiped clean interior of control panel and treated the seals. Filter element for blower canister filter replaced. Air pre-filter cleaned. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/08/2023 | 06:43 AM
03/08/2023 |  | RoutineScheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Raised spin clean filter and pumped all tanks | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
09/30/2023 | Alternative |  | 001-STS-92314 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [18 empty] | See attachment | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 12:00 AM
11/13/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 11:30 AM
06/21/2023 | Alternative | Routine/Scheduled | 234-14-296 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | Dec 30 1899 10:13AM
04/11/2023 |  | RoutineScheduled | 179-14-0236-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
05/31/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Uncovered distribution and removed tree roots. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/15/2023 | Dec 30 1899 12:05PM
05/31/2023 |  | RoutineScheduled | SP-05-117 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Air filter will need replacement next year. Most likely septic tank will need pump out next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
03/02/2023 |  | RoutineScheduled | SWP-05-360 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"SludgeScum Accumulation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend scraping the Advantex textile sheets to remove sludge buildup and pumping the Advantex tank afterwards. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
09/17/2023 | Alternative | RoutineScheduled | SD-05-543 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1000 | septic | multiflo | Gravity | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/17/2023 | 01:55 PM
02/10/2023 |  | RoutineScheduled | SWP-02-606 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 2-2 | 0-2 | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/10/2023 | 12:00 PM
03/08/2023 |  | RoutineScheduled | 179-07-0104-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
05/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
07/13/2023 | Alternative | RoutineScheduled Component Maintenance | {FIPSCode}-STS-10379 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Outstanding proposal to repair sand filter tanks from roots tree growing in. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/18/2023 | 11:45 AM
06/07/2023 | Alternative | Pump-Out Only | 08-160-0240 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [17 empty] | Pumped Out | - pumped/cleaned pump chamber so maintenance provider can complete repair | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/08/2023 | 12:00 AM
01/10/2023 | Alternative | RoutineScheduled | 061-16-250 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation"] | ["Control Operation" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Biweekly inspection. Also inspected lift station for Ross Industries: pump #1 5.27 amps 2496.2 hrs, pump #2 6.25 amps 1026.9 hrs; Tanncor: pump #1 8.25 amps 854.6 hrs, pump #2 30.15 amps 171.4 hrs (impeller was stuck at first, amp draw dropped to 8.62 amps); and the new terminal (ground saturated near the treeline on road coming in, possible broken air release valve). Microfast to drip system - in the past 21 days, the system pumped an average of 1553.4 gals/day at 374.9 gals/cycle (avg.) for a total of 32,622 gallons. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
05/17/2023 |  | RoutineScheduled | {FIPSCode}-STS-15876 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Control Operation","Dispersal System Operation","Disinfection","Level Sensor Operation"] | ["Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation"] | NA | Musty | Clear | 6.800000 |  |  | 1.500000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/20/2023 | 12:00 AM
09/21/2023 | Alternative | Follow-Up Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Blower connected. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/16/2023 | Dec 30 1899 12:58PM
01/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
05/19/2023 |  |  | 2014-143-0148 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/02/2023 | 12:00 AM
02/23/2023 |  | RoutineScheduled | SP-05-205 | King George | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Distribution Pump Operation" ,"Attached Growth Medium"] | ["Distribution Pump Operation" ,"Attached Growth Medium"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | The peat in the Puraflo modules is no longer providing treatment. Owner has had a conventional drainfield designed by an AOSE to replace this system. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/03/2023 | 08:19 AM
01/18/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [7 empty] | 01/18/2023 |  | 15.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
05/25/2023 | Alternative | RoutineScheduled | 181-06-0267 | Rockbridge | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Central Shenandoah | Valley Soil & Environmental Consulting, LLC | 1942001218 | John | Lam | 1.000000 | 1000 | Septic tank |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["Distribution Pump Operation"] | [] | NO | [17 empty] | Semi-annual inspection of LPD #1; HD ID 181-04-0275. The LPD pump and control panel are not operational and will require replacement. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/01/2023 | 12:00 AM
02/02/2023 |  | Routine/Scheduled | PPIE-A6SRL5 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Microfast |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | Jan 1 1900 1:30PM
11/13/2023 | Alternative | RoutineScheduled | 101-07-0405 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 1.000000 | 1500 | Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [14 empty] | Inspected | Sludge/Scum Accumulation - Septic 3", ATU 3" Blower Amperage - 3a | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 09:00 AM
01/30/2023 |  | RoutineScheduled |  | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
03/30/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/17/2023 | 12:44 PM
08/02/2023 | Alternative | Routine/Scheduled |  | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Mound | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump, Effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. LPP Pad - no indications of surfacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/03/2023 | 07:45 AM
05/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Aerator was not functioning upon arrival. It was replaced and is functioning as designed at this time. The effluent filter was very clogged and causing a high-level in the septic tank and possibly coming out the riser. Filter was cleaned and the lever returned to normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/30/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20 |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter","Control Operation"] | ["Auxiliary Filter","Control Operation"] | NA | [17 empty] | Annual inspection. New homeowner. 15" of accumulated solids in septic tank. 6" of solids in discharge pump tank. Cleaned recirculation pump solids basket filter. Flushed treatment unit spray manifold. Sprayed off treatment unit sheets. Replaced recirculation pump middle float. Removed large amount of tree roots from discharge pump tank. Tested floats, pumps and alarm. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/23/2023 | 07:03 PM
11/16/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/16/2023 | Dec 30 1899 1:00PM
01/16/2023 |  |  | 107-16-0161 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Auxiliary Filter"] | ["Effluent Screens","Auxiliary Filter"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/08/2023 | 12:00 AM
12/26/2023 | Alternative | Routine/Scheduled | 150-19-0061 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Septic Tank Condition of above Component Notes for above Component Water level normal. Inlet tee appears to be intact. Flushed and cleaned effluent screen. Not due for pump out Discharge/Pump Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. Noted surfacing next to tank and found that it is the result of a separated fitting with theories main leading to dispersal field. Homeowner gave approval and force main was repaired while on site. Checked and confirmed no surfacing issues afterwards. Peat Moss Condition of above Component Notes for above Component Raked and tilled peat moss. Peat moss is in good condition. Tipping bucket is broken. Drain Field Condition of above Component Notes for above Component Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2024 | 08:18 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend keeping vehicles away from drainfield area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/12/2023 | Alternative | Routine/Scheduled | 550-STS-6407 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | Dec 30 1899 11:30AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/03/2023 |  | Reportable Incident | 175-18-0347 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | High level alarm has been on several days. System is getting rid of water automatically. The problem is too much water coming into the tanks: active groundwater infiltration observed at the bottom riser joint, outlet end of pump tank, and an unexplained slow but steady trickle of water flowing through the sewer line (owner to check all toilets). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 09:31 AM
11/02/2023 | Alternative | Routine/Scheduled | C800-17-0392 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | EZ Treat Sandfilter |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | Dec 30 1899 9:55AM
11/02/2023 | Alternative | Routine/Scheduled | 093-03-0270 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | Dec 30 1899 1:00PM
05/30/2023 |  | Reportable Incident | 228-04-1025 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/30/2023 | Jan 1 1900 7:30AM
10/25/2023 | Alternative |  | 033-06-0309-SR | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/26/2023 |  | Follow-Up |  | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Payment | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001682 | Frank | Hogan | 2.000000 | 14900 | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Recirculation Pump"] | ["Dispersal System Operation" ,"Recirculation Pump"] | NA | Musty | Cloudy | 6.400000 | [12 empty] | Will be sent separately | Inspected | Tracking plant and dose adjustments week ending 3-26-23 3-16-23 Adjusted drip to only dose zones 1,3,5, & 6 reduced run time to provide smaller doses 3-17-23 Discharge tank alarm incresed run time 3-18-23 Still in alarm arrived to check site all tanks nearly full light overflow through conduit in control room. Limed area 3-18-23 Pumped 4 loads out of system increased run time on discharge tank 3-19-23 Recirdc tank in oveeride alarm, site visit no issuies, out of alarm by 3 pm. 3-22-23 Site visit with Peter Brooks to assess plant and optiosn for drainfuield. 3-24-23 Working with Steve Barry at Aqwa to assess plant performance, advisewd to go to 7 day trend and not 21 day. Adjusted recric ration to 3:1. Sent panel log in to steve so he can mange from his offciue when needed. Steve discvered that the Recirculation Pumps that show as 30 gpm on the plans are actually 75 GPM Pumps. This allows moving the recirc rate up to 4.5:1 No alarms No adjustments 3-25 & 3-26 All Monitoring wells in compliance with the exception of TN of 6.11 in DG-5 N in excess was picked up during intital tests 2015 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/17/2023 | 01:00 PM
04/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
12/28/2023 | Alternative | RoutineScheduled Component Maintenance | 175-16-0244 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | 01:58 PM
04/08/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/09/2023 | 12:00 AM
03/02/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
01/16/2023 | Alternative | Reportable Incident | 119-STS-101627 | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | None | None | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | COSS - Maintenance - VDH Permit - 159-22-0166 Primary septic tank pumped empty, crushed in place & abandoned. Installed new 1000g concrete mid-seam septic tank. Installed new bull run valve between existing gravity fed absorption field and pump station. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/17/2023 | 07:00 AM
06/09/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-03-323 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
07/14/2023 | Alternative |  | 033-10-0107-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
10/04/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/30/2023 |  | RoutineScheduled | 153-STS-20270 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["Disinfection","BlowerCompressorAerator Operation"] | ["Disinfection","BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic-4"sludge 3"scum/ Microfast ATU .5-3"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working properly, ATU color and odor normal/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-1236 ETM-225h 3m/ High level-12/ Water meter-00,089,668.6/ Zone counts: zone1-567 flush-53 zone2-561 flush-55 Drip rates : Both zones-5gpm / On-11m 42s Off-4h 48m/ UV-Light needs replacement, sleeve cleaned and uv-light bulb replaced during inspection/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
10/16/2023 | Alternative | RoutineScheduled | 085-STS-33446 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:00 AM
09/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Henrico | C & E Mechanical Corporation | 1942001339 | Louis | Timberlake | 1.000000 | 500 | AquaKlear |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | ["Septic Tank Baffles","SludgeScum Accumulation","Level Sensor Operation","Distribution Pump Operation","Dispersal System Operation","Control Operation"] | YES | [16 empty] | Pumped Out | Recommend more frequent pump outs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 01:45 AM
05/18/2023 |  |  | 2005-143-0129 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Puraflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/02/2023 | 12:00 AM
06/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump chamber concrete lid was replaced. Recommend pumping ATU and possibly the pump chamber as there is some scum. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/30/2023 | Alternative | RoutineScheduled | 175-04-0597 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Routine Annual Washed pump, reset floats a bit, probably need pumping next year based on scum accumulation levels | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 12:00 AM
10/09/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 8.350000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 03:45 PM
04/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | drain line from modules to pump chamber had broken. DSS repaired. System appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/19/2023 |  | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | 10:27 AM
03/14/2023 |  | Routine/Scheduled | 550-STS-6767 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | Jan 1 1900 2:00PM
10/18/2023 | Alternative | RoutineScheduled | 019-STS-27296 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Effluent filter installed or maintained | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Drip |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | Alarm on Septic system, found water had flooded the junction box wire nuts causing a short on 2 of the control floats. Repairs these and retested and floats responed correctly. Upon this repair discovered a broken union in the recirc tank. We scheduled to return and repair this line tomorrow. It was not leaking on the ground and has had little occupancy since the issue developed after rental season. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/21/2023 | 09:30 AM
09/08/2023 | Alternative | Routine/Scheduled | 800-07-0234 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Ecoflo |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None |  | 7.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | Dec 30 1899 10:17AM
08/25/2023 | Alternative | Routine/Scheduled |  | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - recommend pumpout - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/29/2023 | Dec 30 1899 1:00PM
06/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/24/2023 | Alternative | RoutineScheduled | 2030-96-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Control Operation","Dispersal System Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation","Septic Tank Baffles"] | ["Control Operation","Dispersal System Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation","Septic Tank Baffles"] | YES | Musty | Clear | 7.900000 |  |  | 1.900000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/27/2023 | 12:00 AM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 08/31/2023 |  | 9.000000 | [5 empty] | Will be sent separately | Inspected | Lab Sample Normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
12/18/2023 | Alternative | Routine/Scheduled | 157-13-0060 | Mathews | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Type of System Alternative Type of AOSS System Clearstream with uv to drip Septic Tank Condition of above Component Notes for above Component Found above normal level due to bad timer. 12in of sludge and less than 1in of solids. Pulled and cleaned filter. Riser is broken and below grade Discharge/Pump Tank Condition of above Component Notes for above Component Found above normal level due to bad timer. Less than 1in of sludge and solids. Tested floats and pump. All working but have met life expectancy. Pump pulled 8.3 amps Riser showing signs of leaking. Pressure gauges have met life expectancy Uv, salcore uv is not working. Bulb burnt out. sleeve foe uv is torn.,uv has met life expectancy Aeration Condition of above Component Notes for above Component Found above normal level due to bad timer. Found 10in of sludge and less than 1in of solids. High level alarm float working but aged. Diffuser has holes drilled in it Air Pump/Blower Condition of above Component Notes for above Component Air pump is running but not moving air. Air pump has met life expectancy. Air pressure sensor working as it should. Pulled one side of air pressure sensor so the alarm, is not active. Left Air pump breaker off. Control Panel Condition of above Component Notes for above Component 120 volts, audio and visual alarms working as they should. Replaced timer onsite. Panel has met life expectancy. Romex wire in the panel. Customer stated that there are underground splices kit the the conduit from previous work. Drip Field Condition of above Component Notes for above Component No signs of surfacing in drainfield area. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/21/2023 | 02:19 PM
08/02/2023 | Alternative | Routine/Scheduled | 085-STS-33180 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine service Trash Tank - normal level Aeration Tank - normal level - mixing present - aspirator serviced. Clarifier - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. DBox - plastic - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/03/2023 | Dec 30 1899 7:00AM
03/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Valve box riser cover needs to be replaced as it is broken. Low pressure does not appear to be functioning as designed. Homeowner is contacting company for repairs. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/04/2023 | 06:02 AM
01/04/2023 |  | Routine/Scheduled | 550-STS-6474 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 |  |  |  | 01/24/2023 |  | 3.000000 |  | 250.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 9:45AM
05/22/2023 |  | Reportable Incident | 179-14-0067-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system alarming due to clogged bio tube filter. Cleaned filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
11/11/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex AX20RT |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. 0" of solids in recirculation portion of treatment unit. 0" of solids in discharge portion of treatment unit. Excellent treatment quality. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 07:03 PM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/13/2023 |  | Routine/Scheduled | 234-18-097 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/13/2023 | Jan 1 1900 12:15PM
10/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Zones 2 and 3 a little soggy across nearly every run about 5' from supply manifold. Reduced run time by 1 minute for zones 2 & 3. Treatment quality looks good. Nothing to suggest that atu is suffering from infiltration. No new high level alarms recorded in control panel since last December. High level count now at 10 (after testing). Timer enabler float was stuck on, replaced it. Atu is getting close to needing pumped. Advised owner to schedule it around the holidays to increase capacity when guests are over. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
12/14/2023 | Alternative | Reportable Incident | 159-04-300 | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Ecoflow. System has been alarming. When we arrived he tank was at normal level. Found the on/off float and panel were failing. Jim approved to replace the panel and both floats. Informed him about the sink hole between the pump chamber and Peat chamber. We dug through the Peat and found a hole that the dirt is coming through. He wants Zach to give him a quote to fix and or replace the chamber. The panel has a 230v feed powering the pump and control and Jim will not be here to be able to turn off power when we replace the panel Repairs 12/15: -Installation of a Orenco Control Panel to control system operations -Installation of 2 new Floats | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/18/2023 | 09:55 AM
05/03/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/25/2023 | Alternative | RoutineScheduled Component Maintenance | 175-12-0276 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 | 3600 | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Septic Tank is 1500 gallons. Pump Tank is 1500 gallons. Effluent Pump is Aerometor T-25-100 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
10/19/2023 | Alternative | Reportable Incident | 136-11-0090 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm call: -Advantex ax20. Discharge in high level and alarming. Discharge pump was pulling 70+ amps and tripping the breaker. Brandon approved to replace the discharge pump with a liberty 280. Got the tank pumped down to normal level | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 12:47 PM
05/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Ecoflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | filter was clogged | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
08/01/2023 | Alternative | Initial Visit | 800-STS-14662 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm - owner had a running toilet. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 2 minutes every 2 hours. Did not take BOD and Fecal samples due to the system being flooded at time of service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/01/2027 | Dec 30 1899 10:15AM
05/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/25/2023 | Alternative | Routine/Scheduled | 157-06-185 | Mathews | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Serviced the Eco-flo. Pump, alarm, and panel all good. The septic tank needs to be pumped out. The peat needs to be replaced and it is full of roots. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/25/2023 | 12:00 PM
07/27/2023 | Alternative |  | 10-197-A2 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/27/2023 |  | 18.900000 |  |  | 8.530000 |  |  | Will be sent separately |  | BOD: 18.9 TSS: 8.53 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | 12:00 AM
03/27/2023 |  | RoutineScheduled | 099-17-0091 VU | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions | 2705163102 | Michele | Ware | 2.000000 |  | Puraflo | [6 empty] | [] | ["Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/12/2023 | 12:00 AM
11/14/2023 | Alternative | Routine/Scheduled | 02-0382A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | [15 empty] | Replaced RSV | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | Dec 30 1899 3:00PM
06/02/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1875 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/01/2023 | Alternative | RoutineScheduled Component Maintenance | 179-07-0031-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Small root coming into 1 pod through small crack on wall, removed root and wire wheel it and sealed (pod farther from home). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
07/26/2023 | Alternative |  | 02-125-301 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/26/2023 |  | 8.500000 |  |  | 8.800000 |  |  | Will be sent separately |  | BOD: 8.50 TSS: 8.80 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/26/2023 | 12:00 AM
08/16/2023 | Alternative |  | 04-142-0400 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Recirculation Pump","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/29/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Auxiliary Filter"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Annual inspection. Bottom float switch (RO) was stuck on again. Replaced it under warranty with a different brand of float. Changed setting to have tubing flushed every 15 cycles instead of 20 (owners don't use much water). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
06/02/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | 12:00 AM
03/30/2023 |  | RoutineScheduled |  | Warren | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 1.000000 |  | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Scum and 8" of sludge in septic tank. Pump. alarms are working. Field is good and dry. The peat moss in all Puraflo pods needs replaced. All pods are ponding and peat is bad. Metal crossmembers in pods are rusted and falling apart. Recommend that the pods and peat moss are changed or the system is upgraded. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/04/2023 | 08:30 AM
03/06/2023 |  | RoutineScheduled | 10-125-090 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Pump | Pressure | Mound | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Distribution Pump Operation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","Effluent Screens","Dispersal System Operation","Control Operation","Auxiliary Filter"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/06/2023 | 12:00 AM
05/09/2023 |  | Routine/Scheduled | 11-142-0111 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Biofilter - 4 modules - Peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | Jan 1 1900 1:00PM
03/28/2023 |  | RoutineScheduled | 175-13-0443 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 04/27/2023 | Sample Chamber | 9.000000 | [5 empty] | Attached to this report |  | Septic Tank-12"sludge 6"scum/ Microfast-18"sludge/ Pump Tank-4"sludge/ Septic Microfast Tank requires pump out/ Upon arrival blower was turned off/ Turned blower on, cleaned air filter , blower now working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-3544 ETM-28688/ No breakout or spongy areas on the drainfield. Returned on 4/27/2023 for the sample | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
11/09/2023 | Alternative | Routine/Scheduled | 2005-143-0061 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and found recirculation middle float has failed. Flushed and cleaned effluent screen. -RSV (Recirculating Splitter Valve): Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Checked and confirmed spray height is good. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly -Drain Field: Found no signs of surfacing on dispersal field Repairs scheduled for 11/14 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 02:08 PM
03/09/2023 |  | RoutineScheduled | 177-STS-87709 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
12/13/2023 | Alternative | RoutineScheduled | 107-10-0114 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 3159.000000 | [] | [] |  |  |  | 7.410000 | 8.280000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/12/2024 | 04:55 PM
07/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
06/15/2023 |  | RoutineScheduled | 033-07-0298-ST | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 3-5 | 0-0 | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear |  |  | 11.000000 | [11 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/15/2023 | 02:00 PM
08/02/2023 | Alternative | RoutineScheduled | 09-110-099 | Bland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | R & R Enterprises, Inc | 1942001111 | William | Robinson | 1.000000 | 1250 | ECO-FLO |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | Dec 30 1899 12:00AM
07/14/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [18 empty] | Repair only: Replaced faulty check valves for Zones 1 & 2 in the drip field/ Tested and functioning correctly at this time. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Fairfax | Ace Contracting Services, Inc | 1942001120 | Lawrence | Fellenz Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | Dec 30 1899 3:09AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/19/2023 | Alternative | RoutineScheduled | 085-STS-31724 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/13/2023 | 12:00 AM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance | 2132-10-153 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation"] |  | NA | Musty | Clear | 7.200000 | 3.600000 | [11 empty] | Will be sent separately | Inspected | Needs aerator at discharge. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 11/15/2023 | 02:02 PM
04/05/2023 | Alternative | Initial Visit | 093-STS-14748 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 4.000000 |  | 1.000000 | [5 empty] | Owner called due to an alarm - muted it. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the alarm light bulb. The septic tank needs additional risers on it to be properly inspected in the future. The timer was set at 1 minutes every 1.5 hours changed it to 2 minutes every 1.5 hours. Took initial BOD and Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/05/2023 | Dec 30 1899 3:00PM
01/12/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Cleaned the air pre-filter as preventative maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
04/07/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/26/2023 |  | RoutineScheduled | 06-192-357 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","SludgeScum Accumulation","Septic Tank Baffles"] | YES | Musty | Clear | [15 empty] | 3 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/26/2023 | 12:00 AM
07/06/2023 | Alternative | Routine/Scheduled | 136-05-0033 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service - extended period between service events - new owners since last service event. Processing Tank - normal level - RSV, recirc pump, Effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensor, pump and controls operating. DBox - plastic - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | 07:30 AM
07/12/2023 | Alternative | RoutineScheduled Component Maintenance | 179-10-0308-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. 16 psi. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/18/2023 | 11:45 AM
02/16/2023 | Alternative | Reportable Incident | 119-STS-106024 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | ["Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | COSS - Maintenance - GMP2018-02 PUmped septic tank empty - installed cannister style effluent screen and access riser to grade. Replaced deteriorated DBox with new 8 port Concrete Dbox. Spliced to existing conveyance line Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 06:45 AM
02/02/2023 |  | Routine/Scheduled | 800-07-0176 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 8.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | Jan 1 1900 1:34PM
06/22/2023 | Alternative | RoutineScheduled | 154-08-0141 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | 12:00 AM
04/24/2023 |  | RoutineScheduled | 177-10-0189-ST | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [5 empty] | 04/24/2023 | [7 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Blower 3.05 amps. Removed small roots from dbox and added root x. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
05/03/2023 |  | RoutineScheduled | 175-12-0071 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Distribution Pump Operation"] | ["Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Distribution Pump Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | New owners said that system alarmed a couple of days ago. Not in alarm today, but discharge tank was close to high level. Reconnected alarm horn in control panel (someone had pulled off one of the wires). Electronic log indicated that high level alams had actually started April 26th in the recirc tank. Owner checked toilets, none running or leaking down. At this point, it appears that extra loads of laundry is what started the alarms. The 4" sleeve for the discharge force main has a new crack in it. This would only be a problem if the crack continued to outside the tank and picked up ground water during a heavy rain. No infiltration seen today. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
02/14/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
08/28/2023 | Alternative | RoutineScheduled | 98-197-A3 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodeny | Neece | 1.000000 | [11 empty] | None | Clear | 7.600000 | 7.000000 |  | 0.000000 | [11 empty] | The discharge pipe is way down the dirt road | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
12/21/2023 | Alternative | RoutineScheduled | 17-137-0160 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 2250 |  |  | Pump | Pressure | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","SludgeScum Accumulation","Level Sensor Operation","Effluent Screens","Control Operation","Disinfection","Distribution Pump Operation"] | YES | Pungent | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | 12:00 AM
07/14/2023 | Alternative | Follow-Up Component Maintenance | SWP-05-120 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic and pump tank pumped out by others 2 days prior. Replaced peat in pods 1-4. (Removed degraded peat by hand). Replaced 1 support bar. Peat was purchased from Drillers Services. Degraded peat was disposed at Spotsylvania Refuse. Will return to inspect distribution boxes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/18/2023 | 11:45 AM
08/15/2023 | Alternative | Routine/Scheduled |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating DBox - minor roots present - remvoed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | 06:30 AM
11/10/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-03-45 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation" ,"Level Sensor Operation"] | ["Distribution Pump Operation" ,"Control Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
02/01/2023 |  | Follow-Up | 550-STS-6829 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [20 empty] | 23.000000 |  | 3.000000 | [5 empty] | Took initial BOD and Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/01/2023 | Jan 1 1900 12:00PM
01/04/2023 |  |  | 06-172-0113A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 2000 | 1000 | 1000 | Pump | Pressure | Mound | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Effluent Screens","Level Sensor Operation"] | YES | None | Clear | 7.000000 |  | 7.000000 | [11 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/04/2023 | Jan 1 1900 10:00AM
03/10/2023 |  | Reportable Incident | 175-11-0425 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | [18 empty] | Service call only; Replaced faulty HP80 Clearstream Blower and rebuilt the float tree. Counts: Hand-106/ High level-24398/ Pump-19205/ Run time-1133h | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
04/24/2023 |  | RoutineScheduled | 133 15 0323 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Biomicrobics Fast |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Septic zone 1" scum and 3-5" sludge in septic tank. 6" sludge in Fast tank 12" sludge on Discharge side port of Tank -Alarm on Blower is operational. Good aeration in Fast unit. Trough is clear with water flowing correctly, Cleaned Air filter. Does not need pumping this year. Fully Operational. Added one 2lb Rootx treatment | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
03/17/2023 |  | RoutineScheduled | 169-STS-27127 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | ATL |  | Gravity | Gravity | Mound | Not Applicable | 200.000000 | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/17/2023 | 12:00 AM
10/04/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.420000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 04:00 PM
04/04/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
11/30/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Clear | 8.360000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 02:20 PM
04/27/2023 |  | RoutineScheduled | 132-18-0018 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco | Bio Reactor | Gravity | Pressure | Mound | UV | 600.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/04/2023 | 12:00 AM
09/05/2023 | Alternative | Routine/Scheduled | C16-111-0009 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | Jan 1 1900 2:00PM
07/04/2023 | Alternative | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 |  | 1500 |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | 12:00 AM
11/13/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 2.000000 | [13 empty] | Replaced aerator and alarm buzzer | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | Dec 30 1899 11:25AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Lower line appears to show signs of nitrification outside of the trench area. There are no signs of wet or soggy areas though. Recommend rebalancing D-Box and checking header connection to ensure that effluent isn't bleeding down to lower line. Camera headers if necessary. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
08/08/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Service call only: Replaced faulty blower (Ecopod E-75) Tested and working properly at this time. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/20/2023 |  | RoutineScheduled | 051-STS-17493 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Pump | Pressure | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Recirculation Pump","SludgeScum Accumulation","Level Sensor Operation","Effluent Screens","Control Operation","Auxiliary Filter"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","Recirculation Pump","Effluent Screens","Control Operation","Auxiliary Filter"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 12 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/20/2023 | 12:00 AM
08/14/2023 | Alternative | Routine/Scheduled | 228-04-0981 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | Musty | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/14/2023 | Dec 30 1899 9:00AM
10/04/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:00 AM
12/06/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-10"sludge 1"scum/ Microfast-12"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ No pump out needed at this time but may be necessary by next year/ Blower air filter cleaned and blower is working correctly/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-204 ETM-6h 3m/ Pump2-198 ETM-5h 50m/ Peak-12/ High-7/ On-1m 46s Off-6h/ Peak off-4h 48m/ No breakout or spongy areas on the LPD Pad site and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/18/2023 | Alternative | Routine/Scheduled | 06-160-0202 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable | 208.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | 02:45 PM
07/10/2023 | Alternative | RoutineScheduled Component Maintenance | 179-16-0121-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend mowing the dispersal area & maintaining it in a mowed condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
07/17/2023 | Alternative | RoutineScheduled | 09-100-0504 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 |  | BIOCOIR |  | Pump | Pressure |  | Not Applicable | 450.000000 | [] | [] | [18 empty] | SLUDGE JUDGE 2" FROM BOTTOM CLEANED FILTER EVERYTHING WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 02:40 PM
09/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
05/11/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/23/2023 | 09:32 AM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/30/2023 | Alternative | Routine/Scheduled | 025-STS-14047 | Brunswick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Southside | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | 10:00 AM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
06/26/2023 | Alternative |  | 177-08-0220-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
03/11/2023 | Alternative | RoutineScheduled | 171-17-0093 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | EZ-Treat |  | Gravity | Gravity | Discharge | UV |  | ["Attached Growth Medium","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA |  |  | 7.250000 | 8.900000 |  |  |  | 02/27/2023 | Sample Chamber | 6.300000 |  |  | 4.600000 |  |  | Will be sent separately | Inspected | Septic Tank under 1" scum laye-6-8" sludge on bottom in Septic tank - Recirc zone of tank 1" scum and 12-16" sludge, Owner replaced UV bulb and took lab samples to Pace, Blower unit runs and owner cleaned/replaced aitfilter, Clear Effluent on top, Pumps operational, 1 min on 15 min off but not accurate per owner. alarm operational, all floats tested operational. DO 8.94 and pH7.65, Owner takes samples to Eden PACE Analytical lab in NC for testing. TSS - 4.6, BOD - 6.3 Ecoli N.D. Total Coliforms 1410 mpn/100ml. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/23/2023 | 09:30 AM
05/16/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. ATU airline broken. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | 12:05 PM
08/04/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 1.000000 |  | Septic | Puraflo | Pump | Gravity | Trenches |  |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | 0 scum and very little sludge in septic tank. filter is clean. peat moss look recently changed. pump tank is clean, All alarms, floats and pump is working. Everything looks good | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | 11:00 AM
06/10/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 300 | BioMicrobics MicroFast |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Blower defective. Diagnosed on 6-10-2023. Replaced blower and performed annual inspection on 6-17-2023. 15" of accumulated solids in septic tank. 24" of solids in treatment unit. 12" of solids in discharge pump tank. Cleaned drip manifold spin filter. Tested floats, pump and alarms. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/24/2023 | 07:03 PM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/31/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Puraflo | [6 empty] | ["Control Operation","Dispersal System Operation","Level Sensor Operation"] | ["Control Operation","Dispersal System Operation","Level Sensor Operation"] | N/A | [17 empty] | Replaced alarm float | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/31/2023 | Dec 30 1899 8:00AM
07/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 12:49 PM
04/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/17/2023 |  | RoutineScheduled | 177-STS-89663 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
09/22/2023 | Alternative | RoutineScheduled | 132-05-0145 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 12:00 AM
04/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/04/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
04/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/27/2023 |  | Reportable Incident | 228-13-0111 A | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/27/2023 | Jan 1 1900 8:00AM
02/21/2023 |  | RoutineScheduled | 177-07-0381-SWP/177-07-0100-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. 4 wetspots on drip field, fixed. No more water above surface. Trees has not been cut. Drip rate around4.5 gallons per minute, recommend to do a bleach flush next year. Not able to measure drip rate accurately due to lack of flow meter. Alarm for blower not working any more, recommend to replace. Sludge level didn't change much Since last year most likely will need it next year. Will send proposal for bleach flush and panel replacement. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
11/17/2023 | Alternative | RoutineScheduled | 153-STS-19069 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ EZ-Treat Recirculation Tank | Pump Tank | Pump | Pressure | Drip | UV |  | ["Recirculation Pump","Disinfection"] | ["Disinfection","Recirculation Pump"] | YES | [17 empty] | Septic Tank-8"sludge 0"scum/ EZ-Treat Recirculation Tank-4"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ No pump out needed at this time/ UV-Light bulb requires replacement and done during inspection/ Faulty pump replaced during inspection/ Controls, pumps, floats and alarms are now functioning properly/ Counts: EZ-Treat Pump-0117356 ETM-04803.57 On-2m 30s Off-14m/ Discharge Pump Counts: 2044 ETM-578h 18m High level-13 On-18m 24s Off-4h/ Watermeter-0157585.66/ No breakout or spongy areas on the drip field and is dosing properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommended to homeowner that the sump pump drain is diverted away from the ends of the lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance | 179-07-0057-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. 1 pod was ponding on top, augered and drained. Media showing its age, evaluate next year for replacement. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
02/02/2023 |  | Routine/Scheduled | 800-11-0200 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | Jan 1 1900 11:41AM
03/09/2023 |  | RoutineScheduled | 001-STS-92081 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Bundick Well & Pump |  | 1.000000 | 1500 | Septic Tank | EcoPod E50N | Gravity | Pressure | Trenches | Not Applicable | 450.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/27/2023 | 12:30 PM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/06/2023 |  | Routine/Scheduled | 2013-143-0053 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Bionest |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/06/2023 | 01:54 PM
08/23/2023 | Alternative | RoutineScheduled | 163-STS-337950 | Rockbridge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Rejected | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | Septic Tank Only | AdvantexAX20RT | Gravity | Gravity | Discharge | UV |  | ["Effluent Screens","Disinfection"] | ["Effluent Screens","Disinfection"] | YES | [7 empty] | 08/23/2023 | Pump Chamber | 1.000000 |  |  | 3.000000 |  |  |  |  | The system did not need to be pumped. The effluent filter was pulled and cleaned. The textile sheets were sprayed off. The UV bulb was pulled and inspected. The outer housing of the UV was cleaned. The evaporation bed was inspected and was operating as designed. The post air pump was operating as designed. The BOD and TSS samples were well within the permitted limits. The controls were inspected and were operating as designed. The lids were secured. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/13/2023 | 09:20 PM
03/27/2023 | Alternative | Routine/Scheduled | S175-11-0090 | Southampton | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Norweco Singulair ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [14 empty] | Needs a new aerator | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/27/2023 | Dec 30 1899 10:00AM
03/17/2023 | Alternative | RoutineScheduled | 169-STS-27127 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | ATL |  | Gravity | Gravity | Mound | Not Applicable | 200.000000 | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/17/2023 | 12:00 AM
01/10/2023 |  | Routine/Scheduled | 228-16-0040 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | Jan 1 1900 2:27PM
02/27/2023 |  | RoutineScheduled | 177-STS-89545 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens" ,"BlowerCompressorAerator Operation"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
01/13/2023 |  | RoutineScheduled | 07-197-A5 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/13/2023 | 12:00 AM
08/24/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-88746 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. clogged pump intake on recirc pump, cleaned pump intake, spray heads and manifold also installed a SIM-TECH filter on recirc pump to prevent clogging. customer complained of smell around tanks some days, treatment looks clear but we still changed off time to improve treatment. raked media. Outstanding proposal for sealing leaks. HL-8, LL-35, OVERRIDE-6. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
07/06/2023 | Alternative | Initial Visit | 067-STS-38935 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20RT |  | Pump | Gravity | Trenches |  |  | ["Recirculation Pump","Control Operation"] | ["Recirculation Pump","Control Operation"] | NA | [17 empty] | Initial start-up visit. Set recirculation pump timers according to new manufacturer's memorandum for this unit's serial number. Set recirculation pump flow rate. Rearranged recirculation floats as they were in the incorrect position from installation. Set discharge pump float switches according to manufacturer's memorandum. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | 07:03 PM
06/02/2023 |  | RoutineScheduled | 175-12-0253 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank | Delta DF-60 to Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["Other","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Other"] | NA | [17 empty] | Septic Tank-7"sludge 0"scum/ ATU-4"sludge 3"scum/ Pump Tank-4"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ Cleanout was broken and repaired during inspection/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-41279 ETM-52h/ High level-115 On-5n 52s Off-1h 54m/ Watermeter-1,284,680/ Cleaned spin filter in the hydraulic unit/ No breakout or spongy areas on the drip field and dosing correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/26/2023 | Alternative | Reportable Incident | 119-STS-106025 | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Control Operation","Dispersal System Operation","Level Sensor Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | COSS - Maintenance - GMP2018-02 Primary septic tank - normal level. Pump Tank - pumped empty for confined space entry - re-parged interior of tank - replaced pump plumbing - replaced access riser with new. Installed new control panel, float sensors. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/30/2023 | 08:45 AM
05/30/2023 | Alternative | Reportable Incident | 166-01-688 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to a red light on. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream, cleaned the filter in the aerator, and cleaned the filter in the septic tank. Replaced the pump float. It was raining at the time of service and could not check out the drainfield or mound. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/30/2023 | 05:00 PM
09/18/2023 | Alternative | RoutineScheduled Component Maintenance | 182-14-0071 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
01/04/2023 |  | RoutineScheduled | 175-04-0460 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/24/2023 | 08:34 AM
01/30/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Control panel is broken out the bottom due to settling. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/31/2023 | 12:26 PM
08/11/2023 | Alternative | RoutineScheduled Component Maintenance | 061-STS-24499 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
12/20/2023 | Alternative | RoutineScheduled | S16-180-0008 | Roanoke | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Fast Biomicrobics |  | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | NA | [16 empty] | Inspected | Repair the system- New blower installed, system returned to normal after. Replaced the main air header line due to the bent pipe to make and glue the fitting tight to blower and no leak exhist anymore. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/28/2023 | Dec 30 1899 9:30AM
10/24/2023 | Alternative | Reportable Incident | 02-120-0269A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm call: -Came out to take a look at system customer stated keeps going in alarm Found leaking recirculation tank riser Presented options to customer Repair are scheduled for Nov 1st | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/30/2023 | Dec 30 1899 4:13PM
02/21/2023 |  | RoutineScheduled | 09-197-041 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Pump | Pressure | Trenches | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Distribution Pump Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Distribution Pump Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/21/2023 | 12:00 AM
08/09/2023 | Alternative | RoutineScheduled | 003-STS-32495 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [9 empty] | [] | [] | [8 empty] | 08/08/2023 |  | 12.000000 |  |  | 31.100000 |  |  |  |  | TSS 31.1 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/15/2023 | 12:30 PM
05/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-3"sludge 4"scum/ Microfast-4"sludge 0"scum/ Pump Tank-1"sludge/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ Counts: Pump1-389 ETM-31h 37m/ Pump2-377 ETM-30h 46m/ On-4m 58s Off-12h Peak Off-11h 36m/ No breakout or spongy areas on the Drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/13/2023 | Alternative | RoutineScheduled | 05-165-0271 | Northampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | ECOFLO |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | [] | [] | YES | [17 empty] | SLUDGE JUDGE SEPTIC TANK 6-7" FROM BOTTOM EVERYTHING WORKING AS IT SHOULD PEAT IS AT GOOD LEVEL AND IN GOOD CONDITION COUPLE SMALL ROOTS IN IT | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/14/2023 | 09:45 AM
07/06/2023 | Alternative | RoutineScheduled | 12-100-0062 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 500 | AQUASAFE |  | Pump | Gravity | Trenches | UV | 450.000000 | [] | [] | [18 empty] | REPLACED MUSHROOM VENT AND INSTALLED A NEW NORWECO UV LIGHT UNIT REPAIRED THINWALL PIPE GOING FROM THE DISTRIBUTION BOX TO THE DRAIN FIELD EVERYTHING WORKING AS IT SHOULD | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/17/2023 | 01:45 PM
02/24/2023 |  | RoutineScheduled | 08-137-0046 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/25/2023 | 12:00 AM
02/16/2023 | Alternative | Routine/Scheduled | 175-07-0135 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/16/2023 | Dec 30 1899 8:00AM
04/17/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | We sludge judged the septic tank and cleaned the filter. Also replaced the concrete lid on the pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
08/22/2023 | Alternative | RoutineScheduled Component Maintenance | 175-04-0876 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
03/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank and pump tank full. Pump appears to be functioning on hand but not under control of the panel. Homeowner is scheduled for pumping and repair | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
12/05/2023 | Alternative | Routine/Scheduled |  | Dinwiddie | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/05/2023 | Dec 30 1899 2:07PM
02/08/2023 |  | Routine/Scheduled | 800-STS-14095 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 1 minute every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/08/2023 | Jan 1 1900 2:15PM
08/17/2023 | Alternative | RoutineScheduled | 107-09-0059 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Attached Growth Medium"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Attached Growth Medium"] | [18 empty] | blower repaired and roots removed from FAST | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/21/2023 | 12:00 AM
08/09/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | BEST 1 |  |  | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | 12:00 AM
03/22/2023 | Alternative | Follow-Up Component Maintenance | 175-06-0477 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Distribution Pump Operation"] | ["Distribution Pump Operation" ,"Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced Gast blower and Goulds pump that were found to be failed last week. Also replaced all led light assemblies in the control panel and installed a new air filter. Some work remains: repair conduit separation and install rodent guards in the vent pipes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 06:43 AM
11/27/2023 | Alternative | Routine/Scheduled | 05-172-0296A | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Ecoflo |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/27/2023 | Dec 30 1899 10:09AM
08/11/2023 | Alternative | Follow-Up Component Maintenance | 177-STS-92270 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Wire wheeled and sealed joint in septic tank inlet riser. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
10/23/2023 | Alternative |  | 099-STS-92493 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/28/2023 | Alternative | Reportable Incident |  | Middlesex | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Fuji |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | None | None | N/A | [17 empty] | System re-activated at owners request - unknown if Any repairs have been made to the absorption field - No repairs have been made by Millers Services. Expect first pump activation may cause surfacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/31/2023 | 08:00 AM
11/03/2023 | Alternative | RoutineScheduled | 153-STS-20325 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Pad | UV |  | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | NA | [17 empty] | Septic Tank-4"sludge 0"scum/ Microfast ATU Tank-0"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower is working correctly/ Replaced faulty redundant off and timer enable floats/ Controls, pump, floats and alarms are now functioning properly/ UV-Light sleeve cleaned and light working correctly/ Counts: Pump-509 ETM-40h 21m On-4m 57s Off-12h/ Peak-2/ High-8/ No breakout or spongy areas on the LPD Pad Site and dosing properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
12/07/2023 | Alternative | RoutineScheduled | VAG401956 | Rockbridge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None |  | 7.800000 |  |  | 1.600000 |  | 12/07/2023 |  | 15.000000 |  |  | 10.000000 | [5 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/28/2023 | 02:00 PM
12/15/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/18/2024 | 12:00 AM
11/14/2023 | Alternative | RoutineScheduled | 15-113-035 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | CLEARSTREAM |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | 12:00 AM
12/12/2023 | Alternative | Routine/Scheduled | 041-STS-274793 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Aqua Klear |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/12/2023 | Dec 30 1899 8:17AM
07/14/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | Dec 30 1899 1:44PM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
04/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/10/2023 | Alternative | RoutineScheduled | 107-04-0304 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
05/19/2023 |  | RoutineScheduled | SD 89-603 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Blower 3.02 amps. Vacuumed sludge out of D-box and dumped it into septic tank. Septic tank most likely will need pump out next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
09/14/2023 | Alternative | RoutineScheduled | 107-91-0120 (LEGACY SEPTIC) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | LP |  |  | Pressure | Trenches | Not Applicable |  | ["Septic Tank Baffles","Dispersal System Operation","SludgeScum Accumulation"] | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | damaged lid, riser and caps replaced. Septic pumped out | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/14/2023 | 12:00 AM
06/19/2023 | Alternative | Routine/Scheduled | 087-STS-6588 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/19/2023 | 04:06 PM
07/19/2023 | Alternative | RoutineScheduled | 166-11-075 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned pump intake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/24/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Multiflo ATU |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge levels-- 1" Scum 10" sludge in Septic tank zone. Treatment tank had 2-3" scum lkayer and 6-7" Sludge trace. Aerator pump and alarm are opperational. Clear Effluent on top. Sprayed Large Black widow spider sprayed. Cleaned up the cone as it had Slight sudsing in treatment Owner had replaced the aerator and will be replacing the socks this year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
08/25/2023 | Alternative | RoutineScheduled | 150-18-0156 | King William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [18 empty] | Replaced L280 pump | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | pump tank concrete lid needs replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
08/29/2023 | Alternative | Routine/Scheduled | 234-17-19 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/29/2023 | Dec 30 1899 9:35AM
10/19/2023 | Alternative | RoutineScheduled | 185-STS-17544 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 8 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/19/2023 | 12:00 AM
07/21/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Multiflo FTB |  | Pump | Gravity | Trenches |  | 450.000000 | None | None | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/25/2023 | 01:47 PM
07/10/2023 | Alternative | Reportable Incident | 196-10-142 | Westmoreland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | High water & UV failure. Cleaned filters & replaced UV ballast | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
10/24/2023 | Alternative | RoutineScheduled Component Maintenance | 177-15-0091-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["SludgeScum Accumulation" ,"Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Presale inspection. Current homeowner has made an appointment with a local pumper to get the Microfast septic tank pumped out next week, and will refill the tank with fresh water afterwards. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
09/06/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | 12:00 AM
08/18/2023 | Alternative | Routine/Scheduled | 136-17-0048 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/18/2023 | 08:15 AM
10/02/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-89658 | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Recirculation Pump"] | ["Dispersal System Operation" ,"Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | The pump line is broken leaving the pump tank and the area around the pump tank is saturated. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/01/2023 | 07:38 AM
02/17/2023 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:43 PM
05/02/2023 | Alternative | RoutineScheduled | 115-18-0131 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Acres of Virginia, Inc. |  | Melvin | Collins | 1.000000 | 1500 | Septic Tank | Ecoflo | Pump | Gravity | Trenches | Not Applicable | 250.000000 | ["Auxiliary Filter"] | ["Auxiliary Filter"] | [18 empty] | Peat in pod needs changing. Customer has been notified. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/23/2023 | 11:35 AM
04/25/2023 |  | RoutineScheduled |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 1-3 | 0-1 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear |  |  | 8.000000 | [11 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | 09:00 AM
06/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank | Delta ATU to Pump Tank | Pump | Pressure | Drip |  |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | [7 empty] | 06/27/2023 | Sample Chamber | 29.000000 | [5 empty] | Attached to this report |  | Septic Tank-6"sludge 0"scum/ ATU-3"sludge 2"scum/ Pump Tank-3"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Replaced faulty float during inspection/ Controls, pump, floats and alarms now functioning properly/ Counts: Pump-46413 ETM-2113h On-8m 20s Off-1h 52m/ High cnts-60/ Switch to Hand-129/ No breakout or spongy areas on the drip field. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/19/2023 |  | Routine/Scheduled | 10-120-0185A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/19/2023 | Jan 1 1900 10:26AM
12/01/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | Delta Environmental Products, DF Series | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/18/2023 | Dec 30 1899 8:36AM
10/16/2023 | Alternative | RoutineScheduled Component Maintenance | 179-09-0066-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Water standing in dbox clean out, customer states they had rain last 2 days before inspection. Recommend to dig up dbox and camera snake lines to check for roots or saturated lines. Clogged up septic filter, cleaned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
09/21/2023 | Alternative | RoutineScheduled | VAG408220 | Rockbridge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 2.000000 | 2000 | Septic Tank Only | MicroFast | Gravity | Gravity | Discharge | Chlorination |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The blower filter was pulled and cleaned. The controls were operating as designed. The MicroFast unit was in good operating condition. The et bed was in good operating condition. The out fall pipe was in good operating condition. There was no samples drawn because there was no discharge at the time of service. There were tablets in both of the tablet feeders. The lids were secured. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/17/2023 | 05:25 PM
11/04/2023 | Alternative | RoutineScheduled | 109-17-0488 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex AX20RT |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. 0" of solids in recirculation portion of treatment unit. 4" of solids in discharge portion of treatment unit. Tested floats, pumps and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 07:03 PM
11/30/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Level Sensor Operation"] | [18 empty] | Float replaced. Pumping of FAST/septic scheduled | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/30/2023 | 12:00 AM
08/10/2023 | Alternative | RoutineScheduled | 08-160-0033 | Montgomery | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - New River | King's Alternative Septic | 1942001094 | David | King | 2.000000 | 1500 | Premier Tech 650 Eco Flow |  | Gravity | Gravity | Trenches | Not Applicable | 100.000000 | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | YES | [17 empty] | Raked peat, peat is getting low. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/06/2023 | 12:00 AM
04/11/2023 |  | Routine/Scheduled |  | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 07:00 AM
05/16/2023 |  | Routine/Scheduled | 085-STS-35589 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | None |  | Pump | Gravity | Trenches | Not Applicable |  | SludgeScum Accumulation | SludgeScum Accumulation | N/A | [17 empty] | Septic tank pumped out. Fixed outlet Tee. System should return to normal operation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/22/2023 | Jan 1 1900 9:31AM
04/05/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump chamber wall appears to be compromised. Homeowner is looking into process of repair. Dwelling in not occupied. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
08/14/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | ["Other"] | YES | None | Clear | 7.900000 |  | 10.000000 | [12 empty] | Power washed system | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/15/2023 | 12:00 AM
01/20/2023 |  | RoutineScheduled | 177-STS-90229 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | 90-Day Inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
05/03/2023 | Alternative | Routine/Scheduled | 093-STS-14444 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Microfast |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/03/2023 | Dec 30 1899 11:39AM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/21/2023 | Alternative | RoutineScheduled | 101-13-0364 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | 2023 Annual Inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/21/2023 | 12:00 AM
06/28/2023 | Alternative | Routine/Scheduled | 234-16-211 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | Dec 30 1899 11:15AM
07/19/2023 | Alternative | Routine/Scheduled | 196.04.314 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Puraflo |  | Pump | Pressure | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | 05:14 PM
09/21/2023 | Alternative | RoutineScheduled | 061-15-457 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2500 | trash/Microfast | Pump tank | Gravity | Pressure | Mound |  |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/21/2023 | 03:00 PM
09/12/2023 | Alternative | RoutineScheduled Component Maintenance | 175-14-0050 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Zoner has cracked & needs replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | 12:58 PM
01/03/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 01/03/2023 |  | 15.000000 | [5 empty] | Will be sent separately | Inspected | Possible partial clog from primary tank and pump tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
03/30/2023 |  | RoutineScheduled | 2006-143-0313 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1250 | MicroFAST |  | Pump | Pressure | Trenches |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 12:00 AM
12/08/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | Louisa | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Rejected | EHD - Blue Ridge | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/08/2023 | 09:00 AM
10/04/2023 | Alternative | RoutineScheduled Component Maintenance | 033-STS-91677 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Control Operation" ,"Disinfection" ,"Auxiliary Filter"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Control Operation" ,"Disinfection" ,"Auxiliary Filter"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
07/31/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20271 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Chlorination |  | ["Disinfection" ,"Effluent Screens"] | ["Disinfection" ,"Effluent Screens"] | YES | Musty | Clear | 7.300000 | 6.100000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 08/15/2023 | 01:44 PM
06/06/2023 | Alternative | Reportable Incident | 234-14-307 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/06/2023 | Dec 30 1899 11:00AM
11/07/2023 | Alternative |  | 124-STS-2379 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/01/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/10/2023 | Alternative | Reportable Incident | SHUN-BAGKW4 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed a rebuild kit on the aerator. The timer is set to 3 minutes every 3 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/10/2023 | Dec 30 1899 1:30PM
06/01/2023 | Alternative | RoutineScheduled | 15-137-0168 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 2.000000 | 1850 | Multiflo |  | Pump | Pressure | Trenches |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/07/2023 | 12:00 AM
04/19/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 2.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/16/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/30/2023 | Alternative | RoutineScheduled |  | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | 12:00 AM
08/09/2023 | Alternative | Routine/Scheduled | 234-17-0084 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | Dec 30 1899 9:05AM
04/07/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank to Puraflo Modules | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NO | [17 empty] | Septic Tank-6"sludge 0"scum/ Pump Tank-3"sludge 0"scum/ ( Pump out required every 5 years) Pureflo Peat turned in all 5 modules and is in good condition at this time/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-12409 ETM-16670h/ Pump2-12732 ETM-17070h On-47s Off-2h/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/11/2023 | Alternative | RoutineScheduled Component Maintenance | 182-10-0127 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
05/22/2023 | Alternative | Reportable Incident | 151-90-465 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 300.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | COSS - Repair - VDH Permit 151-23-0073 - GMP2018-02 Pumped existing septic tank empty - crushed and removed. Installed new Infiltrator IM1060 poly tank as allowed by AOSE New 4" PVC conveyance line to existing distribution box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 07:30 AM
08/02/2023 | Alternative | Routine/Scheduled |  | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 3000 | EZ Treat Sandfilter |  | Pump | Pressure | Pad | UV | 1000.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Pumped primary and secondary septic tanks empty - serviced effluent screen. Tanks pumped to repair damaged / settled conveyance lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/03/2023 | Dec 30 1899 7:00AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/13/2023 | Alternative | RoutineScheduled | 103-STS-96410 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/06/2023 |  | RoutineScheduled | SWP-03-949 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Replaced broken lid on pureflow closer to driveway. Replaced broken extension on sample box. Junction box at pump tank riser was knocked off, put 3 screws to hold it back in place. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
01/30/2023 | Alternative | RoutineScheduled | SD-04-292 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity |  | Chlorination |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | Sulphitic | Cloudy |  | 9.950000 |  |  |  | 01/30/2023 | Sample Chamber | 2.000000 | 0.030000 | 6.300000 | 1.000000 |  |  | Will be sent separately | Inspected | Effluent Sample taken. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
08/30/2023 | Alternative | RoutineScheduled | 181-06-0302 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 2.000000 | 2500 | Biomicrobics MicroFAST |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | Filters checked and cleaned. Blower, alarm and control panel functioning properly. System did not need to be pumped. No apparent leaks in system or drain field area. Lids were properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/15/2023 | 05:35 PM
09/14/2023 | Alternative | RoutineScheduled Component Maintenance | SD-12-376 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | None | Clear | [5 empty] | 09/14/2023 | Sample Chamber | 6.000000 | [5 empty] | Will be sent separately | Inspected | Completed annual inspection and collected effluent sample for 5-year BOD test. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
08/17/2023 | Alternative | RoutineScheduled | 041-STS-260315 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Multi Flo |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","Distribution Pump Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/17/2023 | 12:00 AM
10/09/2023 | Alternative | RoutineScheduled | 18-142-0433 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Recirculation Pump","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/06/2023 |  | RoutineScheduled | 03-197-A3 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/06/2023 | 12:00 AM
07/05/2023 | Alternative | Routine/Scheduled | 04-160-0573 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NO | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | 09:50 AM
10/16/2023 | Alternative | RoutineScheduled | 171-08-0279 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank Pumped | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | NA | [16 empty] | Inspected | Annual Routine inspection combined with a pump out, Removed the Pump Biolfilter and pump basin to provide access. Foutz pumped 1500 Gallons and backwashed until very clean of heavy solids. Cleaned recircultion pump screen which was covered in seed husks and cleaned biofilter also heavy in plant matter. Rinsed and flushed RSV Hosed off the media. Reassembled system. Owenr will fill with lake water to return to normal operation. Pump run time 1817.6 Hours and 46,078 cycles in history- RTU116481 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | 09:30 AM
02/10/2023 |  | RoutineScheduled | 09-160-0158 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [18 empty] | - replaced Microfast Blower | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2023 | 12:00 AM
04/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
03/14/2023 |  | RoutineScheduled | 175-15-0273 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["SludgeScum Accumulation"] | [] | NA | [17 empty] | Septic-12"sludge 6"scum/ Microfast ATU-16"sludge/ Pump Tank-2"sludge/ Pump out required on the Septic-Microfast Tank due to sludge levels/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-8760 ETM-1125h 42m/ Peak-8 ETM-94h 24m/ Watermeter-459607/ Pump On-8m Off-1h 28m/ Blower air filter cleaned and blower working correctly/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/30/2023 | Alternative | Routine/Scheduled | 119-STS-95924 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Normal Level 5" of sludge and 1" of solids -Aeration: Normal Level Less than 1" of suspended solids Pulled and cleaned aeration/ aspirator Pulled and cleaned bio kinetic filter assembly -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 03:38 PM
07/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
01/05/2023 |  | RoutineScheduled | 099-STS-89617 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
04/13/2023 |  | RoutineScheduled | 101-05-0134 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/16/2023 | 12:00 AM
06/16/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/14/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 06/14/2023 |  | 10.000000 |  | 1600.000000 |  |  |  | Will be sent separately | Inspected | Broken ARV in drip field causing improper dosing and surfacing effluent. Appears to have been hit by lawnmower when cutting field. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/07/2023 | Dec 30 1899 6:25AM
04/25/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
02/23/2023 |  | Reportable Incident |  | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Three Rivers | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | COSS - Maintenance - GMP2018-02 Replaced degraded DBox with new 8 port concrete dbox. Spliced to existing conveyance line. Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/27/2023 | 06:45 AM
06/05/2023 | Alternative | Follow-Up Component Maintenance | 099-14-0006-SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Installed new Orenco UV unit per engineer's repair plan. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
03/30/2023 |  | RoutineScheduled | 2090-04-153 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Chlorination |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Cloudy | 7.300000 | 13.200000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 04/15/2023 | 07:20 PM
08/04/2023 | Alternative |  | 175-05-0713 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | EcoVirginia LLC | 1942001235 | William | Poindexter | 3.000000 |  | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | 12:00 AM
06/13/2023 | Alternative | Routine/Scheduled | 19-163-0055 | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  |  | Aqua Klear | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/13/2023 | Dec 30 1899 12:38PM
08/03/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-21175 | Clarke | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 |  |  | Pump | Pressure | Trenches |  | 450.000000 | ["Dispersal System Operation","Distribution Pump Operation","Septic Tank Baffles"] |  | N/A | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/13/2023 | 01:58 PM
10/31/2023 | Alternative |  | 179-17-0372-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/28/2023 | Alternative | RoutineScheduled Component Maintenance | 182-18-0305 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
06/16/2023 | Alternative | RoutineScheduled | 128.01.248 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/06/2023 | Alternative | Reportable Incident | 16-172-0413A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Upon arrival, I found the control panel in alarm condition indicating high level alarm in discharge. Checked and visually confirmed discharge was in high level. Checked pumps and found discharge pump not functioning due to a tripped residential breaker. I reset the residential breaker and confirmed discharge pump is functioning properly. Checked discharge amperage and confirmed it's within operating range. Flushed and cleaned disk filter for preventative maintenance. While checking system I noted surfacing next to headworks box. I excavated and found a fitting had cracked due to stress from settling. Homeowner gave approval for repair and I repaired the fitting while on site. Checked and confirmed the repair was good and there were no more surfacing issues. Checked and visually confirmed drawdown. Informed Homeowner that system should return to normal in 24-48 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | Dec 30 1899 10:54AM
07/14/2023 | Alternative | Follow-Up Component Maintenance | 175-10-0346 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Gravity | Gravity | Trenches | UV |  | ["Disinfection" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Compressor has been replaced and operational. Uv unit still has not been replaced and is still not functioning. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 09/15/2023 | 02:41 PM
10/12/2023 | Alternative | RoutineScheduled | 04-100-1017 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1250 | PURAFLO |  | Pump | Gravity | Pad | Not Applicable |  | [] | [] | NA | [17 empty] | SLUDGE JUDGE SEPTIC TANK 4-5" FROM BOTTOM EVERYTHING WORKING AS IT SHOULD RAKED PEAT. GOOD LEVEL AND GOOD CONDITION | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:15 PM
11/21/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | MicroFast | Pump | Pressure | Drip |  |  | [] | ["Dispersal System Operation","BlowerCompressorAerator Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [17 empty] | 12" Of sludge, 0 scum in septic tank. 12" in fast side. 6" in pump tank. Recommend pumping tanks before next years inspection. Cleaned filter, alarms, pump, blower all working. transducer good. Fixed a leak in the drip field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/04/2023 | 11:00 AM
01/24/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | UV |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/02/2023 | Jan 1 1900 11:08AM
04/04/2023 | Alternative |  | 124-STS-2379 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Blue Ridge |  |  | JULIANA | DUNLAP | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/10/2023 | Alternative | Reportable Incident | 18-190-061 | Surry | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm and red light. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. Replaced the UV light bulb. The septic tank needs to be pumped out and pump the trash out when pumping the septic tank. The timer is set to 1.2 minutes every 1.5 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/10/2023 | Dec 30 1899 12:45PM
10/05/2023 | Alternative | Routine/Scheduled | 11-120-0283A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/05/2023 | Dec 30 1899 10:48AM
09/08/2023 | Alternative | Routine/Scheduled | 234-16-111 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/08/2023 | Dec 30 1899 10:50AM
02/23/2023 |  | RoutineScheduled | 065-STS-32281 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/25/2023 | 12:00 AM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
04/26/2023 | Alternative | RoutineScheduled | 133-STS-95841 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/18/2023 | Alternative | Follow-Up | 810-STS-3963 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 10/18/2023 |  | 4.000000 |  | 109.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | Dec 30 1899 1:00PM
12/07/2023 | Alternative | RoutineScheduled Component Maintenance | SD-05-289 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Chlorination |  | ["Attached Growth Medium" ,"Disinfection" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Disinfection" ,"Recirculation Pump"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Effluent sample results will be sent separately | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/02/2023 | Alternative | RoutineScheduled | 10-167-038 | Nottoway | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Retaw Engineering LLC | 1965008335 | Ginasiyo | Mutoti | 10.000000 | 60,000 | Settling | Equalization/Pre-Anoxic | Pump | Gravity | Trenches | Not Applicable | 262.000000 | ["Control Operation","Distribution Pump Operation","Recirculation Pump","SludgeScum Accumulation","Dispersal System Operation","Septic Tank Baffles"] | ["SludgeScum Accumulation","Other","Control Operation","Distribution Pump Operation","Recirculation Pump","Septic Tank Baffles"] | NA | None | Clear | 6.900000 | 3.900000 | 0.000000 | 0.000000 |  | 11/02/2023 | Sample Chamber | 23.100000 | 0.000000 | 62.000000 | 0.000000 | 18.310000 | 5.320000 | Attached to this report | Pumped Out | Pump and Haul of Grease trap and Septic Tank was just so we can have a clean start under this contract. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | Dec 30 1899 9:05PM
07/17/2023 | Alternative | RoutineScheduled Component Maintenance | 179-08-0182-SWT | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/18/2023 | 11:45 AM
12/04/2023 | Alternative | RoutineScheduled | 107-03-0056 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | Septic and Pump tank needs pumping | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/04/2023 | 12:00 AM
05/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The lids were not screwed in. Hardware was replaced at the time of inspection. Blower was replaced by others. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/15/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | DeHaven's Backhoe Service Inc. | 1942001541 | Wayne | Edmonson | 2.000000 | 2500 | Microfast |  | Pump | Pressure | Drip | Not Applicable | 175.000000 | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/17/2023 | 12:00 PM
10/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
11/01/2023 | Alternative | RoutineScheduled Component Maintenance | 179-16-0060-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | None | Clear | [5 empty] | 11/01/2023 |  | 4.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
09/01/2023 | Alternative |  | 033-16-0068-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
02/07/2023 |  | RoutineScheduled | 179-15-0244-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"Level Sensor Operation" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | ["Septic Tank Baffles" ,"Level Sensor Operation" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Blower 3.13 amps. Treatment looks very clean. Sump pump discharging towards pump tank recommend to extend pipe away from tanks to prevent future problems. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
05/26/2023 |  | Follow-Up | 175-16-0116 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Replaced faulty blower Model: VFC 200P-5T | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
08/26/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 10" of accumulated solids in septic tank. Cleaned recirculation pump basket filter. Flushed treatment unit spray manifold. Tested floats, pump and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/17/2023 | 07:03 PM
07/17/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced Puraflo peat in 5 modules. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 06:01 AM
10/25/2023 | Alternative | Routine/Scheduled | S 800-16-0188 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [16 empty] | Pumped Out | Annual Maintenance: -Septic Tank: Flooded upon arrival. Was pumped prior to inspection. All solids and sludge removed. Inlet riser is leaking. No outlet effluent filter installed. Liars of non biodegradable items in the septic tank -Discharge/Pump Tank: Plumbing broken which is not allowing effluent to escape the system to the drainfield. Inlet and outlet risers of discharge tank are leaking with heavy water intrusion. Tank was flooded upon arrival, but was pumped while on site, and all solids and Sludge were removed. Floats are improperly secured to the Forcemain. No float tree installed in the discharge tank. All wires are buried directly in the ground going to the panel. -Aeration: Tank was flooded upon arrival, but as the rest of the system was pumped down, it returned to normal level for inspection. Alarm float is functioning properly at time of inspection. Weir is intact and was cleaned during the inspection. Pulled and cleaned the serviceable, airline assembly, cleaned the diffuser, however, it is recommended to be replaced to prolong the life of the air pump. Riser is leaking with heavy water intrusion. -Air Pump/Blower: Air blower is functioning properly at this time and is currently pulling 1.3 A which is within proper operating range. -Control Panel: Control panel, and all visual and audible. Alarms are functioning properly at this time. -Distribution Box: Was unable to locate distribution box, however, was able to narrow down the probable location of the box. The area in which the distribution box most likely is does not show any signs of ground, sinking or collapse, and no signs of blowouts or surfacing. -Drain Field: Was able to locate all eight drain lines, and after probing noted that there are no signs of surfacing or blowouts, and ground was not saturated during probing. Pump out (10/27): - Pumped 1500 gallons from flooded system, out of septic tank. Removed all solids and sludge from septic tank. Pumped 500 gallons from discharge tank and removed all sludge. Repair (10/30): -Installation of 6" - 12" Riser on Pump Tank -Installation of 6" - 12" Riser on Pump Tank -Installation of 6"-12" Riser on the Septic Tank -Installation of 6" Effluent Filter in Septic Tank -Installation of 3 new Floats Installation of a Float Tree Assembly to secure Floats -Installation of a Plumbing Kit -Installation of a Diffuser -Conduit & Wiring up to 10' -Installation of a water-resistant SB4 Junction Box inside a Riser includes Conduit and Grommet Kit | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/30/2023 | Dec 30 1899 4:30PM
03/10/2023 |  | RoutineScheduled | 2006-143-0022 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1250 | Clearstream |  | Pump | Pressure | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | 12:00 AM
10/10/2023 | Alternative | RoutineScheduled | 07-163-0050 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/06/2023 |  | RoutineScheduled |  | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Recommend move trees, pump screen clogged cleaned | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
04/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/24/2023 |  | RoutineScheduled | SWP-04-344 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Effluent Screens"] | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Timer enabler float was stock close, replaced under warranty. Septic filter alarm was on due to clogged filter, cleaned filter and water level went back to normal. Water quality in Dbox was really bad due to peat moss ponding and breaking down bad. Media needs to be replaced due to age and conditions. 3 pods closer to road are ponding, augered to help drain. Will send proposal for peat replacement. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
04/05/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 2.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
04/13/2023 |  | Reportable Incident |  | Mathews | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | ["Control Operation","Distribution Pump Operation","Level Sensor Operation"] | None | N/A | [17 empty] | AOSS - Initial visit - Real Estate Inspection. System flooded - discharge pump (high head turbine) pulling minimum amperes indicating that pump is functioning, but head is not functioning. Sump pump found in aeration compartment - indicating that system is being pumped to ground surface. Recommend pumpout of trash tank, aeration tank. Drip return line fractured inside of pump tank. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/17/2023 | 09:30 AM
01/02/2023 |  | RoutineScheduled | 04-125-072 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Fast |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/02/2023 | 12:00 AM
02/17/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | Dec 30 1899 12:05PM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance | 175-19-0109 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
03/01/2023 |  | RoutineScheduled | 179-STS-89702 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter" ,"Control Operation" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Auxiliary Filter" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
02/06/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Dispersal System Operation"] | ["Dispersal System Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
04/03/2023 |  | Reportable Incident |  | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | [18 empty] | COSS - Maintenance - GMP2018-02 Replaced deteriorated DBox with new "Monster" plastic DBox Spliced to existing conveyance line. Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | 06:30 AM
08/17/2023 | Alternative | RoutineScheduled Component Maintenance | 179-14-0104-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
05/10/2023 | Alternative | Reportable Incident | 136-10-0092 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | N/A | [17 empty] | AOSS - Alarm Event - Compressor Failure Compressor replaced on property - replaced air diffuser. Restored to proper operation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/25/2023 | 07:00 AM
05/10/2023 |  | Routine/Scheduled | 17-120-0498A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | The trash tank needs pumping | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/10/2023 | Jan 1 1900 9:19AM
11/02/2023 | Alternative | Routine/Scheduled | 151-15-0020 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3000 | EcoPod | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | 05:49 PM
06/23/2023 | Alternative |  | 101-17-0520 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Brittney | Wills | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/07/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1125 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/03/2023 |  | Routine/Scheduled | 093-06-0142 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | [15 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/03/2023 | Jan 1 1900 10:50AM
08/12/2023 | Alternative | RoutineScheduled | SD-05-241 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2000 | septic | ATU | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | 07:50 AM
01/19/2023 |  | Reportable Incident | 177-STS-87327 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was not running due to failed panel. Replace bio-microbics panel. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
06/06/2023 |  | RoutineScheduled | 175-13-0543 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["Disinfection","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | [17 empty] | System in alarm upon arrival: Found loose wires on the UV-Light causing alarm, repaired and no longer in alarm. Septic Tank-3"sludge 0"scum/ Microfast-2"sludge/ Pump Tank-0"sludge/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ Controls, pump, floats and alarms now functioning properly/ Counts: Pump-17526/ Pump Run Time-2362/ Hand-52/ High-13/ Watermeter-045651.3/ No breakout or spongy areas on the drip field and dosing correctly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
09/18/2023 | Alternative | RoutineScheduled Component Maintenance | 182-04-0507 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
08/18/2023 | Alternative | RoutineScheduled Component Maintenance | 099-18-0159 SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Attached Growth Medium" ,"Control Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Disinfection" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Control Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Disinfection" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Replaced uv bulb. Grass to tall in drip field, customer said he will mow it asap. 40 psi. RECIRC: HL-4, LL-11, OVERRIDE-30. DISCHARGE: HL-15, LL-12, OVERRIDE-12. Air release valves will be accessible once drainfield gets mowed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
03/20/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | DSS repaired air release valve and cleaned Advantex spray heads. Effluent pump had failed. The system appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/29/2023 | Alternative | RoutineScheduled Component Maintenance | 2090-04-153 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Chlorination |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | No Discharge Sign | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 12/06/2023 | 09:34 AM
07/06/2023 | Alternative | RoutineScheduled | 182-08-0182 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","SludgeScum Accumulation","Dispersal System Operation","Septic Tank Baffles"] | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/25/2023 | 12:00 AM
11/13/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | Dec 30 1899 12:15PM
10/19/2023 | Alternative |  | 16-160-0003 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Trenches |  |  | [] | [] | NO | [16 empty] | Inspected | - pump non-functional, recommend pump replacement - alarm is also not working at this time | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/30/2023 | 12:00 AM
05/02/2023 | Alternative | RoutineScheduled | 115-00-0509 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Acres of Virginia, Inc. |  | Melvin | Collins | 1.000000 | 1500 | Septic Tank |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/23/2023 | 12:40 PM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance | {FIPSCode}-STS-83661 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
08/29/2023 | Alternative | Follow-Up Component Maintenance | 099-07-0017-SR | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation" ,"Dispersal System Operation"] | ["Level Sensor Operation" ,"Control Operation" ,"Dispersal System Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Follow up. Repaired 2 bad emitters. Bleach flush drip field, gallons per minute improved. 13 psi. Shut both valves at head works and waited to pressurized to 20 psi, 5 minute draw down and got 7.35 gallons per minute. After draw down set valves to 13 psi. Cleaned spin filter before testing. Panel st back to original setting 7 minutes on. No water coming up to surface. Replaced air filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
02/13/2023 | Alternative | Initial Visit | 166-04-305 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 1250 | Biomicrobics MicroFAST |  | Pump | Pressure | Trenches | Not Applicable | 1000.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | AOSS - Initial Visit - FOIA Filed - Health Department FAILED to send appropriate paperwork and Documentation as requested! Grease Trap - inspected. Trash Tank - pumped and cleaned tank. Aeration Unit - mixing present - compressor serviced - pumped aeration tank empty - refilled with fresh water for restart Pump Tank - float sensors, pump and controls operating - control panel seals are allowing water and condensation to enter panel - recommend replacing. Walked LPP Field - no indications of surfacing. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/13/2023 | 12:00 PM
07/07/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None | Clear | 8.190000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 10:35 AM
10/05/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | 12:00 AM
06/06/2023 |  | Follow-Up |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [6 empty] | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/13/2023 | 01:25 PM
07/26/2023 | Alternative | RoutineScheduled | 11-160-0128 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 | 1500 | Microfast | [6 empty] | [] | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | [8 empty] | 07/26/2023 | Sample Tap | [6 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/14/2023 | 12:00 AM
04/17/2023 |  | Routine/Scheduled | 234-12-12 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | Jan 1 1900 8:25AM
09/08/2023 | Alternative | Routine/Scheduled | 166-12-158 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2850 | Clearstream |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 0.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 05:15 PM
04/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/23/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-92595 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Zone number was was doing 8.4 gallons per minute, found broken fitting at dripfield. Replaced broken fitting area should dry out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
06/01/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 12:00 AM
12/13/2023 | Alternative | Routine/Scheduled | 127-STS-35052 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 750 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 11:30AM
06/09/2023 | Alternative | RoutineScheduled | 30A-A-102 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic |  | Pump | Pressure | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | 0 scum 8" of sludge, Pump tank clean. Effluent filter was clogged. cleaned it. Field dry. Alarm, floats, and pump all work. Float tree not secured. I secured it. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/09/2023 | 11:00 AM
09/11/2023 | Alternative | RoutineScheduled | 075-STS-33813 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco | Norweco | Gravity | Pressure | Mound | UV | 600.000000 | [] | ["Auxiliary Filter","Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/22/2023 | 12:00 AM
10/05/2023 | Alternative | Routine/Scheduled | 2016-143-0197 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 400 | Norweco Singulair ATU |  | Pump | Gravity | Trenches | Not Applicable | 300.000000 | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | NO | [17 empty] | Effluent filter was checked. The rubber feet for the compressor bracket apparently came off from vibration. Three feet were reapplied to bracket, the fourth was missing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 12:38 PM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity |  | Chlorination |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Sampling could not be done no discharge present. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/30/2023 | 10:30 AM
05/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/11/2023 | Alternative | Reportable Incident | 234-16-64 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | Cleaned Weir filter | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/11/2023 | Dec 30 1899 10:00AM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance | 015-STS-334434 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 2.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced drip tank audible alarm and rehung floats | This AOSS should now return to normal function after having provided the above state routine maintenance | 08/23/2023 | 06:57 AM
12/21/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | Dec 30 1899 12:25PM
01/21/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [16 empty] | No Grease. Needs Pump out, I flagged lids that need pumping. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/21/2023 | Dec 30 1899 9:00AM
01/13/2023 |  | RoutineScheduled | 175-02-0052 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic -ATU-Pump Aquarobic Tank |  | Pump | Gravity | Mound | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic-Aquarobic-Pump Tank- 8"sludge 0"scum/ No pump out needed at this time/ Controls, pump, floats and alarms functioning properly/ Blower air filter cleaned and blower working properly/ No breakout or spongy areas on the Aquarobic Mantle area and Vegetation is in good condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/24/2023 | Alternative | RoutineScheduled | 047-17-017 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1500 | septic | Ez Treat | Gravity | Gravity | Discharge | UV |  | ["Disinfection"] | ["Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | Musty | Clear | [14 empty] | Pumped Out | No discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/10/2023 | 07:20 AM
03/31/2023 | Alternative | Routine/Scheduled | 053-STS-10019 | Dinwiddie | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/31/2023 | Dec 30 1899 2:32PM
11/28/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1942001117 | Charles | Seal |  |  | Advantex AX20 RT |  |  | Pressure | Drip | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | [18 empty] | Replaced control panel | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/28/2023 | 12:00 AM
09/25/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | Dec 30 1899 11:15AM
03/06/2023 |  | RoutineScheduled | 179-06-0128-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend pumping the Advantex tank & pump tank with our staff present to assist the pumper to remove the scum & sludge from the tanks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
11/03/2023 | Alternative | RoutineScheduled | 182-06-0490 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Control Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Control Operation"] | [18 empty] | Buzzer placed | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/03/2023 | 12:00 AM
11/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
09/14/2023 | Alternative | Routine/Scheduled | 04-163-0225 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Found at normal level, 4in of sludge and less than 1in of solids. Inlet tee is kicked up on a bad angle. Trash tank riser has signs of leaking. -Recirculation Tank: Found at normal level, found 5in of sludge and less than 1in of solids. Pulled and cleaned pump, floats and biotube filter. Riser is showing signs of leaking Floats and pump are aged -RSV: Pulled and cleaned rsv inside and out -Discharge/Pump Tank: Found at normal level, less than 1in of sludge and solids. Top 12in riser section and lid is broken. Tested floats and pump all working as they should. Floats are hung off the plumbing Where forcemain exits the riser is not sealed properly. Pump is aged -Media Sheets: Found bridging across media sheets. Sprayed media sheets brushed laterals and flushed unit. Media sheets are aged. No locking strut kit -Control Panel: 120 vo.ts audio and visual alarms working as they should. Recirc pump pulled 12.8 amps Discharge pump pulled 10.7 amps Panel is aged -Distribution Box: Unable to locate dbox -Drain Field: No signs of surfacing in drainfield area | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | Dec 30 1899 12:55PM
04/04/2023 | Alternative | Reportable Incident | 199-13-0034 | York | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Norweco Singulair ATU | Norweco Singulair ATU | Pump | Pressure | Trenches | Not Applicable | 750.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] |  | YES | [17 empty] | System 2 has absorption field failure - attempted to locate end of laterals to flush, scour and clean LPP pipe. Found entire field flooded, soil, gravel black - unable to conduct evaluation. Absorption field Failure - recommend primary septic tank, processing tank, and pump tank be pumped empty and go on a routine pump & haul until soil evaluation and engineering design for repair can be conducted / completed. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/05/2023 | Dec 30 1899 9:30AM
11/08/2023 | Alternative | RoutineScheduled | 150-17-0078 | King William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 1.000000 | 1500 | Clearstream ATU |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","SludgeScum Accumulation","Level Sensor Operation"] | NA | Musty | Cloudy |  |  | 55.000000 | [11 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/21/2023 | 10:35 PM
01/06/2023 |  | Initial Visit | 075-STS-32218 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 290.000000 |  | 5000.000000 | [5 empty] | Contractor contacted us due to some problems. Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Re-installed the UV correctly. Appears to be low voltage wire in the panel - owner should have an electrician check it out. The timer is set to 2 minutes every 2 hours. Took initial BOD and Fecal samples. NOTE : The BOD and Fecal samples were high - system should function properly after service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/06/2023 | Jan 1 1900 12:30PM
06/06/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Distribution Pump Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Distribution Pump Operation","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/21/2023 | 12:31 PM
08/05/2023 | Alternative | RoutineScheduled | 019-STS-26497 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | YES | [17 empty] | Annual inspection. Septic Tank - First section - 8" solids crust, 6" solids on bottom. Second section - 1" solids crust, 10" solids on bottom. Recirculation portion of treatment unit - 0" of solids. Discharge portion of treatment unit - 10" of solids. Discharge pump tank - 8" of solids. Cleaned septic tank filter. Flushed treatment unit spray manifold. Flushed drip manifold spin filter. Tested floats, pumps and alarm. Septic tank and treatment unit need to be pumped out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/06/2023 | 07:03 PM
05/16/2023 |  | Reportable Incident | 228-14-0463 A | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/16/2023 | Jan 1 1900 5:00PM
09/27/2023 | Alternative |  | 18-100-0472 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 12:00 AM
02/02/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.300000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2023 | 08:00 AM
08/03/2023 | Alternative | RoutineScheduled | 181-02-0294 (LEGACY ALT. SYSTEM) | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NO | [17 empty] | The system did not need to be pumped. The blower and spin filters were both cleaned. The treatment unit was in operating condition. The controls were operating as designed. There were no visible leaks in the leech field. There was return effluent returning to the pump tank so the drip field was operating as designed. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/16/2023 | 12:25 PM
04/27/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The trees were removed from the ends of the lines. DSS verified that the lines were not impacted. The system appears to be functioning as designed at this time. Recommend homeowner monitor that area and notify if there are any changes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/09/2023 | Alternative |  | 099-13-0093-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance | 179-12-0241-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend replacing the boards that mount the American Manufacturing control panel. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
03/24/2023 |  | Reportable Incident | NYII-B9RMWK | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/24/2023 | Jan 1 1900 10:00AM
07/10/2023 | Alternative | Initial Visit |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip | Not Applicable |  | ["None"] | [] | [18 empty] | system start up | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | 12:00 AM
09/11/2023 | Alternative | RoutineScheduled Component Maintenance | 182-04-0454 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 09/11/2023 |  | 3.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
02/28/2023 | Alternative | Reportable Incident | 133-STS-105902 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | COSS - Maintenance - GMP2018-02 Replaced conveyance line with new 4" PVC. Replaced distribution box with new 8 port concrete DBox. Spliced to existing header lines. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/01/2023 | 10:00 AM
04/24/2023 |  | RoutineScheduled | 02-113-116 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/24/2023 | 12:00 AM
06/19/2023 | Alternative | Routine/Scheduled | 05-163-0046 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Septic Tank Baffles | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - no riser access - effluent screen serviced. Aeration tank - normal level - mixing present - compressor serviced. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | Dec 30 1899 11:15AM
06/07/2023 | Alternative | RoutineScheduled | SD-05-41 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 65.600000 | ["SludgeScum Accumulation","Attached Growth Medium"] | ["SludgeScum Accumulation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/13/2023 | 06:05 PM
04/17/2023 |  | Routine/Scheduled | {FIPSCode}-STS-3228 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | Jan 1 1900 10:05AM
01/04/2023 |  | Routine/Scheduled | 228-04-1181 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/04/2023 | Jan 1 1900 1:01PM
02/03/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Installed new sample box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 10:55 AM
04/12/2023 |  | RoutineScheduled |  | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | new blower pumped redone mulch bad | This AOSS should now return to normal function after having provided the above state routine maintenance | 05/22/2023 | 11:15 AM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance | 107-00-0243 (LEGACY ALT. SYSTEM) | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 06/27/2023 |  | 7.000000 | [5 empty] | Will be sent separately | Inspected | Inlet clogged was repaired Primary tank pumped Lab sample normal | This AOSS should now return to normal function after having provided the above state routine maintenance | 08/23/2023 | 06:57 AM
06/08/2023 | Alternative | Reportable Incident | 136-15-0014 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Peatmoss Biofilter Changeout. 06/05/2023 - septic tank pumped for storage - effluent screen replaced. 06/08/2023 - Removed spent biofilter media and replaced with new. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/09/2023 | 06:45 AM
10/10/2023 | Alternative | Routine/Scheduled | 03-142-0335 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | Filter cleaned. Peat checked. Sample chamber dry. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/10/2023 | Dec 30 1899 9:48AM
11/06/2023 | Alternative | RoutineScheduled Component Maintenance | 179-14-0209-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
08/15/2023 | Alternative | RoutineScheduled | 132-05-0294 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Norweco 960 |  | Pump | Pressure | Drip | Not Applicable | 150.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | 12:00 PM
09/13/2023 | Alternative | RoutineScheduled | 06-125-178 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
05/26/2023 | Alternative | Reportable Incident | 073-STS-105717 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 750 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | [17 empty] | Pumped Out | COSS - Maintenance - GMP2018-02 Pumped septic tank empty for repairs. Replaced terracotta conveyance line with 4" PVC Installed cannister style effluent screen. Installed access risers to grade. Replaced DBox with new 8 port concrete DBox Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 11:00 AM
09/28/2023 | Alternative | Routine/Scheduled | 093-09-0045 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/28/2023 | Dec 30 1899 11:00AM
05/11/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-90443 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
03/31/2023 |  | Reportable Incident | {FIPSCode}-STS-2316 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [17 empty] | Replaced diffuser, aerator, Zoehler 152 pump, on/off float, alarm float, & hose bib | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/31/2023 | Jan 1 1900 7:30AM
03/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 2.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
05/23/2023 | Alternative | RoutineScheduled | 143-STS-16984 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 4.000000 | 6000 | None |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge levels-2-4" scum layer on top-6-10" sludge on bottom in Septic tank on left side of street -even Septic Tanks on left side of the street had 2-4" scum and 10-20" sludge- No pumping needed this year. System appear fully operational. Pump tank no scum and 10-12" sludge- Both pumps are operational- System control panel recently replaced- reduce the Fat oil and grease in the system. Levels are correct, Pittless adapter shows rust on pump stem. Reduce Wipes used in the system | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
02/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 2.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Water Meter Readings: 01/10/2023 7585000 02/06/2023 7600700 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2023 | 08:47 AM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/17/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the alarm going off. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the UV light bulb. Changed the filter in the aerator and changed the mesh screen in the spinfilter (screen was pretty dirty). Need to pump and clean the Clearstream tank and pump tank. Need to check the water softener to make sure it is not discharging into the septic system. The timer is set to 6 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/17/2023 | Dec 30 1899 12:00PM
05/22/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/30/2023 | 09:36 AM
08/09/2023 | Alternative | Reportable Incident | 800-STS-13213 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Changed the filter in the aerator. Replaced relay in the control panel (pump was running constantly) and wired pump through the float. The septic tank needs to be pumped out as well as the Clearstream tank. The timer is set to 2.5 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/09/2023 | Dec 30 1899 11:30AM
01/30/2023 |  |  | 07-113-154 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/30/2023 | [7 empty] | Will be sent separately |  | BOD: BDL TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | 12:00 AM
03/23/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | septic/atu tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
03/27/2023 |  | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 01:42 PM
09/20/2023 | Alternative | Routine/Scheduled | 151-11-0009 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level Has less than 1" of solids with about 6" of sludge -Discharge/Pump Tank: At normal level Pump and floats working -Aeration: At normal level Has about 2" of suspended solids Pulled and cleaned wier and defuser -Air Pump/Blower: Working properly Pulled and cleaned filter -Control Panel: Working properly Visual and audible alarms working -Distribution Box: Plastic dbox at grade At normal level All lines balanced -Drain Field: Showing no signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/06/2023 | 02:01 PM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Hydro-Action ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/11/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1530 | Microfast |  | Pump | Pressure | Drip |  | 300.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 12:09 PM
12/19/2023 | Alternative | RoutineScheduled | 13-120-0371A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1750 | 1000 | 750 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Distribution Pump Operation","SludgeScum Accumulation","Dispersal System Operation","Level Sensor Operation","Effluent Screens"] | YES | None | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | Dec 30 1899 9:00AM
04/21/2023 | Alternative | Routine/Scheduled | C13-180-0011 | Roanoke City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/21/2023 | Jan 1 1900 11:30AM
03/27/2023 |  | Routine/Scheduled | 228-15-0435 | Virginia Beach | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/27/2023 | Jan 1 1900 10:40AM
10/23/2023 | Alternative | RoutineScheduled | 00-197-A3 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/06/2023 | Alternative | RoutineScheduled | 2013-143-0156 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/06/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 750 | Treatment Level 1 |  | Gravity | Gravity | Discharge | Not Applicable |  | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | NA | Septic | Cloudy | [14 empty] | Inspected | No Effluent was seen at discharge point pipe. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | Jan 1 1900 5:00PM
05/04/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | MicroFast needs pumping. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | Dec 30 1899 12:05PM
08/15/2023 | Alternative |  | 17-142-0449 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
06/01/2023 | Alternative | RoutineScheduled Component Maintenance | 154-15-0090 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity |  | UV |  | ["Disinfection" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | ["Disinfection" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
06/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was replaced. Aquaworx bugs were replaced. Bristle filter was added. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/15/2023 | Alternative | RoutineScheduled | 132-15-0055 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2024 | 12:00 AM
02/23/2023 |  | RoutineScheduled | 179-09-0056-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Trees growing on drainfield. Will follow up with customer. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
05/16/2023 |  | RoutineScheduled | 153-STS-20344 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
07/06/2023 | Alternative | RoutineScheduled | 109-09-0237 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Whitewater |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Rebuilt and replace air blower for treatment unit and provided a spare rebuilt on site as well. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/30/2023 | 09:30 AM
05/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Mound | UV |  | ["Level Sensor Operation","SludgeScum Accumulation","Disinfection","BlowerCompressorAerator Operation"] | ["Level Sensor Operation","Disinfection","BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-12"sludge 3"scum/ Microfast-6"sludge/ Pump Tank-0"sludge/ Recommend pump out of the Septic Microfast Tank due to scum migrating to the Microfast side/ Replaced faulty Redundant Off and Timer Enable floats (stuck in closed position) Controls, pump, floats and alarms now functioning properly/ Blower air filter cleaned and blower working correctly/ UV-Light sleeve cleaned and light working properly/ Counts: Pump-2120 ETM-386h 45m/ Peak-18 ETM-13h 19m/ High-26/ Watermeter-61,035.55/ No breakout or spongy areas on the drip mound areas. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
07/21/2023 | Alternative |  | 162-07-0154 | Nelson | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Blue Ridge | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Replaced blower | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/21/2023 | 12:00 AM
03/24/2023 |  | RoutineScheduled |  | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Blue Ridge | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
02/13/2023 |  | RoutineScheduled | SP-05-370 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | As noted previously, the drainfield is overgrown with trees & bushes. This area should be cleared and maintained in a mowed condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
02/07/2023 |  | Follow-Up | 234-15-216 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Control Operation","Disinfection"] | ["Control Operation","Disinfection"] | N/A | [17 empty] | Replaced UV ballast and UV bulb | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/07/2023 | Jan 1 1900 10:00AM
03/20/2023 | Alternative | Routine/Scheduled | 136-04-0405 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level Processing Tank - RSV, recirc pump and effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/21/2023 | 08:00 AM
11/24/2023 | Alternative | RoutineScheduled Component Maintenance | 154-05-0614 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
06/01/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-287 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected | Defective float was replaced. We recommend adding topsoil to the drip dispersal system where tubing is visual. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
11/03/2023 | Alternative | Routine/Scheduled | 179-18-029 | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Advanced Septic |  | Pump | Pressure | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 45.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/03/2023 | 06:05 PM
06/27/2023 | Alternative | Follow-Up Component Maintenance | 179-09-0104-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [7 empty] | 06/27/2023 |  | 63.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
11/16/2023 | Alternative | RoutineScheduled |  | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | trash | Microfast | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/02/2024 | 11:30 AM
08/01/2023 | Alternative |  | 12-113-163 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 08/01/2023 |  | 5.450000 |  |  | 1.900000 |  |  | Will be sent separately |  | BOD: 5.45 TSS: 1.90 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/01/2023 | 12:00 AM
12/01/2023 | Alternative | RoutineScheduled | 159-12-083 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/29/2023 | 12:00 AM
01/04/2023 |  | Initial Visit | 07-160-0229 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner |  |  |  |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | Septic | [15 empty] | Inspected | - recommend tank being pumped/cleaned - if alarm continues, recommend replacing blower | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/04/2023 | 12:00 AM
01/31/2023 |  | Routine/Scheduled | 550-STS-6450 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 02/06/2023 |  | 2.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | Jan 1 1900 7:35AM
08/18/2023 | Alternative | Follow-Up Component Maintenance | SP-04-537 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Reattached Advantex pod lid to pod with stainless steel screws. Replaced gas struts. Assisted pumper with pump out of Recirc tank and refilled with water to proper operating level. Replaced air vent cap. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
10/09/2023 | Alternative | RoutineScheduled Component Maintenance | 015-STS-337418 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
07/07/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-5817 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/07/2023 | Dec 30 1899 1:34PM
07/27/2023 | Alternative | Initial Visit | 128-05-191 | Essex | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit - Alarm Condition. Primary septic tank - high level on arrival - effluent screen serviced. - riser damaged and should be replaced. Aeration Tank - no mixing present - compressor has blown diaphragms - requires replacement or rebuild. Pump Tank - discharge pump failure - on/off float sensor failed - Control panel in poor condition. DBox - did not locate - request FOIA for permit documents | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/31/2023 | 07:15 AM
10/27/2023 | Alternative | Routine/Scheduled |  | Sussex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/27/2023 | Dec 30 1899 10:24AM
05/02/2023 | Alternative | RoutineScheduled | 175-13-0134 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
07/11/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Mckim Septic and Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | [] | NA | [17 empty] | Replaced 3 pod lids and 3 grids. a tree had fallen and damaged them Septic system is in working condition at this time | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/20/2023 | Dec 30 1899 7:45AM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
03/03/2023 | Alternative | RoutineScheduled | 061-16-250 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation"] | ["Level Sensor Operation" ,"Control Operation"] | NA |  | Clear | [13 empty] | Will be sent separately | Inspected | Biweekly inspection. In the past 11 days, the system pumped an average of 1,140 gals/day at 339.1 gals/cycle (avg.) for a total of 12,549 gallons. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
04/12/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced UV bulb, ballast & glass housing. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/02/2023 | Dec 30 1899 4:23AM
02/28/2023 |  | RoutineScheduled | 132-10-0041 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
09/22/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and pumping | 1942001330 | Michelle | McKim | 2.000000 |  | 1500 |  | Pump | Pressure | Drip | UV |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 2:45PM
11/16/2023 | Alternative | RoutineScheduled | 08-192-104 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/16/2023 | 12:00 AM
06/01/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.700000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/13/2023 | 01:15 PM
04/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/15/2023 | Alternative | Routine/Scheduled | 15-120-0268A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component Normal level 2 in of sludge 1 in of solids Pulled and cleaned filter No signs of infiltration Recirculation Tank Condition of above Component Notes for above Component Normal level 4 in of suspended solids Tested floats and pump all working as should Pulled and cleaned pump All plumbing intact and pump moving water properly Discharge/Pump Tank Condition of above Component Notes for above Component Normal level 4 in of suspended solids Loose connection for on float in jbox remade all connections verified everything was functional Pulled and cleaned pump All plumbing intact and pump moving water properly Uv bulb burnt out Media Sheets Condition of above Component Notes for above Component Lateral intact brushed and flushed Spray wheels where not dispersing water properly due to being dirty and lateral clogged Now working as should Sprayed sheets clean no bridging or standing water Control Panel Condition of above Component Notes for above Component 120 volts coming in All visual and audible alarms functional Discharge pump pulled 11.9 amps Recirc pump pulled 8.2 amps All components working as should Distribution Box Condition of above Component Notes for above Component Normal level 4 lines all intact and taking water properly Speed balancers intact and functional No cracks or deterioration Drain Field Condition of above Component Notes for above Component No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | Dec 30 1899 10:25AM
02/07/2023 |  |  | 06-197-A9 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 0.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear |  |  |  | 0.000000 | The tablets are installed now | [10 empty] | Tablets in the chambers now | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/07/2023 | 12:00 AM
03/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | Delta Environmental Products, DF Series | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/13/2023 | 11:23 AM
07/03/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-558 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend mowing the drainfield area and maintaining it in a mowed condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
03/10/2023 |  | RoutineScheduled |  | Frederick | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","SludgeScum Accumulation","Septic Tank Baffles","Level Sensor Operation","Distribution Pump Operation","Dispersal System Operation","BlowerCompressorAerator Operation","Control Operation","Auxiliary Filter"] | NA | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/13/2023 | 06:55 AM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter"] | ["Effluent Screens" ,"Auxiliary Filter"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/30/2023 | 10:30 AM
07/27/2023 | Alternative |  | 05-113-031 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/27/2023 |  | 6.300000 |  |  | 13.000000 |  |  | Will be sent separately |  | BOD: 6.30 TSS: 13.0 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/27/2023 | 12:00 AM
05/15/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Whitewater |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Called due to an alarm- Replaced Clogged spin filter, reglued pump pipe stem which had separated after pulling pump and cleaning the intlet screen.Pump reading 947,500 versus 947,350 last visit a month ago- | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
01/16/2023 |  | RoutineScheduled | 153-STS-20274 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank | Delta ATU to Pump Tank | Pump | Pressure | Discharge | Not Applicable |  | ["Other"] | ["Other"] | NO | [17 empty] | Septic Tank-4"sludge 2"scum/ ATU-4"sludge 4"scum/ Pump Tank to Sand filter-1"sludge 0"scum/ Turned sand in the sand filter which is in good condition- no ponding/ This system is a spray discharge system- spray functioning properly/ Controls, pump, floats and alarms functioning properly/ Blower air filter cleaned and blower working properly/ Counts: Pump-777 ETM-295h 55m/ Peak-21/ High-20 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/19/2023 | Alternative | Pump-Out Only | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 | 1250 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | Dec 30 1899 11:00AM
03/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend moving the newer tree that is in close proximity to the drainfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/01/2023 |  |  | 2004-143-0285 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Puraflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Pumped Out | Replaced pump | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | 12:00 AM
04/27/2023 |  | Routine/Scheduled | 550-STS-6424 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/27/2023 | Jan 1 1900 12:50PM
10/06/2023 | Alternative | RoutineScheduled | 107-13-0145 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
03/16/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
10/03/2023 | Alternative |  |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.420000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 04:00 PM
12/16/2023 | Alternative | Reportable Incident | 14-118-0020 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Opened system found system above normal level. Pulled and found dirty spin filter installed new filter Pumped system down and closed system up | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | Dec 30 1899 10:29AM
01/09/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
11/27/2023 | Alternative | Reportable Incident Component Maintenance | 179-STS-88745 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to faikled discharge pump. Replaced failed pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
12/27/2023 | Alternative | RoutineScheduled | 12-177-1030 | Pulaski | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | 1.000000 | 1500 | MICROFAST |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | [16 empty] | Will be sent separately | Inspected | Annual Inspection of Alternative Septic System This system is functioning but not as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Components are recommended to be repaired/upgraded. - recommend full septic system evaluation as next steps | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/04/2024 | 12:00 AM
05/22/2023 |  | RoutineScheduled | 175-04-0676 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Mound | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-4"sludge 2"scum/ Microfast-0"sludge/ Pump Tank-0"sludge/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-61211 ETM-62504/ Watermeter-178,029.5/ No breakout or spongy areas on the mound. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/16/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | Jan 1 1900 12:26PM
05/23/2023 |  |  | 127-STS-33632 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Multi Flo |  | Gravity | Gravity | Trenches |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/23/2023 | 12:00 AM
09/13/2023 | Alternative | RoutineScheduled | 13-125-076 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | CLEARSTREAM |  | Gravity | Gravity | Drip | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
04/14/2023 | Alternative | Routine/Scheduled | C06-180-0073 | Roanoke City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | Jan 1 1900 1:30PM
06/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
03/29/2023 |  | Routine/Scheduled | 11-120-0344A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/29/2023 | Jan 1 1900 1:01PM
10/13/2023 | Alternative | Pump-Out Only | 11-142-0304 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [16 empty] | Pumped Out | Supervised pump out of 1000 gallon septic tank/ ATU tank performed by CWS. Septic tank had been retrofitted with a Retrofast ATU unit. Vac truck will need to bring water and refill the tank after the peat change has been completed. Aerator has been unplugged and will need to be plugged back in after the tank has been refilled | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | Dec 30 1899 8:04AM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance | 033-STS-87361 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
02/06/2023 |  | RoutineScheduled |  | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
09/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
08/14/2023 | Alternative | RoutineScheduled Component Maintenance | 177-17-0150-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NO | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/25/2023 | Alternative | RoutineScheduled | 061-19-049 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | MircoFast |  | Pump | Pressure | Drip | UV |  | ["Attached Growth Medium","SludgeScum Accumulation","Septic Tank Baffles","BlowerCompressorAerator Operation"] | ["SludgeScum Accumulation","Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection"] | NA | [16 empty] | Pumped Out | System was Pump Out by Virginia Septic | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/15/2023 | 08:00 AM
06/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/14/2023 | Alternative | Reportable Incident Component Maintenance | SD-04-161 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Control Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | High level alarm. On arrival, contactor was pulled in but pump was not running. Hot wire connection at tank was loose/ burnt/ corroded. Stripped all pump wires and all float switch wires (similar condition) and installed new wire nuts. System pumped itself out of alarm (with override) at a reasonable amp draw. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/18/2023 | 11:45 AM
05/22/2023 | Alternative | RoutineScheduled | 171-09-0201 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Ecoflo |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | [16 empty] | Inspected | Sludge level-under 1" scum layer on top-12" sludge on bottom in Septic tank - Cleaned Effluent filter- Peat moss in shows its age, peat was ponding in all 4 quadrants and some roots observed in lower half when tunring the peat. We turned the peat moss in all 4 quadrants and it broke up and drains better after turninging. tipping tray is good and effluent filter has broken handle. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
08/18/2023 | Alternative | Routine/Scheduled |  | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Aeration Tank - normal level - mixing present - compressor serviced. PUmp Tank - float sensors, pump and controls operating. Drip field - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | 10:30 AM
03/14/2023 |  | RoutineScheduled | VAG408315 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.510000 |  |  | 0.610000 |  | 03/14/2023 |  | 40.000000 |  |  | 16.600000 |  |  |  |  | BOD is 40 , will resample. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/30/2023 | 08:40 AM
03/10/2023 |  | RoutineScheduled | 179-STS-89329 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection, light rain. Most of zone 2 seemed soggy and there were a couple of silver dollar sized wet spots. Dug up one of those wet spots, emitter dripping normally. Tubing had 10.5" of cover, plans called for 12". Site should be visited after 4 days of no rain. If no improvement, owner should probably contact the original AOSE for an evaluation. Advantex treatment is good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
04/26/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | 12:00 AM
05/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 11:24 AM
04/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/23/2023 | Alternative | Follow-Up |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | [9 empty] | Dispersal System Operation | Dispersal System Operation | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/27/2023 | 12:11 PM
04/14/2023 |  |  | 124-STS-2379 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Rappahannock |  | 1942001165 | Michele | Ware | [9 empty] | [] | [] | [17 empty] | Inspected | No site visit day or inspection details entered. Believe this was entered by mistake. NO septic records found for this property either. MWEBB | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/11/2021 | 06:12 AM
04/26/2023 |  | Routine/Scheduled | 234-13-32 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | Jan 1 1900 7:50AM
04/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The septic/atu tank needs pumped out. The drain field needs mowed with a mower not bush hogged. Not able to inspect it. The zones will not pressurize. Once field is mowed we will need to inspect and find where brakes are. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
03/29/2023 | Alternative | RoutineScheduled | 133-STS-101233 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/11/2023 |  |  | 124-STS-2379 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Rappahannock | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out | Address does not exist. No tax map to go off of. Tried typing in owner's name in Caroline database, no results. No results googling owners name and road name either. MWEBB 5/3/23 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
07/05/2023 | Alternative | Routine/Scheduled | 10-160-0197 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | 10:15 AM
11/28/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection"] | ["BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Septic | Cloudy | [13 empty] | Will be sent separately | Inspected | Upon arrival found blower and UV unit turned off. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 12/06/2023 | Dec 30 1899 9:34AM
07/04/2023 | Alternative | RoutineScheduled | 133 04 1026 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | BioWheel |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | June 2023 monthly report. Total flow for month of June 2023 - 201,850 gallons. Average daily flow- 6,728 gallons | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | 07:03 PM
05/18/2023 |  | Routine/Scheduled | 175-03-0009 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Orenco Advantex |  | Gravity | Gravity | Trenches |  | 600.000000 | None | None | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | 10:30 AM
05/26/2023 | Alternative | RoutineScheduled | 166-02-138 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Multiflo |  | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | [] | [18 empty] | The system needs a new blower and the septic tank treatment tank needs pumping. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 12:00 AM
05/15/2023 |  | RoutineScheduled | 2099-05-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Distribution Pump Operation","Level Sensor Operation"] | YES | Musty | Clear | 7.300000 |  |  | 1.800000 |  | 05/25/2023 | Sample Chamber | 21.000000 |  |  | 8.800000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/07/2023 | 12:00 AM
03/07/2023 |  | Routine/Scheduled | 087-STS-6119 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Processing tank - recirc - recirc pump, media drapes, spray grid serviced. Processing tank - discharge - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | 09:00 AM
02/03/2023 |  | Routine/Scheduled | 234-17-474 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | Jan 1 1900 9:43AM
04/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/22/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
05/22/2023 |  | Routine/Scheduled | {FIPSCode}-STS-2316 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/22/2023 | Jan 1 1900 11:50AM
06/09/2023 | Alternative | Reportable Incident | 234-14-149 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Replaced pump | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/09/2023 | Dec 30 1899 10:00AM
07/17/2023 | Alternative | Routine/Scheduled | 234-12-34 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [13 empty] | Replaced diffuser and aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/17/2023 | Dec 30 1899 7:58AM
01/30/2023 |  | Follow-Up | SWP-05-118 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Follow up. Replaced 30" concrete lid on pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
04/10/2023 | Alternative | RoutineScheduled | 133-STS-96766 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/13/2023 |  | Routine/Scheduled | 067-STS-38058 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 11:45 AM
06/30/2023 | Alternative | Routine/Scheduled | 08-120-0400A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/30/2023 | Dec 30 1899 11:49AM
10/09/2023 | Alternative | RoutineScheduled | 00-125-011 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 4 - Blue Crystal tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/09/2023 | 12:00 AM
10/17/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | NA | [7 empty] | 10/17/2023 | Sample Chamber | 6.000000 | [5 empty] | Attached to this report |  | Septic Tank-10"sludge 3"scum/ Microfast ATU-16"sludge (Clogged media) Pump Tank-2"sludge 0"scum/ Septic-Microfast Tank requires chemical cleaning and pump out/ Blower air filter cleaned and blower is working correctly/ Replaced a faulty off float/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-404 ETM-25h 7m/ Pump2-394 ETM-24h 28m/ Peak-5/ High counts-7/ No breakout or spongy areas on the drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/09/2023 |  | RoutineScheduled |  | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [7 empty] | 03/09/2023 |  | 273.000000 | [5 empty] | Will be sent separately | Inspected | blower was off and was turned back on | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
03/06/2023 |  | RoutineScheduled | 153-STS-19043 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Clearstream | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Zoner is cracked & needs replacement. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/31/2023 | 12:26 PM
01/30/2023 |  | RoutineScheduled | 17-192-006 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Clearstream |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/30/2023 | 12:00 AM
12/07/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-91688 | Stafford | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | UV |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Risers septic tank are taking on ground water infiltration and need to be resealed. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 12/20/2023 | 02:30 PM
03/21/2023 |  | Reportable Incident | 228-18-0352 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Owner called due to an alarm going off. Replaced spinfilter screen. Cleaned pump screen. Ran 1/2" pipe from pump tank to inlet tee in septic tank for spinfilter return line. Pump tank may need to be cleaned. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/21/2023 | Jan 1 1900 12:00PM
12/20/2023 | Alternative | RoutineScheduled | 121-STS-12976 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | 2.000000 | 2000 | Aquasafe |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | Septic | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 12:00 AM
02/24/2023 |  | RoutineScheduled | VAG408068 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Sand |  |  |  | Discharge |  |  | ["None"] | ["None"] | [18 empty] | no discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/24/2023 | 12:00 AM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | Dec 30 1899 11:24AM
06/07/2023 | Alternative | RoutineScheduled | 02-173-165 | Prince Edward | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Bobby's septic inspections LLC | 1942001548 | Robert | Burnett | 3.000000 | 1000 | Grease trap | Microfast | Gravity | Gravity | Trenches | Not Applicable | 600.000000 | ["BlowerCompressorAerator Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | None | Clear | 6.700000 |  | 0.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | Dec 30 1899 7:50AM
05/31/2023 | Alternative | Reportable Incident Component Maintenance | 175-08-0286 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced N98 effluent pump, 3 Orenco & 3 blue control floats. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
03/30/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"SludgeScum Accumulation"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 12:48 PM
08/08/2023 | Alternative | RoutineScheduled Component Maintenance | 182-06-0179 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 08/08/2023 |  | 13.000000 | [5 empty] | Will be sent separately | Inspected | Minimal air supply added cleaner Leak in drainfield repaired | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | There is no power getting to the Norweco control panel. Aerator/alarm are not functioning due to this. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
10/23/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/23/2023 | Dec 30 1899 8:35AM
12/01/2023 | Alternative | Pump-Out Only | 05-160-0224 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner |  |  | WHITEWATER | [6 empty] | [] | [] | [17 empty] | Pumped Out | - SERVICED TANKS FOR ADVANCED ENVIRONMENTAL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 12:00 AM
03/09/2023 |  |  | 07-142-0037 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex | [6 empty] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 12:00 AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/17/2023 | 12:46 PM
01/30/2023 |  | Routine/Scheduled | {FIPSCode}-STS-1772 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | Jan 1 1900 12:30PM
02/02/2023 |  |  | 196-08-102 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
11/22/2023 | Alternative | Routine/Scheduled | 800-08-0175 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Flushed and cleaned effluent screen. Not due for pump out. No riser access for effluent screen. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. Discharge pump has met life expectancy. Discharge pump plumbing has met life expectancy. Discharge floats are not properly secured and have met life expectancy. Discharge riser is damaged -Aeration: Water level normal. Flushed and cleaned effluent screen. Not due for pump out -Air Pump/Blower: Checked and confirmed aerator is functioning properly. Flushed and cleaned air intake filter -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Control panel has met life expectancy. -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact. -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | Dec 30 1899 9:14AM
12/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/07/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-90035 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
06/07/2023 | Alternative |  | 10-183-016 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 06/07/2023 |  | 6.090000 | [5 empty] | Will be sent separately |  | BOD: 6.09 TSS: BDL | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/07/2023 | 12:00 AM
09/08/2023 | Alternative | Routine/Scheduled | S12-180-0042 | Roanoke City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | EcoPod |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | Dec 30 1899 10:00AM
11/07/2023 | Alternative | Initial Visit |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the yellow light being on. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and diffuser in both Clearstreams, cleaned the UV light bulb, and cleaned the filter in the septic tank. Replaced the filter in both aerators and replaced the mesh screen in the spinfilter. The grade on the pipe in the Clearstreams need to be addressed - pushed them down as far as the tech could. The timer is set to 5 minutes every 2 hours. Did not take samples. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/07/2023 | Dec 30 1899 9:30AM
09/13/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0065-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. signs of high level in recirc tank. Strong musty smell but clear treatment. Added Root-x in D-box. Recirc tank most likely will need pump out next year due to sludge levels. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
03/08/2023 | Alternative | Routine/Scheduled | 136-12-0258 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank- effluent screen serviced Pump Basin - float sensors, pump and controls operating. Biofilter - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/09/2023 | 08:15 AM
04/08/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/09/2023 | 12:00 AM
11/16/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Found - Blower Off upon arrival UV light not working Repairs on Site: Installed a new UV light New UV light plug | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/01/2023 | Dec 30 1899 10:33AM
08/07/2023 | Alternative | Routine/Scheduled | 800-08-0233 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | Dec 30 1899 11:40AM
11/13/2023 | Alternative | Routine/Scheduled | 095-STS-5091 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level Has 5" of sludge and about 8" of solids build up There is also Grease and debris building up in the tee Recommend pumping -Discharge/Pump Tank: At normal level Pump and floats functioning properly -Aeration: At normal level Has right at 15" of suspended solids Should be pumped and refilled soon -Air Pump/Blower: Working properly Pulled and cleaned filter -Control Panel: Both discharge and aerator panels working properly Visual and audible alarms working Aerator pulling 2.78amps Discharge pump pulling 9.23amps -Distribution Box: At normal level All lines balanced -Drain Field: Showing no signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/15/2023 | Dec 30 1899 8:48AM
04/20/2023 |  | Reportable Incident |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Installed Repair - VDH Permit #: 136-23-0082 Pumped empty, crushed and removed septic tank, and pump tank. Installed new Infiltrator IM1060 tanks as septic tank and pump tank in same general location. Installed new 2 breaker demand dosed controls, float sensors, re-used existing pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/24/2023 | 07:00 AM
03/17/2023 |  | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Microfast |  | Pump | Pressure | Mound |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | 12:40 PM
01/27/2023 |  | Pump-Out Only | 121-STS-12047 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner |  |  | Whitewater | [6 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | 12:00 AM
05/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | UV light is not functioning as designed | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
04/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
02/15/2023 |  | RoutineScheduled | 179-STS-88068 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Control Operation"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Level Sensor Operation" ,"Attached Growth Medium"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Pump tank almost in high level alarm due to leak around return pipe coming into tank. broken tubing in zone #2, repaired tubing and tested again and gallons per minute went back to normal. No more water above surface. Will send proposal to seal leak. RECIRC: HL 7, LL 12, OVERRIDE 110. DISCHARGE: HL 16, LL 11, OVERRIDE 178. ZONE #1- 3.75(12.0FF) ZONE#2- 3.75(11.9FF) | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
07/26/2023 | Alternative | RoutineScheduled | 2016-143-0076 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/19/2023 |  | Follow-Up | 179-STS-89329 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Made follow up visit after speaking to manufacturer and AOSE in reference to 2 wet spots on drip field and lower arv holding water. Manufacturer stated grass must be planted on drip field. I was there in dryer conditions as the prior inspection was done in the rain. Wet spots were no longer there and arv was not holding water. I will make a follow up visit in the summer to verify drip field conditions. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/05/2023 | 07:56 AM
01/18/2023 |  | RoutineScheduled | 182-04-0393 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 1.000000 | 1000 | Best 1 |  | Pump | Pressure | Drip |  |  | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Effluent filter checked and cleaned. Septic tank and treatment unit pumped and cleaned. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/25/2023 | 03:50 PM
05/02/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Water Meter Readings: 03/06/2023 1831100 03/28/2023 1831100 04/04/2023 1831100 04/18/2023 1831100 05/02/2023 1831100 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
03/03/2023 |  | Routine/Scheduled | 095-STS-5875 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. PUmp Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | Jan 1 1900 7:00AM
11/10/2023 | Alternative | RoutineScheduled | SD-03-449 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | Microfast |  | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | YES | Musty | Clear | [15 empty] | No Discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/01/2023 | 09:05 AM
09/19/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-92461 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The drain field area is overgrown. We recommend mowing the drainfield and maintaining it in a mowed condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
08/24/2023 | Alternative | RoutineScheduled | 033-06-0026-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 0-3 0=0 | 0-0 | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear |  |  | 4.000000 | [11 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/24/2023 | 12:00 PM
04/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/02/2023 |  |  | {FIPSCode}-STS-31829 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Norweco | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [18 empty] | Pumping the septic tank on 2/8/23 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | 12:00 AM
03/22/2023 | Alternative | Routine/Scheduled | 04-160-0250 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/22/2023 | 10:15 AM
11/01/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | Dec 30 1899 8:40AM
07/21/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | septic | Eco pure | Pump | Pressure | Drip |  |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | 0 scum , 3" of sludge in septic , filter is clean, eco pure had very little ponding, still filtering through effluent looks good. maybe 1 -2 years left in the peat moss Pump working, field is dry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 02:00 PM
05/20/2023 | Alternative | RoutineScheduled | 12-100-0084 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | AQUASAFE |  | Pump | Pressure | Trenches | UV | 450.000000 | [] | [] | [18 empty] | REPLACED UV LIGHT UNIT. EVERYTHING WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/09/2023 | 12:00 AM
08/24/2023 | Alternative | RoutineScheduled Component Maintenance | 107-08-0509 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Homeowner recently removed media washed and put back into tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
02/28/2023 |  |  | 2006-143-0362 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Microfast | [6 empty] | ["Control Operation","BlowerCompressorAerator Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 12:00 AM
08/23/2023 | Alternative | Routine/Scheduled | 151-12-0052 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1250 | Ecoflo |  | Gravity | Gravity | Pad |  |  | ["Attached Growth Medium","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Effluent Screens","SludgeScum Accumulation"] | YES |  |  |  |  | 35.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/23/2023 | 05:26 PM
08/11/2023 | Alternative | RoutineScheduled Component Maintenance | 175-17-0121 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
11/06/2023 | Alternative | RoutineScheduled | 17-142-0221 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/05/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | Jan 1 1900 7:20PM
08/30/2023 | Alternative |  | SD-09-90 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [18 empty] | See attachment | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 12:00 AM
11/22/2023 | Alternative | RoutineScheduled |  | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 1.000000 | 1000 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","SludgeScum Accumulation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/22/2023 | Dec 30 1899 3:00AM
11/27/2023 | Alternative | RoutineScheduled | 107-04-0629 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Pressure | Trenches | Not Applicable |  | ["Recirculation Pump","Septic Tank Baffles"] | ["Recirculation Pump","Septic Tank Baffles"] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/27/2023 | 12:00 AM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-19254 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
08/10/2023 | Alternative | Routine/Scheduled | 147-16-0035 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream. Changed the filter in the aerator. Replaced the buzzer. The timer is set to 2 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | Dec 30 1899 9:15AM
01/23/2023 |  | RoutineScheduled | SWP-04-281 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | New riser lids were installed on the septic tank. We continue to recommend replacing the riser & lid on the pump tank. We also recommend clearing the entire drainfield and maintaining in a mowed condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
09/29/2023 | Alternative | RoutineScheduled | R15-180-0021 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | MicroFast | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [7 empty] | 09/29/2023 | Pump Chamber | 4.800000 |  |  | 9.500000 |  |  | Attached to this report |  | The system did not need to be pumped. The blower and spin filters were both pulled and cleaned. The effluent filter was pulled and cleaned. The discharge pump was pulled and cleaned. The treatment unit was in good operating condition. The controls were operating as designed. There was return effluent returning to the pump tank so the drip field was operating as designed. There were no visible leaks in the drip field. The BOD and TSS were within the permitted limits. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | Dec 30 1899 5:45PM
11/14/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 12:00 AM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance | 175-07-0389 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance | 175-12-0277 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
06/19/2023 | Alternative | Reportable Incident Component Maintenance | SD-11-168 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Clearstream | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | High level alarm. Spin filter was extremely dirty so that flow was greatly reduced. Pump was almost dead-heading as indicated by the low amp draw and low pump pressures (30 supply, 0 return). Cleaned dirty spin filter and adjusted spin filter flush valve. Ran a couple of cycles back to back while looking for surfacing effluent in dripfield. Dug down at both sites of moving water and replaced failed drip tube adapters. During next test cycle, supply pressure increased to 40 psi, return line 22 psi. No surfacing effluent seen. Owner cut down the cedar trees that were growing on top of the tank. Advised her to apply root kill to the stumps. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
12/01/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Pump | Pressure | Drip |  | 750.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:50 PM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | System appears to be functioning as designed. There was some nitrification down hill on the header lines. The box was uncovered and appeared to be functioning as designed. Recommended to contact the installer and monitor the area and advise of any changes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/08/2023 | Alternative | RoutineScheduled | 18-197-A1 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 1 - 4" Sch. 40 solid cap | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/08/2023 | 12:00 AM
05/24/2023 |  | RoutineScheduled |  | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Sand Filter |  | Gravity | Gravity | Discharge |  |  | [] | [] | NA | [16 empty] | Inspected | Septic Tank trace scum 12-14" sludge - Water level is about 4" high in septic tank, likely is backed up between it and sandfilter with large tree. Roots possible issue.. No flow observed in CL2 or dechlor tanks. unable to confirm location of effluent pipe in creak, No flow. No sample Added root treatment septic tank. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/30/2023 | 09:30 AM
02/02/2023 |  | RoutineScheduled | {FIPSCode}-STS-9611 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/02/2023 | 12:00 AM
01/24/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Siphon | Gravity | Drip | UV |  | ["Effluent Screens" ,"Disinfection"] | ["Disinfection" ,"Effluent Screens"] | YES | [7 empty] | 01/24/2023 |  | 32.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/11/2023 | Dec 30 1899 11:24AM
03/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Effluent pump had failed. It was replaced and the system appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
04/06/2023 |  | RoutineScheduled | SP-04-384 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Small roots in wedge lid still the same and no water infiltrating. Metal bars inside pods corroding pretty bad will need replacement when peat gets replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
09/18/2023 | Alternative | RoutineScheduled Component Maintenance | 047-STS-26243 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
02/28/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 02/28/2023 |  | 26.000000 | [5 empty] | Will be sent separately | Inspected | filter clog cleaned no air supply to media- fixed new blower, valve box, lid, buzzer | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
12/12/2023 | Alternative | Routine/Scheduled | 166-07-078 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Puraflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 45.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 05:15 PM
08/14/2023 | Alternative | Routine/Scheduled | 02-142-0100 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/17/2023 | Dec 30 1899 1:00PM
10/25/2023 | Alternative | RoutineScheduled | 166-04-425 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump | Pressure | Pad | Not Applicable |  | ["Dispersal System Operation"] | ["None"] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/16/2023 |  | RoutineScheduled | 179-11-0239-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Wipes in septic tank (few) | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
11/01/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | Dec 30 1899 11:35AM
02/06/2023 |  | RoutineScheduled | 128-94-036 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/07/2023 | Alternative |  | -STS-91637 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
05/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Mound | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping this year. Recommend evaluating the manifold and repairing/replacing foam filters if necessary. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/01/2023 | Alternative | RoutineScheduled | 13-160-0027 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 |  | Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/26/2023 | 12:00 AM
10/30/2023 | Alternative | RoutineScheduled | 061-STS-21184 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Microfast 0.5 | A | Pump | Pressure | Drip | UV |  | ["Attached Growth Medium","Disinfection"] | ["Control Operation","Disinfection","SludgeScum Accumulation"] | NO | Musty | Clear | [15 empty] | Jett UV light Bulb was replaced during time of inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | 03:00 PM
03/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | K-Rain is cracked and sprays when pump is on. It is scheduled to be replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
06/02/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001527 | Jacob | Hott | 1.000000 | 1500 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/19/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 3.000000 |  | Septic | Puaflo | Pump | Pressure | Trenches | Not Applicable |  | [] | ["Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | [18 empty] | 2" of Scum, 24" of sludge, Recommended having tank pumped before next year, Pump tanks clean, pumps working, alarm working, peat moss looks great, field looks good. Recommended having a alarm put in second tank and verifying that the timers are working. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/20/2023 | 09:00 AM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
01/05/2023 |  | RoutineScheduled | 147-15-0013 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Parley Septic Tank , Inc. | 1942001106 | James | Parsley | 1.000000 |  | Multi Flo |  | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/20/2023 | 12:00 AM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, UC Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/27/2023 | Alternative |  | 162-18-0014 | Nelson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/22/2024 | 12:00 AM
05/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Blue Ridge | SES Mid Atlantic, LLC | 1942001236 | Stuart | Lynn |  |  | Whitewater ATU | Whitewater ATU | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Disinfection" ,"Level Sensor Operation"] | ["Level Sensor Operation" ,"Disinfection" ,"BlowerCompressorAerator Operation"] | NA | None | Clear | [5 empty] | 09/26/2023 | Pump Chamber | 12.000000 |  |  | 8.000000 | 22.000000 |  | Will be sent separately | Inspected | Q# 2023 Report Fix Control VFD 6-15-23 7-17-23 mlynn - S. Michael Lynn - 7/17/2023 6:12:18 AM - Discharge pump repaired: Casino, Steven and Robert meet at Oxford with Tripod to pull and repair discharge pump. Casino take tripod from SES and meet them on site: 7-21*23 Pump out tanks WWTP Secure / Locked: Yes Unusual Odors?: No Alarms upon arrival?: Yes. Dosing Tank 'HIGH LEVEL' and EQ Tank 'HIGH LEVEL'. Blowers and ECOPODS all functioning: No. Level to high. rrothgeb - Robert Rothgeb - Jul 21, 2023 4:09 PM Adjust timers to balance flow. WWTP ecure Blowers and ECOPODS all functioning: Yes. Blower #2 restored and ECOPOD #2 back to normal. 8-21-23 Install Program on new PLC from COx research to replace PLC from Generator malfunction. Program installed system running in auto 9-29-23 rrothgeb - Robert Rothgeb - Sep 22, 2023 10:09 AM Change out Activated Carbon. WWTP Secure / Locked: Yes Unusual Odors?: No Alarms upon arrival?: Yes - Recirc Pumps #1 and #2 Low Level ECOPOD Tanks. Blowers and ECOPODS all functioning: Yes Drianfield walkover: Yes - Okay rrothgeb - Robert Rothgeb - Sep 22, 2023 10:14 AM WWTP Secure and gates locked on arrival: Yes Unusual odors around plant: No Blowers working if present: Yes Any component in Alarm?: Yes - 2. ECOPOD Tanks Low Level. Pump Station Locked if present: Not Applicable Test telemetry system raise all floats for notice for office: Telemetry Not working Drive through community look for alarms and overflows: No alarms identified Community alarms or overflow detail: NA - 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | 01:58 PM
08/18/2023 | Alternative | Routine/Scheduled | 18-120-0236R | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/18/2023 | Dec 30 1899 8:14AM
02/27/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | When arrived the effluent pump was not working. We replaced with the same model. A draw down was done to insure it was pumping as designed. Septic system is in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
04/27/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
12/05/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic/ Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 12/05/2023 | Sample Chamber | 32.000000 | [5 empty] | Attached to this report |  | Septic Tank-6"sludge 8"scum/ Microfast ATU-12"sludge 0"scum/ The Septic-Microfast ATU needs pump out / Blower air filter cleaned and blower working correctly at this time / Need additional 6"riser on the tank/ Sample box requires a 12"lid/ Microfast controls and alarm are functioning properly/ No breakout or spongy areas on the drainfield. Repairs on 12/6/2023: replaced sample box lid/ Added 6" riser to the tank so the lid could be secured properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
11/30/2023 | Alternative | RoutineScheduled | 2005-143-0173 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Ecoflo |  | Pump |  | Trenches |  |  | [] | ["Attached Growth Medium","Distribution Pump Operation","Control Operation","Level Sensor Operation"] |  | None | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/30/2023 | 12:00 AM
01/13/2023 | Alternative | RoutineScheduled | 166-09-072 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Ecoflo |  | Pump |  | Trenches | Not Applicable |  | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | 12:00 AM
01/05/2023 | Alternative | Initial Visit | 159-11-113 | Middlesex | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit - pending FOIA for permit documents. Primary septic tank - normal level - effluent screen serviced. Aeration Tank - normal level - NO MIXING present - Compressor Failed. Pump Tank - pump fail - control panel fail DBox - concrete - intact. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/09/2023 | 07:30 AM
06/15/2023 | Alternative | RoutineScheduled | 175-15-0289 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ Advantex Recirculation Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | [17 empty] | Recirc. Tank in alarm upon arrival: Found recirc. pump wire was disconnected, repaired and now functioning properly/ Septic/ Advantex Recirculation Tank-3"sludge 1"scum/ Pump Tank-2"sludge/ No pump out needed at this time/ Controls, pumps, floats and alarms now functioning properly/ Pump intakes cleaned/ Recirc. pump counts: 25458/ Run hours-1766/ Discharge pump counts: 13448 ETM-1851h 35m/ Watermeter-862,359.41/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
04/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/21/2023 | Alternative | RoutineScheduled | 109-13-0076 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Aqua Klear |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | NA | Musty | [15 empty] | Inspected | Replaced the blower alarm panel due. System alarm is now fully operational- Blower motor is original but fully operational. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/28/2023 | 09:30 AM
12/21/2023 | Alternative |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Advantex | Pump | Pressure | Trenches |  |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | YES | [17 empty] | Little scum, 12" of sludge on inlet side, 6" on outlet side, loose sludge in Advantex. Next time it gets pumped Advantex will need to be cleaned as well. Alarms , pump, floats all working. Bottom discharge float was stuck when arrived. Working when I left. Let the owners now that it could need replaced if it starts causing troubles. R- 3446.5 Runtime, 92849 Cycles, D- 112.6 Run time, 4559 Cycles | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/04/2024 | 10:30 AM
08/23/2023 | Alternative | RoutineScheduled Component Maintenance | 109-STS-34172 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
03/21/2023 |  | RoutineScheduled | 179-18-0199-VU | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance | SD-07-163 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | Annual inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
06/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/28/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 12:00 AM
08/01/2023 | Alternative | RoutineScheduled | VAG408452 | Augusta | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | EZ Treat |  |  | Pressure | Discharge | UV |  | ["Auxiliary Filter","Disinfection","Attached Growth Medium"] | ["Auxiliary Filter","Disinfection","Attached Growth Medium"] | [18 empty] | (2) Ballast cords and bulbs replaced. 8 emitters cleaned that were clogged. Lid replaced on sample port. No discharge at this time | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 08/02/2023 | 12:00 AM
01/18/2023 |  | RoutineScheduled | 177-14-0200-SR | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Gravity | Gravity |  | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection"] | ["BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | Installed new Norweco UV unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
11/02/2023 | Alternative | Routine/Scheduled | 151-03-218 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Ecoflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 50.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | 05:52 PM
02/08/2023 |  | RoutineScheduled |  | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Control Operation"] | NA | [7 empty] | 02/08/2023 |  | 119.000000 | [5 empty] | Will be sent separately | Inspected | blower audible not working, panel replaced pump panel alarm was off new blower panel drainfield leak repair | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
03/24/2023 | Alternative | Initial Visit | 093-13-0111 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Visit. Primary septic tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | Dec 30 1899 7:45AM
07/21/2023 | Alternative | Routine/Scheduled | 234-12-110 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | [15 empty] | Replaced UV unit | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/21/2023 | Dec 30 1899 8:30AM
02/09/2023 |  | RoutineScheduled | 023-STS-42917 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Western Virginia Water Authority | 1942001145 | Michael | Doss |  |  |  |  | Gravity | Pressure | Drip | Not Applicable |  | [] | [] | NA | None | Clear | [5 empty] | 02/09/2023 | Sample Chamber | [9 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | Jan 1 1900 7:40AM
02/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/28/2023 | Alternative | Routine/Scheduled | 199-07-0087 | York | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/28/2023 | Dec 30 1899 8:52AM
01/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Mecklenburg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Southside | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | 12:00 AM
05/10/2023 |  | Routine/Scheduled | 2009-143-0135 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [17 empty] | Checked system operation. The system appears to be operating normally. Cleaned air filter and checked drip function. CT 1455, ETM 101 Hrs 30 min., HL 6, LL 0, Overrides 181 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 12:00 PM
11/14/2023 | Alternative | RoutineScheduled Component Maintenance | 061-STS-26215 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Distribution Pump Operation"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/01/2023 | 10:33 AM
09/22/2023 | Alternative | RoutineScheduled Component Maintenance | 175-14-0128 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
01/20/2023 |  | RoutineScheduled | 175-18-0486 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2023 | 08:47 AM
04/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/09/2023 | Alternative | Reportable Incident | VAG408038 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Gravity | Discharge | Chlorination |  | ["Control Operation","Disinfection"] | ["Control Operation","Disinfection"] | NA | Musty | Clear | [15 empty] | no discharge during visit. Replaced control box | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/06/2023 | 12:00 AM
05/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/31/2023 | Alternative | RoutineScheduled | 154-07-0577 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | 12:00 AM
01/26/2023 |  | RoutineScheduled | SWP-05-163 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | E-Z Treat |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Septic Tank Baffles","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | 03:00 PM
11/20/2023 | Alternative | RoutineScheduled | SD-09-297 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank to Sand Filter to American Drip | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation","Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-5"sludge 1"scum/ Pump Tank-1"sludge/ No pump out needed at this time/ Control panel not functioning properly (Unable to back flush the hydraulic unit) Recommend replacement of the control panel/ Floats and pump is functioning properly/ No pump counts or etm counts register in the control box/ Watermeter counts; 0,198,310/ Sand filter media was turned and is in good condition/ No breakout or spongy areas on the drip field. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
09/01/2023 | Alternative | Initial Visit | 2011-141-43ES | Halifax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Southside | Matthews Sanitation Services Llc | 1942001226 | Brian | Matthews | 6.000000 | 10,000 |  |  | Pump |  | Discharge | Chlorination |  | [] | [] | NA | [15 empty] | Will be sent separately | Pumped Out | WATER TEST HAS BEEN SCHEDULED FOR THE NEXT DISCHARGE EVENT | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/06/2023 | 12:00 AM
01/04/2023 |  |  | 127-STS-33191 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | 12:00 AM
02/20/2023 |  | Routine/Scheduled | 234-15-46 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | Jan 1 1900 11:45AM
01/16/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2023 | Dec 30 1899 8:47AM
06/15/2023 | Alternative | Pump-Out Only | C09-180-0140 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner |  |  | Whitewater | [6 empty] | [] | [] | [18 empty] | - customer does not want to proceed with required maintenance visits | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/16/2023 | 12:00 AM
08/11/2023 | Alternative | Initial Visit | 800-STS-13867 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 4.000000 |  | 6000.000000 | [5 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream and cleaned the UV light bulb. Changed the filter in the aerator. The timer is set to 3.75 minutes every 3 hours. Took initial BOD and Fecal samples. NOTE - Fecal sample was high - system should function properly after service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | Dec 30 1899 8:30AM
05/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank needs pumped out. D-box is broken and will need replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
02/24/2023 | Alternative | Follow-Up Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Dirt has been removed and unit is now serviceable. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2024 | Dec 30 1899 11:49AM
04/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Strongly recommend flushing and balancing lines in the near future | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/15/2023 | Alternative | RoutineScheduled | 150-07-0219 | King William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 3.000000 | 2900 gallons | septic tank | Clearstream | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation","Distribution Pump Operation"] | ["SludgeScum Accumulation","Level Sensor Operation","Distribution Pump Operation","Control Operation","BlowerCompressorAerator Operation"] | NA | Musty | Clear |  |  | 0.000000 | [12 empty] | Septic tank 0" fog, 2" sludge. Clearstream 0% SS. Aerator not running, rebuilt now functioning properly. Pump, alarm, floats, controls operating properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/23/2023 | 08:10 PM
11/14/2023 | Alternative | Pump-Out Only | 157-17-0038 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Pumped and refilled system found aspirator not working properly. Turned over to service expert | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | 10:26 AM
09/05/2023 | Alternative | RoutineScheduled | 182-18-0177 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Presby |  |  | Pressure | Mound |  |  | ["Recirculation Pump","Distribution Pump Operation"] | ["Distribution Pump Operation"] | [18 empty] | pump replaced | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/07/2023 | 12:00 AM
09/07/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 RT |  |  | Pressure | Drip | Not Applicable |  | ["Septic Tank Baffles","Dispersal System Operation"] | ["Dispersal System Operation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | 12:00 AM
03/24/2023 |  | Routine/Scheduled | 810-STS-3966 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/24/2023 | Jan 1 1900 2:55PM
05/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
01/23/2023 |  | RoutineScheduled | 17-195-160-SP | Washington | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 200.000000 | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2023 | 12:00 AM
10/18/2023 | Alternative | RoutineScheduled Component Maintenance | 177-09-0244-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | ["BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
07/28/2023 | Alternative |  | SP-05-437 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
03/17/2023 | Alternative | RoutineScheduled | SD-11-58 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment is crystal clear. Old style panel for blower not alarming any more recommend to replace with new style. Will send proposal. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
02/28/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/22/2023 | Alternative | RoutineScheduled | 165-STS-334005 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Control Operation"] | ["Effluent Screens","Control Operation"] | YES | Musty | Clear | [15 empty] | delayed local alarm | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/06/2023 | 12:00 AM
11/20/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | Dec 30 1899 11:30AM
09/07/2023 | Alternative | Routine/Scheduled | 196-09-154 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | 05:52 PM
11/07/2023 | Alternative | Routine/Scheduled | 041-STS-260605 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [16 empty] | Recommend pump out, septic doctor 804-325-4100 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/07/2023 | Dec 30 1899 11:30AM
07/31/2023 | Alternative | Reportable Incident | {FIPSCode}-STS-2346 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/31/2023 | Dec 30 1899 9:00AM
05/23/2023 | Alternative | RoutineScheduled | 07-173-036 | Prince Edward | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Septic | Delta Whitewater | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | [] | ["SludgeScum Accumulation","Septic Tank Baffles","Level Sensor Operation","BlowerCompressorAerator Operation"] | NA | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/23/2023 | Dec 30 1899 11:15AM
11/27/2023 | Alternative | RoutineScheduled | 087-STS-6124 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Aqau Klear |  | Pump | Pressure | Drip |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Level Sensor Operation","Distribution Pump Operation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/27/2023 | 12:00 AM
11/29/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-157 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Control Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. pump doing 23.6 gallons per minute so we had to adjust run time to get rid of full dose, new run time 1m54s. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
11/17/2023 | Alternative | Pump-Out Only | 18-120-0346AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [16 empty] | Pumped Out | 11/17/23. Arrived open septic tank pumped 1000 gallons | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | Dec 30 1899 10:03AM
09/25/2023 | Alternative | RoutineScheduled | 061-17-206 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | MicroFast | Pump | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [17 empty] | 5' liquid depth. 10" of loose sludge. Cleaned filter on blower was very dirty. pump tank is clean. alarms, floats, blower, pumps working. Monster box visible, field dry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/02/2023 | 12:15 PM
02/17/2023 |  | Initial Visit | 085-STS-34737 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | UV | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit - System Commissioning / Start-up. Primary septic tank - normal level - effluent screen present. Processing Tank - Recirc - float sensors & timers adjusted. Spray grid adjusted. Processing Tank - UV - bulb serviced, and verified operating. Processing Tank - discharge - float sensors, & timers adjusted. DBox - intact and balanced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | Jan 1 1900 10:00AM
04/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 | [8 empty] | [] | ["Attached Growth Medium","Control Operation","Auxiliary Filter","Dispersal System Operation","Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation","Level Sensor Operation","Disinfection","BlowerCompressorAerator Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/20/2023 | Dec 30 1899 5:45PM
05/21/2023 | Alternative | Initial Visit | 136-07-0306 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Virginia Septic Solutions LLC | 1942001500 | Justin | Barker | 1.000000 |  | Ecoflo Biofilter |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/21/2023 | 12:00 AM
03/31/2023 | Alternative | Reportable Incident Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Prince William | Ace Contracting Services, Inc | 1942001120 | Lawrence | Fellenz Jr. | 1.000000 | 2500 | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"SludgeScum Accumulation"] | ["Effluent Screens" ,"Level Sensor Operation" ,"SludgeScum Accumulation"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected | Alarm Float Was Replaced We Pumped Out Septic Tank And Pump Station To Get Excess Sludge Cleaned Out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 03:09 AM
06/02/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001527 | Jacob | Hott | 1.000000 | 2000 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/15/2023 | Alternative | Routine/Scheduled | 157-89-130 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Purasys |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | Musty | Clear | [5 empty] | 02/15/2023 | Sample Chamber | [8 empty] | 180 day system inspection & lab sampling. Primary septic tank - normal level - siphon operating. Aeration / Processing Tank - Sludge return operating. Aeration / Processing Tank - mixing present - submersible aerator serviced. Aeration / Processing Tank - float sensors, pump and controls operating. Lab samples obtained for BOD5 & TSS DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/16/2023 | 07:00 AM
06/05/2023 | Alternative | RoutineScheduled | SD-13-64 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | MircoFast |  | Pump | Pressure | Trenches | Not Applicable |  | ["SludgeScum Accumulation","Attached Growth Medium","BlowerCompressorAerator Operation"] | ["SludgeScum Accumulation","BlowerCompressorAerator Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 05:05 PM
09/20/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-92341 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | UV |  |  |  | NA | Musty | Clear | 7.000000 | 14.200000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 10/16/2023 | 12:58 PM
04/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/17/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
08/23/2023 | Alternative |  | SWP-05-409 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 0-1 | 0-0 | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/23/2023 | 12:00 PM
11/30/2023 | Alternative | RoutineScheduled | 99-184-5002 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/13/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | replaced K-Rain system is in working condition | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
04/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/14/2023 |  | RoutineScheduled | 153-STS-20308 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [5 empty] | 02/14/2023 |  | 8.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/14/2023 | 03:49 PM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance | -STS-20143 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter"] | ["Effluent Screens" ,"Auxiliary Filter"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
05/18/2023 |  | Routine/Scheduled | 234-13-319 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/18/2023 | Jan 1 1900 1:13PM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/18/2023 | Alternative | Pump-Out Only |  | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  |  | N/A | [16 empty] | Pumped Out | Pumped processing tank empty and refilled with fresh water for restart. Maintenance to be scheduled at later date. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | Dec 30 1899 10:00AM
03/17/2023 | Alternative | RoutineScheduled | 14-183-153 | Russell | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 10 Dechlorine | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/17/2023 | 12:00 AM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | System appears to be functioning as designed. On the far side of the mounds there is a small hole/depression. No effluent presented when cycling the system. It appears to be mole/vole burrow possibly? Advised homeowner to monitor and notify us if anything changes/. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/30/2023 | Alternative | Routine/Scheduled | 136-06-0447 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Primary septic tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 01:30 PM
04/13/2023 |  | Follow-Up | 099-06-0149-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank was pumped out by others prior to peat repalcement. Degraded peat was removed by hand with shovels/pitch forks and new peat was installed. Peat was purchased from Wrights Ready Mix, degraded peat was disposed at Spotsylvania Refuse. Resealed septic tank outlet riser. Resealed pump tank wedge lid & riser joint. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
05/08/2023 |  | RoutineScheduled | 175-18-0347 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | On site to complete annual inspection and to investigate ongoing high level alarms. Control panel was showing a total of 25 high level alarms on 1-3-23; today the count was up to 40. Owner had been advised to check for running toilets. Today he was given assistance and 2 toilet flappers were confirmed to be not sealing correctly. Owner said he would hire local plumber to go through all the toilets and make necessary repairs. Flush rate still well below design. Bleach-flushed tubing and replaced pressure regulator (they are known to lose accuracy/ restrict flow as they age). Replaced wire nuts for power to field flush solenoid connection in the headworks as solenoid would only hum and valve would not open. Tested drip and flush rate, no improvement. Advised owner that a proper flush rate was imperative to maintaining proper drip rate and that further investigation was needed (such as checking for crimped drip tubing). Groundwater infiltration had been observed at the bottom riser joint outlet end of pump tank on several previous site visits. Today, all outlet risers were removed, flanges cleaned, and reattached with proper type and quantity of sealant. During the digging, a break in the conduit a few feet from the j-box was discovered. Three wires had small spots of bare copper just beginning to show and were repaired with heat shrink tubing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
04/04/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/31/2023 | Alternative | RoutineScheduled | 12-160-0149 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000 | Whitewater |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Septic | Black | [5 empty] | 05/31/2023 |  | 1260.000000 |  |  | 3280.000000 |  |  | Attached to this report | Inspected | - sample taken onsite - both tanks need to be pumped/cleaned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/13/2023 | 12:00 AM
01/31/2023 |  | RoutineScheduled | 175-06-0712 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ Advantex Recirculation Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic-8"sludge 3"scum/ Advantex-8"sludge 3"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Advantex media sheets cleaned / Controls, pumps, floats and alarms functioning properly/ Counts: Recirc pump run time-1889.1 Cycles-69478/ Discharge pump run time-286.1 Cycles-8142 On-3m 18s Off-8h 7m/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/07/2023 |  | Routine/Scheduled |  | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1500 | Microfast |  | Gravity | Pressure | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/07/2023 | 04:56 PM
01/20/2023 |  | RoutineScheduled | 163-STS-333943 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | Septic Tank Only | EZ-Treat | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The pillow beads were sprayed off. The laterals were flushed. The spray heads were spraying as designed. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/25/2023 | 05:40 PM
01/29/2023 |  | Routine/Scheduled | 145-STS-259667 | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [16 empty] | Needs water in the tank! | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/29/2023 | Jan 1 1900 11:00AM
12/14/2023 | Alternative | RoutineScheduled Component Maintenance | 182-06-0238 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation"] | NA | [7 empty] | 12/14/2023 |  | 25.000000 | [5 empty] | Will be sent separately | Inspected | Replaced pump and timer Recommend adding riser to inlet of tank | This AOSS should now return to normal function after having provided the above state routine maintenance | 01/15/2024 | 10:39 AM
02/24/2023 | Alternative | Reportable Incident | 159-01-056 | Middlesex | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 2000 | Clearstream | Clearstream | Pump | Pressure | Trenches |  | 1500.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Pumped 1000 gallons - Restaurant is reported to be open and owner requested pumpout of ONLY 1000 gallons to get them through the weekend. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 02/27/2023 | 09:00 AM
01/30/2023 |  | RoutineScheduled | 177-16-0305SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
04/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/10/2023 | Alternative | Routine/Scheduled | 157-10-0128 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Delta Environmental Products, UC Series |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Real estate inspection - routine service. Trash Tank - normal level - not pumped. Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - plastic - intact - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | 07:00 AM
08/28/2023 | Alternative | RoutineScheduled | 107-06-0650 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Auxiliary Filter"] | ["Effluent Screens","Auxiliary Filter"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
06/20/2023 | Alternative | RoutineScheduled | 139-04-0018 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Ecoflo | [6 empty] | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 12:00 AM
09/21/2023 | Alternative | RoutineScheduled | SD-05-336 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1250 | septic | Advantex | Gravity | Pressure | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation","Recirculation Pump","Effluent Screens"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/21/2023 | 03:00 PM
12/16/2023 | Alternative | RoutineScheduled | 047-18-088 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2500 | septic | Microfast | Gravity | Pressure | Drip | Not Applicable |  | [] | [] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 10:20 AM
11/02/2023 | Alternative | Reportable Incident | 136-07-0481 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm Call: Arrived on site found 2 bad floats. Called customer and they approved Jacob's estimate of replacing 2 floats. Replaced floats onsite. Tested upon completion all components working as they should. Cleaned up area and backfilled | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | 12:20 PM
04/10/2023 | Alternative | RoutineScheduled | 95-197-A6 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/10/2023 | 12:00 AM
10/17/2023 | Alternative | Routine/Scheduled | 07-192-095 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | Dec 30 1899 5:30PM
12/05/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20288 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/08/2023 | 08:29 AM
05/17/2023 | Alternative | Routine/Scheduled | 147-03-0089 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Puraflo |  | Pump | Gravity | Pad |  |  | ["Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/17/2023 | Dec 30 1899 10:00AM
04/25/2023 |  | RoutineScheduled | 179-STS-88774 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. treatment looks good. very small root was growing inside D-box, removed. Recommend adding Root X next year if roots growing in. RECIRC: HL 4,LL 22,OVERRIDE 61. DISCHARGE: HL 4, OVERRIDE 1 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
10/16/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Hott's Septic Service LLC | 1942001301 | Joshua | Hott | [9 empty] | [] | [] | NO | None | [6 empty] | 10/16/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | 12:00 AM
04/03/2023 |  | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 04/03/2023 |  | 60.000000 | [5 empty] | Will be sent separately | Inspected | fixed air supply 2 psi filter clog drip valve open | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/28/2023 | 02:17 PM
06/01/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-03-136 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment crystal clear. No wet spots in drip field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
01/18/2023 |  | Routine/Scheduled | 234-17-437 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | Jan 1 1900 1:30PM
01/19/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Josh | Hott | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/14/2023 | Alternative | RoutineScheduled | 150-07-0217 | King William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 3.000000 | 2900 gallons | septic tank | Delta Whitewater | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Level Sensor Operation","Distribution Pump Operation","Control Operation","BlowerCompressorAerator Operation"] | NA | Musty | Clear |  |  | 20.000000 | [12 empty] | Septic tank 3" fog, 11" sludge. Delta Whitewater 20% SS, no airflow to the unit found break in airline repaired, restored airflow to unit. Serviced aerator. Pump, alarm, floats, and controls operating properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/23/2023 | 05:25 PM
11/07/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Puraflo |  |  | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Septic Tank Baffles","Dispersal System Operation"] | ["Attached Growth Medium","Septic Tank Baffles","Dispersal System Operation"] | [18 empty] | leak appears to be fixed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/07/2023 | 12:00 AM
12/12/2023 | Alternative | RoutineScheduled |  | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Other"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-8"sludge 3"scum/ Microfast ATU-8"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-1955 ETM-207h 26m/ On-7m 9s Off-2h 28m/ Peak Off-1h 36m/ Peak cnts-14/ High cnts-26Watermeter-0,067,151.8/ Pump Tank riser and requires replacement ( To be done on 3/1/2024 -12" x 24" ) No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/07/2023 | Alternative | Routine/Scheduled | 228-19-0108 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream, cleaned the UV light bulb, and cleaned the filter in the septic tank. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Installed a new 1 - 12" x 24" riser, 1 - 6" x 24" riser, 1 - 24" lid and 18 stainless steel screws. The timer is set to 4.5 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/07/2023 | Dec 30 1899 12:00PM
01/05/2023 |  | RoutineScheduled | 177-STS-90024 | Spotsylvania | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | Septic | Cloudy | [5 empty] | 01/05/2023 | [7 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Effluent was coming out of pump tank lid, alarm never went off due to a lose wire (neutral for panel) reconnected wire and alarm and panel started to work. Water level back to normal after testing. Septic tank has 28" of sludge mostly broken down toilet paper, spoke to customer and he called a pumper to schedule pumpout. Water quality was bad due to system being on high level. HL 6, LL2, OVERRIDE 999999. R counts back to zero. | This AOSS should now return to normal function after having provided the above state routine maintenance | 01/12/2023 | 09:31 AM
04/10/2023 |  | RoutineScheduled | 179-14-0124-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Cleaned very dirty atu air filter, drip pump intake, and both (headworks) disc filters. Replaced burnt out alarm bulb in septic control panel. Replaced the 6" valve box and lid for the ARV closest to the street. The buried inlet lids for the septic tank and pump tank are not watertight. Need to add a riser and lid to grade on the septic tank. Wedge lid for pump tank needs properly sealed. Septic tank and pump tank both need pumped out due to sludge accumulation. A repair proposal will be sent to the owner. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
01/18/2023 | Alternative | Routine/Scheduled | 151-06-0130 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 3000 | Advanced Septic | [6 empty] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 0.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | 06:44 PM
04/03/2023 |  | RoutineScheduled | 065-STS-29129 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | 12:00 AM
06/22/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-18985 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Gravity | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | 11:24 AM
05/23/2023 |  |  | -STS-90201 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
04/18/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
03/13/2023 |  | Initial Visit | -STS-92929 | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Rappahannock | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | None |  | Gravity | Gravity | Trenches | Not Applicable |  | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | Located drainfield for possible addition to house. Found a large wet spot in the drainfield with effluent surfacing. System will need a repair. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/24/2023 | 07:34 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/19/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-03-702 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | The septic tank is leaking at the base of the riser. Additionally, the pump tank wedge lid door is also leaking. We recommend excavating by machine and resealing the risers, inlet and outlet pipes and wedge lid doors on both tanks. It will require drier soil conditions to complete any repairs. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
06/13/2023 |  | RoutineScheduled | 175-11-0283 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
01/16/2023 |  |  | 033-STS-87362 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
12/04/2023 | Alternative | RoutineScheduled | 93-184-5002 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Pump | Pressure | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","Septic Tank Baffles"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/04/2023 | 12:00 AM
05/09/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Zone 2 Solenoid is not opening and the pump is deadheading against the valve. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
09/06/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | SES field noted Puraflo Modules lids are warped & not properly fitted. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
12/11/2023 | Alternative | Reportable Incident | 128-04-172 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Arrived on site located pqnel. 120 volts to panel. Air blower not running. Found a crack in the plumbing that is allowing air to escape. Panel for blower has met life expectancy. Uf wire between panel and blower | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 12:47 PM
10/25/2023 | Alternative | RoutineScheduled | 03-197-A5 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.500000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
01/03/2023 |  | Routine/Scheduled | 234-16-286 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2022 | Jan 1 1900 8:40AM
06/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The breaker for the blower had tripped and it was reset at time of inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/14/2023 | Alternative | RoutineScheduled | 03-197-243 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | JET |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/14/2023 | 12:00 AM
12/14/2023 | Alternative | RoutineScheduled Component Maintenance | 177-13-0027-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine/ complaint inspection. Pump tank was on high level due to pump intake clogged up, cleaned intake and tested pump. 16.9 gallons per minute with clea intake. Found jbox for recirc tank full of water, vacuumed water out. Spoke to customer about Do's and don'ts and about checking toilets for leaks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
12/18/2023 | Alternative | RoutineScheduled | 087-STS-6442 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/20/2023 | Alternative |  | 11-113-169 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/20/2023 |  | 5.220000 |  |  | 2.100000 |  |  | Will be sent separately |  | BOD: 5.22 TSS: 2.10 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | 12:00 AM
06/14/2023 | Alternative | Routine/Scheduled | 228-11-0456 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | EZ Treat Sandfilter |  | Pump |  |  | UV |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | [15 empty] | Replaced UV bulb and 8 nozzles | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | Dec 30 1899 3:00PM
05/11/2023 |  |  |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/19/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20 |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. Septic tank - First section - 14" of accumulated solids. Second section - 8" of accumulated solids. 8" of solids in recirculation portion of treatment unit. 12" of solids in discharge portion of treatment unit. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/22/2023 | 07:03 PM
05/05/2023 | Alternative | Routine/Scheduled | 166-18-064 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1500 | Clearstream ATU |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 50.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/05/2023 | 05:19 PM
10/05/2023 | Alternative | Follow-Up | 09-160-0019 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [18 empty] | - replaced control panel | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/06/2023 | 12:00 AM
04/04/2023 |  | Reportable Incident |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | COSS - Repair - VDH Permit 136-23-0001 - GMP2018-02 Pumped existing septic tank empty - filled with flowable fill and abandoned. Installed 1000 gallon concrete mid-seam septic tank with cannister effluent screen and riser access. Installed 1000 gallon concrete mid-seam pump tank - new control panel, float sensors, and pump. Installed forcemain, distribution box and three 60' x 3' laterals at varying depth in accordance with permit and AOSE instructions. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/05/2023 | 09:00 AM
11/14/2023 | Alternative | RoutineScheduled | 150-17-0134 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Biomicrobics Microfast |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Level Sensor Operation","BlowerCompressorAerator Operation"] |  | Septic | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | 12:00 AM
07/26/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | 12:00 AM
06/20/2023 | Alternative | Pump-Out Only | 05-137-0189 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Supervised pumpout of processing tank by Commonwealth Waste solutions. Refilled processing tank for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | Dec 30 1899 12:30PM
05/26/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1875 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/04/2023 |  | Routine/Scheduled | 228-09-0208A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/04/2023 | Jan 1 1900 1:40PM
11/17/2023 | Alternative | Routine/Scheduled | 041-STS-261823 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/17/2023 | Dec 30 1899 1:16PM
10/09/2023 | Alternative | Routine/Scheduled | 09-174-0049 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/09/2023 | Dec 30 1899 9:43AM
10/26/2023 | Alternative | RoutineScheduled | 175-18-0523 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | YES | [7 empty] | 10/26/2023 | Sample Chamber | 7.000000 | [5 empty] | Attached to this report |  | Septic Tank-0"sludge 0"scum/ Recirculation Tank-0"sludge 0"scum/ Discharge Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Recirculation Pump intake cleaned/ Controls, floats, pumps and alarms are functioning properly/ Counts: Recirculation Pump-0125240 ETM-0510838 On-2.5m Off-14m/ Counts: Discharge pump-1124 ETM-120h 8m High-5/ 210 gal. dose On-6m Off-12h/ No breakout or spongy areas on the drainfield and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/01/2023 | Alternative | Routine/Scheduled | 093-STS-14490 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 2.5 minutes every 3 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | Dec 30 1899 3:45PM
07/31/2023 | Alternative |  | 001-STS-92314 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 12:00 AM
12/13/2023 | Alternative | RoutineScheduled | 159-15-0151 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Laneview Environmental, LLC | 1942001775 | James | Boone | 3.000000 | 1000 |  |  | Gravity | Pressure | Trenches | UV |  | ["None"] | ["None"] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/11/2023 | Alternative | RoutineScheduled | 115-05-0156 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | NA | Musty | [15 empty] | Inspected | Sludge level- 1" Scum & 8" Sludge in Septic tank. Cleaned Effluent screens. Pump tank had a trace of sludge. Alarm functional and pump is operational, Peat looks good and was replaced last year. It is full to top of peat layer and was turned in all 4 quadrants, Newly grown roots noted in all 4 quadrants, peat is full to the top. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 09:30 AM
01/30/2023 |  | RoutineScheduled |  | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
06/08/2023 | Alternative | RoutineScheduled | 13-142-0091 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/29/2023 | Alternative | Reportable Incident | 159-07-229 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Came out for alarm call on a Microfast system Found air pump/blower panel in alarm panel was silenced and blower turned off Turned air blower back on pulled amperage it has normal amps however making very loud grinding noise and panel will not go out of alarm Air blower is faulty and panel is aged Created estimates for air blower sent to customer via email | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2024 | 09:55 AM
02/10/2023 |  | RoutineScheduled | SWP-02-383 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 1-3 | 0-0 | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear |  |  | 5.000000 | [11 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/10/2023 | 01:00 PM
09/02/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  | 1000 | Pump | Pressure | Drip | Not Applicable |  | [] | [] | YES | Septic | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 12:00 AM
06/14/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was replaced and the system appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/05/2023 | Alternative | RoutineScheduled | 09-184-5003 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 15 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/05/2023 | 12:00 AM
04/28/2023 |  | Routine/Scheduled |  | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | 08:15 AM
06/26/2023 | Alternative | Routine/Scheduled | 196-12-125 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 1600 | Clearstream |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 10.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/26/2023 | 06:40 PM
06/02/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/12/2023 | 02:06 PM
02/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Gravity | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/05/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Puraflo |  |  | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","Control Operation","Septic Tank Baffles"] | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","Control Operation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 12:00 AM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance | 179-17-0324-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
03/27/2023 |  | RoutineScheduled | 08-184-5003 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","SludgeScum Accumulation","Dispersal System Operation","Control Operation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/27/2023 | 12:00 AM
07/07/2023 | Alternative |  | 124-STS-2379 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1750 | 1000 | 750 | Pump | Gravity | Mound | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/07/2023 | 12:00 AM
05/30/2023 | Alternative | RoutineScheduled | 137-STS-25748 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Pump | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 12:00 AM
01/16/2023 |  | Routine/Scheduled | 550-STS-6707 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 |  |  |  | 01/24/2023 |  | 11.000000 |  | 30.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 10:45AM
04/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
05/21/2023 | Alternative | RoutineScheduled | 047-19-108 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1500 | septic | Aquasafe | Gravity | Gravity | Discharge | UV |  | [] | [] | YES | None | Clear | [15 empty] | Informal | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/01/2023 | 12:45 PM
07/06/2023 | Alternative | RoutineScheduled | 023-STS-42917 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Western Virginia Water Authority | 1942001145 | Michael | Doss |  |  |  |  | Gravity | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | NA | None | Clear | [5 empty] | 07/06/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | Jan 1 1900 6:05AM
06/23/2023 | Alternative | Routine/Scheduled | 2007-143-0017 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level Secondary septic tank - effluent screen serviced. Pump Tank - float sensors,pump and controls operating. Biofilter - 5 modules - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/26/2023 | 12:45 PM
07/18/2023 | Alternative | RoutineScheduled | 14-142-0160 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/25/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/04/2023 | 12:00 AM
12/19/2023 | Alternative | Routine/Scheduled | 041-STS-261654 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 750 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | Dec 30 1899 12:30PM
12/18/2023 | Alternative | Routine/Scheduled | 09-120-0373AR | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Bionest |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/18/2023 | Dec 30 1899 2:07PM
07/17/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | bit of additional cleaning needed but good to go | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/26/2023 | Alternative | Routine/Scheduled | 09-160-0243 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:15 PM
09/13/2023 | Alternative |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  | Microfast Drip | [5 empty] | 450.000000 | ["None"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 12:00 AM
07/17/2023 | Alternative | RoutineScheduled | 16-100-0261 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 500 | AQUASAFE |  | Pump | Gravity | Pad | UV | 450.000000 | [] | [] | [18 empty] | REPLACED UV LIGHT UNIT-EVERYTHING WORKING AS IT SHOULD. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/04/2023 | 01:30 PM
03/15/2023 | Alternative | RoutineScheduled | 159-17-0219 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | [] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
10/26/2023 | Alternative |  | 154-06-0543 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/22/2023 | Alternative | RoutineScheduled | 171-09-0179 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | [16 empty] | Inspected | Sludge level-under 1" scum layer on top-6-12" sludge on bottom in Septic tank - Pump tank Trace sludge, Peat Moist no ponding , Lots of roots noted this year. Some roots noted in tank removed, turned peat in all 4 quadrants and broke up clumps. Tipping tray operational was cracked at one hinge and needs replacement. working unevenly, a new one has been ordered. Pump runs good. Cut the paradise tress from along side the house as remove any suckers.. Pump run time will return for pump numbers in july. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
06/12/2023 | Alternative | Reportable Incident | 157-06-0005 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 750.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | 06/12/2-23 - pumped septic tanks for storage for biofilter changeout. 06/15/2023 - removed biofilter media - replaced with new. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 02:15 PM
10/25/2023 | Alternative | RoutineScheduled | 009-STS-27090 | Amherst | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Effluent filter installed or maintained | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 10000 | BioMicrobics Fast 3.0 |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge level-about 1" scum and 22" in Septic tank and 24" Sludge in EQualization tank. Fast treatment Unit Tank 15-20" sludge and Good aeration in treatment tank, dosing tanks 4-6" sludge. Both Pumps tested functional and filters cleaned prior to my visit. runs on manual switch and via float switch. Alarms opperational. Park Service Rangers maintain drip/spin filter as needed and Cleaned Air filter on blower motor. Recorded pump meter reading. Eq pump 45,179 cycles vs 45,120 last year vs 44,826 cycles 2 years ago = 294 cycles 2 yrs prio and 60 cycles this past season. Park camnpground closed early. timer count 3196.72 hrs vs 3190.8hours last year= abut 6 Hours this season(4 times less then last year) -Discharge or drip dosing pump #1 Pump- 8905 vs 8689 Cycles previous =216 cycles this year and 118630 vs 116737 min = 1893 Min or 31.5hrs for season -- #2 Pump 8437 vs 8243 cycle Count = 194 cycles this year and 112981 vs 111,268 min = 1713 min or 28.5 hrs for the seaons. Pump #1 seems to have run a bit more this year then #2. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/26/2023 | 09:30 AM
10/06/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 2000 | Septic | pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/12/2023 |  | RoutineScheduled | 175-17-0369 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 02:21 PM
02/23/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
05/30/2023 |  |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 12:00 AM
04/11/2023 | Alternative | RoutineScheduled | 18-100-0105 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 500 | AQUASAFE |  | Pump | Pressure | Mound | UV | 450.000000 | [] | [] | [17 empty] | Pumped Out | EVERYTHING WORKING. PUMPED SEPTIC TANK. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 01:55 PM
05/02/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
03/28/2023 |  | RoutineScheduled | 175-19-0200 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Advised owner to get septic tank pumped out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
07/19/2023 | Alternative | Routine/Scheduled | 39055 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 |  |  | Gravity | Pressure | Trenches |  | 450.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/21/2023 | 10:18 PM
03/05/2023 |  | Routine/Scheduled | 041-STS-259909 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 2.000000 | 1500 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/05/2023 | Jan 1 1900 12:00PM
05/12/2023 | Alternative |  | 154-11-0121 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
11/06/2023 | Alternative | Pump-Out Only | 04-160-0088 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner |  |  | Advantex | [6 empty] | [] | [] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/07/2023 | 12:00 AM
04/06/2023 |  | RoutineScheduled | 154-06-0437 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES |  | Cloudy | [13 empty] | Will be sent separately | Inspected | Installed new Geoflow filter housing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
10/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
05/31/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
11/02/2023 | Alternative | Routine/Scheduled | 133-STS-93409 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 4.000000 | 4000 | Clearstream |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 0.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | 05:55 PM
06/15/2023 | Alternative | RoutineScheduled Component Maintenance | 175-08-0286 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/07/2023 | 06:25 AM
01/25/2023 |  | Routine/Scheduled | 228-18-0018 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/25/2023 | Jan 1 1900 10:20AM
02/27/2023 |  | Initial Visit | 182-08-0149 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Sand |  |  | Pressure | Drip |  |  | ["Other","Dispersal System Operation"] | ["Dispersal System Operation"] | [18 empty] | damaged lid to be replaced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/27/2023 | 12:00 AM
12/18/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty |  | 7.410000 |  |  |  |  | 12/18/2023 |  | 40.000000 |  |  | 34.000000 |  |  |  |  | BOD and TSS are over the regulatory limit. When I arrived, the aerator shaft was clogged and I cleaned it out. I believe that contributed to the high results. Will return and resample. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/12/2024 | 04:00 PM
05/12/2023 |  | Initial Visit |  | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit Primary septic tank - normal level - effluent screen serviced. BioFilter - fracture at A6/A7 - Peatmoss spent requires biofilter changeout. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/25/2023 | 01:00 PM
05/30/2023 |  | RoutineScheduled | 2126-09-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | PuraFlo |  | Pump | Gravity | Discharge | UV | 250.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation","Effluent Screens"] | ["Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation","Effluent Screens"] | YES | Musty | Clear | 7.800000 | [15 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/31/2023 | 12:00 AM
02/03/2023 |  | RoutineScheduled |  | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock-Rapidan | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Drip | Not Applicable | 750.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
03/10/2023 |  | Routine/Scheduled | 2009-143-0154 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash Tank - normal level - recommend pumpout. Aeration Tank - normal level - mixing present - compressor serviced. PUmp Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | 09:30 AM
10/02/2023 | Alternative | Reportable Incident | 136-08-0230 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Repair: -added 8 inch section to eco flow riser -inspected quality and made sure everything was functioning | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/12/2023 | 01:06 PM
03/24/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank to Puraflo Modules | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","Distribution Pump Operation","Level Sensor Operation"] | ["Attached Growth Medium","Distribution Pump Operation","Level Sensor Operation"] | YES | [17 empty] | Septic Tank-8"sludge 3"scum/ Pump Tank-2"sludge / No pump out needed at this time/ Turned Puraflo Peat in all 8 Modules and peat is in good condition/ Replaced broken check valve for pump #1 and faulty timer enable float/ Controls, pumps, floats and alarms now functioning properly/ Counts: Pump1-5880 ETM-10127/ Pump2-5989 ETM-9679 On 1m 8s Off-2h/ No breakout or spongy areas on the pad site. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/29/2023 |  | Follow-Up | 179-06-0474-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 | 1900 | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Control Operation" ,"Attached Growth Medium"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Control Operation" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected | Repaired 4 cracks in fiberglass Orenco tank. Replaced broken pump tank with permit. Installed new wire and conduit for both tanks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
12/28/2023 | Alternative | RoutineScheduled | 165-STS-335365 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles"] | ["Auxiliary Filter","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 12:00 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/23/2023 |  | RoutineScheduled | 09-113-091 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","SludgeScum Accumulation","Dispersal System Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/23/2023 | 12:00 AM
04/27/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 04/27/2023 |  | 34.000000 | [5 empty] | Will be sent separately | Inspected | new air vent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/22/2023 | 11:15 AM
05/15/2023 |  | Routine/Scheduled | 196-15-0033 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 06:45 AM
07/19/2023 | Alternative | RoutineScheduled | 015-STS-337728 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | 12:00 AM
06/20/2023 | Alternative |  | SD-12-305 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation","Effluent Screens","Attached Growth Medium"] | ["SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | 12:00 AM
05/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
04/25/2023 |  | Routine/Scheduled | 550-STS-6639 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | Jan 1 1900 9:30AM
02/15/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/03/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
04/18/2023 |  | RoutineScheduled | 101-17-0374 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/23/2023 | 12:00 AM
01/30/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim |  |  |  |  | Pump | Pressure | Drip | UV |  | ["SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [17 empty] | Septic/atu needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/31/2023 | Dec 30 1899 3:05PM
02/06/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | drip field needs to be cleared and small trees cut back | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | 12:00 AM
04/03/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | alarm buzzer replaced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
01/27/2023 |  | Routine/Scheduled | {FIPSCode}-STS-1174 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Cloudy | 7.000000 | 4.000000 | [13 empty] | UV is not working | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/27/2023 | Jan 1 1900 11:35AM
07/21/2023 | Alternative | Routine/Scheduled | S800-17-0036 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The Clearstream tank should be pumped out. The timer is set to 5 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/21/2023 | Dec 30 1899 2:15PM
05/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/07/2023 |  | Follow-Up | 234-18-173 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Control Operation","Disinfection"] | ["Control Operation","Disinfection"] | N/A | [17 empty] | Replaced UV control panel | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/07/2023 | Jan 1 1900 8:00AM
12/04/2023 | Alternative | RoutineScheduled Component Maintenance | 179-14-0367-SP | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  | ["Effluent Screens" ,"SludgeScum Accumulation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | EZ Treat spray heads need replacement. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/06/2023 | 09:34 AM
04/15/2023 | Alternative | RoutineScheduled | SD-96-13 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1000 | septic | Multi-flo | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | YES | Musty | Clear | [15 empty] | No Discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/20/2023 | 04:00 PM
05/23/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 1000.000000 | [] | [] |  |  |  | 7.760000 | 6.500000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/15/2023 | 05:20 AM
11/13/2023 | Alternative | Initial Visit Component Maintenance | 033-STS-92187 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Aqua Klear | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
06/13/2023 |  |  |  | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
08/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/10/2023 | 12:21 PM
01/06/2023 |  | Routine/Scheduled | 234-16-332 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/06/2023 | Jan 1 1900 10:55AM
01/05/2023 |  | Follow-Up | 177-STS-90024 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [7 empty] | 01/05/2023 |  | 325.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
06/07/2023 | Alternative | RoutineScheduled | 11-172-0007 | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 |  | EZ Treat |  | Pump | Pressure | Drip |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 12:00 AM
12/01/2023 | Alternative | RoutineScheduled | (AOSE) C-122-11-0001 | Craig | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | King's Alternative Septic | 1942001112 | William | King, II | 1.000000 | 1500 | BioMicrobics Microfast 0.5 |  | Gravity | Gravity | Trenches | Not Applicable | 250.000000 | ["None"] | ["None"] | NA | [17 empty] | System is working correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/03/2023 | 12:00 AM
04/18/2023 |  | RoutineScheduled | 099-06-0252-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Ecoflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Roots growing inside pad, added 2 cans of Root Destroyer. Filter handle is corroded might need replacement next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
10/16/2023 | Alternative |  | 101-11-0200 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Ivan & Annette L. | Couch-Jareb | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/12/2023 |  | RoutineScheduled | 06-195-272-Dis | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/12/2023 | 12:00 AM
05/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Mound | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping this year. Recommend evaluating the manifold and repairing/replacing foam filters if necessary. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/22/2023 | Alternative | Reportable Incident | SD-15-180 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Replaced failed UV ballast. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/15/2023 | Alternative | RoutineScheduled | 159-02-405 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
05/19/2023 |  |  | 2014-143-0131 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Ecopod | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Inspected | Septic tank needs to be pumped | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/02/2023 | 12:00 AM
04/16/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/16/2023 | Dec 30 1899 11:00AM
02/06/2023 | Alternative | RoutineScheduled | SD-10-49 | Culpeper | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | As noted previously, the drip dispersal system area should be mowed and maintained in a mowed condition. Roots are preventing the drip dispersal system from building pressure & operating properly. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/01/2023 | 12:05 PM
05/25/2023 | Alternative | RoutineScheduled | 10-173-049 | Prince Edward | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Septic | Norweco | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Effluent Screens","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Effluent Screens","Level Sensor Operation","Control Operation","SludgeScum Accumulation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/25/2023 | Dec 30 1899 10:00AM
11/30/2023 | Alternative | RoutineScheduled | 03-184-5001 | Scott | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination | [22 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
04/13/2023 |  | Reportable Incident |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [6 empty] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | [17 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/25/2023 | 10:52 AM
09/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
02/01/2023 |  | RoutineScheduled | 033-STS-88810 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["Effluent Screens" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
11/16/2023 | Alternative |  | 08-184-5006 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/16/2023 |  | 4.670000 |  |  | 16.800000 |  |  | Will be sent separately |  | BOD: 4.67 TSS: 16.8 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | 12:00 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 | 1500 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Sale inspection on a Purflo septic system. The state requires that all alternative septic systems must be inspected every year and filed with the county and the state. The exterior septic control panel is an Orenco timed dose. There are 2 4" pvc clean outs. The sewer line was camera snaked and was clear. The septic tank has a plastic riser on the outlet side for access. There is a filter that was cleaned. The manufacture recommends that the filter be cleaned every 6 months so as not to clog up and cause a back up. The septic tank effluent level was at working level when lid was opened. After tank was pumped out a visual inspection was done and there were no cracks or leaks seen at that time. The conveyance line was camera snaked and also was clear. The pump tank, riser, lid, electric box, floats, force main and pump were inspected. The 6 Purflo pods were all opened and inspected for condition of peat fiber and drainage. There is a black sample box near the pods. The 7-port plastic d-box was dug up it was 10" under the surface. There were speed levelers on all 4 header lines. All 4 header lines were camera snaked and were clear. The drain field was probed and dry. At time of inspection all components were in working condition. This inspection does not guarantee the life of any component. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | Dec 30 1899 11:50AM
04/07/2023 |  | Routine/Scheduled | 234-14-30 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/07/2023 | Jan 1 1900 7:00AM
08/16/2023 | Alternative | RoutineScheduled | 19-142-0047 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/27/2023 |  | RoutineScheduled | 099-18-0157 C-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. 15 psi. RECIRC: HL 3, LL 21, OVERRIDE 339. DISCHARGE: HL 4, LL 11. OVERRIDE 0. "R" counts back to zero. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
11/15/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Pressure | Drip | Not Applicable |  | [] | [] | [18 empty] | System minimally used. Not enough effluent in tanks to check drip field function (return) | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/15/2023 | 12:00 AM
11/13/2023 | Alternative | RoutineScheduled | 05-118-0016 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Advantex AX20 |  | Pump |  |  |  |  | [] | ["Attached Growth Medium","Recirculation Pump","Level Sensor Operation","Auxiliary Filter","Distribution Pump Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 12:00 AM
01/16/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/09/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 2000 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Unit #2 Brand new Advantex AX20RT installed infront of large septic surge tank for newly added RV sites to SWEETWATER RV PARK which pumps to the conventional drainfield. Installer completed install today, its graded and seeded well. We came for start up today. Sludge level in tanks None, treatment unit filled with water and we turned on the new Control box., Ran Recirc pump and tested floats. All good, Alarm sounds. Set setting as per Orenco to handle rated flow. Recirc pump setting 5min 18 sec off time and 1 min on time, 1min30sec overide off, 1 min on override, Min override time 60 min, High alarm delay 35 min- Set time and date, System is now fully operational | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 09:30 AM
08/31/2023 | Alternative | Initial Visit | 550-STS-6603 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 57.000000 |  | 6000.000000 | [5 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream (a lot of paint residue on filter). Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the UV light bulb. Could not check the drainfield or mound due to it raining at the time of service. The timer is set to 2 minutes every 2.5 hours. Took initial BOD and Fecal samples. NOTE - BOD and Fecal samples were high - possibly due to the paint residue - system should function properly after service. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/31/2023 | Dec 30 1899 9:30AM
05/04/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
12/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["Recirculation Pump" ,"Disinfection" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Disinfection" ,"Attached Growth Medium"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Effluent sample results will be sent separately.. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
03/06/2023 |  | RoutineScheduled | 181-07-0175 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NO | [17 empty] | The system did not need to be pumped. The blower and spin filters were both cleaned. The controls were operating as designed. There were no visible leaks in the leech field. The drip field was operating as designed. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | 09:45 AM
11/27/2023 | Alternative | RoutineScheduled Component Maintenance | 177-17-0129-SR | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EZ Treat Sandfilter | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The recirculation pump is working, but the spray dispersal is weak. This pump may need to be replaced in the near future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
08/11/2023 | Alternative | RoutineScheduled | 11-100-0200 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | PURAFLO | DELTA AERATOR |  | Gravity | Pad |  | 300.000000 | [] | [] | YES | [17 empty] | SLUDGE JUDGE REVEALED 4-5" FROM BOTTOM OF SEPTIC TANK INSTALLED NEW SEWAGE ALARM BULB, SEWAGE PUMP FLOAT AND 3 AMP FUSE FOR BLOWER AND CONNECTED BUZZER TO ALARM EVERYTHING WORKING AS IT SHOULD | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/04/2023 | 12:30 PM
04/10/2023 | Alternative | RoutineScheduled | 03-183-001 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/10/2023 | 12:00 AM
05/22/2023 | Alternative |  | 19-173-027 | Prince Edward | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1500 | Septic | Norweco | Gravity | Gravity | Trenches | Not Applicable | 600.000000 | ["BlowerCompressorAerator Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Effluent Screens","SludgeScum Accumulation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/22/2023 | Dec 30 1899 12:00PM
03/14/2023 |  | Reportable Incident | SP-04-498 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | ["Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | SAP & System Upgrade. Installed new plumbing kit, float sensors and controls for Biofilter dosing tank., Installed new plumbing kit, float sensors, and GeoFlow Automatic Control panel for Discharge tank. Marked tanks, absorption field for deck construction. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/16/2023 | 07:30 AM
06/16/2023 | Alternative | RoutineScheduled Component Maintenance | 099-11-0040-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Semi-Annual Inspection We recommend removing the tree growing near the drainfield header line to prevent root intrusions. We also recommend replacing the pod vent cap. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
03/31/2023 |  | Routine/Scheduled | 550-STS-6550 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/31/2023 | Jan 1 1900 2:01PM
10/12/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Installed an aerator rebuild kit. The timer is set to 6 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/12/2023 | Dec 30 1899 1:30PM
02/17/2023 |  | Routine/Scheduled |  | Richmond City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Richmond | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. PUmp Tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | Jan 1 1900 9:45AM
04/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Needs a new A300 filter. Filter is broken | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
09/04/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 |  | NONE |  | Pump | Gravity | Trenches |  |  | ["None"] | [] | NA | [17 empty] | Meters - A - 950, B -680, C - 910. Tested both discharge pumps in "HAND", both pumping. Still no gallons pumped to drain field. Water will be added to the Model Home AOSS during September to force water to the pump tank to verify flow. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | 07:03 PM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Middle Module is fully saturated and has standing water to the lip of the module | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/04/2023 | 06:02 AM
05/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/20/2023 |  | Routine/Scheduled | 02-120-0593AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 2500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level Secondary septic tank - normal level Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/21/2023 | Jan 1 1900 7:00AM
10/02/2023 | Alternative |  | 162-03-0117 | Nelson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Jim | Gates | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/05/2023 |  | Routine/Scheduled | 041-STS-259369 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | [16 empty] | See VENIS report. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/05/2023 | Jan 1 1900 9:30AM
04/11/2023 |  | Reportable Incident | SP-04-508 | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for waste water coming out of sample box due to roots growing in. Removed roots from sample box to get water flowing to d-box again. Dug up d-box and it was full of roots as well. Removed what I could two lines are still completely blocked. Peat is degraded and has ponding water. Check valve is broke on force main. Homeowner to call back to repair force main and inspect system to see if any other repairs need to be done. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/01/2023 | 06:44 AM
01/30/2023 |  | RoutineScheduled |  | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
01/12/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Air filter replaced as preventative maintenance. The four 1-inch vents that were installed earlier in the valve boxes appear to be effective in reducing condensation. One valve box was completely dry, and the other 3 were just damp | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
06/01/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-120 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite to inspect system. Could not give contract due to peat moss needing to be changed. Pod 5 was not getting any water due to rock in manifold that I removed. Proposal to be sent for a peat change. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Only one zone appears to be functioning. Could not get the system to switch zones for the remote zone valves. Filter flush solenoids do not appear to be functioning as well. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
03/09/2023 |  | RoutineScheduled | 03-197-243 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/09/2023 | 12:00 AM
04/10/2023 | Alternative | Initial Visit | 073-STS-94665 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 5.000000 |  | 5.000000 | [5 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the UV light bulb. The timer is set to 4 minutes every 2 hours. Took BOD and Fecal samples. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/10/2023 | 10:15 AM
05/11/2023 | Alternative | RoutineScheduled | 128.01.086 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | ["None"] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | 12:00 AM
06/01/2023 | Alternative | RoutineScheduled | 109-STS-31246 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 12:00 AM
05/02/2023 |  | RoutineScheduled | 179-18-0177-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Delta Environmental Products, DF Series | Delta Environmental Products, DF Series | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Looking away from building - Aerator on left kept blowing fuses and would not run. Was not running upon arrival Aerator on right was running but it does not seem like the air was making it into the treatment unit. It was left off to not burn the motor with back pressure. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
11/08/2023 | Alternative | RoutineScheduled | 109-13-0174 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Aqua Klear |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | Musty | [15 empty] | Inspected | Assisted with replacing the Aquaklear treatment tank, which was fiberglass and had colappsed. Foutz septic did the install and i assisted and reconnected the treatment system and replace new blower, new airline hose and tubing, afterwards confimred new system is operational, Found spin (vortex) filter solenoid control valve was sturck open and not responding creating a loop with the pump running. shut the valve manually and will replace the solenoid and get it working in near future but otherwise is working as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
03/15/2023 | Alternative | Routine/Scheduled | 136-07-0050 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Primary septic tank - normal level - Aeration Tank - normal level - mixing present - compressor serviced. Pump tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/16/2023 | 08:45 AM
07/11/2023 | Alternative | Routine/Scheduled | 08-142-0095 | Hanover | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [17 empty] | Pump alarm reported. Found pump not working, replaced pump. Aerator stopped working while we were there and could not get breaker to stay on in panel. Panel will needs to be replaced. Riser on pump tank is cracked and needs to be replaced. Aerator is hard wired through panel. Cleaned air filter. System is operating but there is no alarm for aerator. Ct 27893, etm 24902, HL 106, LL 42 , override 1459 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/11/2023 | Dec 30 1899 8:31AM
09/11/2023 | Alternative | RoutineScheduled | 150-16-0005 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [18 empty] | Blower is bad | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/12/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | 12:00 AM
04/28/2023 | Alternative | RoutineScheduled | 175-12-0355 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-4"sludge 2"scum/ Microfast-2"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-24536 ETM-3124/ Override-53/ Hand-143/ High-53 On-7m 9s Off-1h 53m/ UV-Light sleeve cleaned and working properly/ No breakout or spongy areas on the drip field and dosing correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/02/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
01/18/2023 |  | Initial Visit | S 800-19-0059 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the alarm - silenced it - water coming out of the tops. Meet with the pumping company - pumped the trash out of the Clearstream and pumped the septic out. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Cut the UV off, disconnected the UV alarm, and disconnected the pressure switch due to the pumping of tanks. The timer is set to 6 minutes every 2 hours. Did not take samples. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/18/2023 | Jan 1 1900 10:45AM
05/04/2023 | Alternative | RoutineScheduled | 153-STS-20272 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
01/30/2023 | Alternative | Routine/Scheduled | 151-06-0068 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Multiflo FTB |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES |  |  |  |  | 20.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | 05:51 PM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/11/2023 | Alternative | RoutineScheduled | 115-11-0173 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | AX20RT ORIGINAL STYLE |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Septic Tank minimal scum and 3" sludge-pumped Feb 2022. Recirc zone trace sludge, discharge trace sludge. Minimal dead roots removed in treatment unit where prior growth was. All floats tested good, Biofilter was clean and septic filter was cleaned. Pump count 2281.4 hours and 84803 cycles on recirc zone, Gravity discharge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 05:30 PM
06/23/2023 | Alternative | RoutineScheduled Component Maintenance | SWP 02-451 | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Effluent is surfacing in multiple locations where the drip dispersal system was damaged during tree removal. The damage is significant, and we recommend contacting an Alternative Onside Soil Evaluator for repair options. A referral has been made to M&M Soil Consultants who originally designed the system. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/03/2023 | 05:43 AM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/01/2023 | Alternative | RoutineScheduled Component Maintenance | 177-08-0145-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 4.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Disinfection" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Disinfection" ,"Effluent Screens" ,"Attached Growth Medium"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
08/30/2023 | Alternative | Routine/Scheduled |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. Dbox - intact - strongly recommended that new growth trees be removed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | 10:00 AM
03/24/2023 |  | RoutineScheduled | 11-183-190 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/24/2023 | 12:00 AM
11/20/2023 | Alternative | RoutineScheduled Component Maintenance | 154-04-1021 | Albemarle | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 11/20/2023 |  | 97.000000 | [5 empty] | Will be sent separately | Inspected | Replaced blower and control panel Added media cleaner | This AOSS should now return to normal function after having provided the above state routine maintenance | 12/06/2023 | 03:05 PM
04/19/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
01/05/2023 |  | RoutineScheduled | 179-14-0368-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Distribution Pump Operation" ,"Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | Installed new screen on recirculation pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
01/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/30/2023 |  | RoutineScheduled | 107-05-0332 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 0.000000 | [] | [] | [18 empty] | No access. No power | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 02:30 PM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
11/10/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | UV |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | Dec 30 1899 1:10PM
03/31/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
08/16/2023 | Alternative | RoutineScheduled | 04-172-0315A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | C & E Mechanical Corporation | 1942001339 | Louis | Timberlake | 1.000000 | 1250 | PremierTech |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Dispersal System Operation","SludgeScum Accumulation","Other"] | ["SludgeScum Accumulation","Effluent Screens","Dispersal System Operation","Other"] | YES | [6 empty] | Peatmoss raked/flipped | [9 empty] | Inspected | Recommend pumping in 3-4 years | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | Dec 30 1899 1:00PM
05/04/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Distribution Pump Operation" ,"SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"SludgeScum Accumulation" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | 5/1/23 On site to replace diffusers, pumper failed to show up (truck broke down). Blower was not running - replaced failed start capacitor. Blower running again, but at a higher amp draw. Discovered broken vent pipe on filterbed and fiberglass damage to access manway. 5/3/23 Tank pumped out by Powell's Plumbing. Observed all kinds of household trash in the tank (food stickers, tampons, surface wipes, etc.). New diffusers installed, flush valve installed for future maintenance, and a spring-check valve installed at the manifold inlet to prevent backflow into the blower during a high level event. Pump stand was found to be cracked, replacement ordered. Air pre-filter cleaned. 5/4/23 New pump stand installed, discharge piping modified (with bracing) to facilitate maintenance, and sample port added for effluent testing. Camlock gasket replaced. Vent pipe repaired on filterbed. Access manway repaired with fiberglass patch. Added enough fresh water back to the tank to verify excellent aeration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 06:43 AM
10/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 | 2500 | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"SludgeScum Accumulation"] | NA | [7 empty] | 10/02/2023 |  | 5.000000 | [5 empty] | Will be sent separately | Inspected | Lab normal Pumped primary tank Alarm was turned back to automatic | This AOSS should now return to normal function after having provided the above state routine maintenance | 11/22/2023 | 09:18 AM
12/08/2023 | Alternative | Follow-Up | 99-197-A6 | Wise | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity |  | Chlorination | [9 empty] | 1.000000 | [11 empty] | Tablets are now in chambers and new lids | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | 12:00 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Aerator was not functioning | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
06/27/2023 | Alternative | Reportable Incident | SADN-9E4NTA | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Puraflo | [6 empty] | ["Control Operation","Effluent Screens"] | ["Control Operation","Effluent Screens"] | N/A | [16 empty] | Pumped Out | Replaced effluent filter | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/27/2023 | Dec 30 1899 8:30AM
04/10/2023 |  | Routine/Scheduled | 16-172-0265A | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | EcoPod |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/10/2023 | Jan 1 1900 11:41AM
01/05/2023 |  | Reportable Incident | -STS-92515 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Septic | [14 empty] | Will be sent separately | Inspected | Atu alarm. Original air pump from 2007 finally failed. Replaced air pump, alarm cleared. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 09:31 AM
12/26/2023 | Alternative | RoutineScheduled | 91-184-5002 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/26/2023 | 12:00 AM
09/30/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | Modified Extended Aeration |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | YES | [17 empty] | Total flow to drain fields September 2023 -330,150gallons. Average 13,206 gallons per day. All aspects of the system are operational. Wasting of settled mixed liquor from the clarifier to the digester and decanting of supernatant from digester are occurring regularly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/03/2023 | 07:03 PM
05/19/2023 |  | Routine/Scheduled | 228-10-0041 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | Jan 1 1900 10:30AM
05/02/2023 | Alternative | RoutineScheduled | SD-05-106 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 |  |  | Pump | Gravity | Trenches |  |  | ["Effluent Screens","SludgeScum Accumulation"] | ["Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/03/2023 | 08:15 AM
10/23/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.050000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/07/2023 | 02:30 PM
06/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend removing tree closest to lower line | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/08/2023 |  | Initial Visit | 810-STS-3854 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 4.000000 |  | 9.000000 | [5 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter (it was in backwards). Installed a filter in the septic tank. Could only locate one vacuum breaker. The timer was set to 4.5 minutes every 1 hour changed it to 9 minutes every 1 hour. Took initial BOD and Fecal samples. Need to go back and perform another draw down test. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/08/2023 | Jan 1 1900 11:00AM
01/17/2023 |  |  | 033-06-0236-SR | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
03/01/2023 | Alternative | RoutineScheduled | 013-STS-1034 | Arlington | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Arlington | FIVE STAR SEPTIC INC | 1942001248.000000 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/01/2023 | Dec 30 1899 2:40PM
06/12/2023 | Alternative | Initial Visit | PPIE-AJFN8F | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Visit - System flooded. Primary septic tank - requires pumpout. Aeration tank - high level - recommend pumpout - mixing present - compressor serviced. Pump Tank - high level - serviced pump, float sensors and controls operating. Drip Field - headworks serviced - no return to pump tank - found return air release / vacuum breaker full of silt / sand - requires underground consult. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/13/2023 | Dec 30 1899 9:00AM
03/27/2023 |  | Routine/Scheduled | 228-05-0419 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/27/2023 | Jan 1 1900 12:40PM
09/11/2023 | Alternative | Routine/Scheduled | 2019-143-0055 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1000 | Purasys |  | Pump | Gravity | Pad | Not Applicable | 150.000000 | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation"] | N/A | [17 empty] | System was in "Away Mode" at time of visit. The drainfield was checked and appeared to be working correctly. Counters: Aerator 3374:57, Sludge 126:18, Discharge 36:37 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/11/2023 | 02:03 PM
07/28/2023 | Alternative | RoutineScheduled | 015-STS-333421 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | AdvantexAX20RT | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Auxiliary Filter"] | ["Effluent Screens","Auxiliary Filter"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The textile sheets were sprayed off. The recirculating and discharge pumps were pulled and sprayed off. The spin filter was pulled and cleaned. The controls were operating as designed. There was return effluent returning to the pump chamber so the drip field was operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/17/2024 | 03:30 PM
11/20/2023 | Alternative | RoutineScheduled Component Maintenance | 175-02-0081 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 09:34 AM
12/12/2023 | Alternative |  | 15-192-042 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/12/2023 |  | 9.290000 |  |  | 4.200000 |  |  | Will be sent separately |  | BOD: 9.29 TSS: 4.20 SV | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 12:00 AM
12/19/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1875 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 12/19/2023 | Sample Chamber | 10.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/12/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Community Pump Maintenance: -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pumps are functioning properly. Checked and confirmed discharge floats are functioning properly. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Distribution Box: Water level normal. Structural integrity of distribution boxes appear to be intact -Drain Field: Found no signs of surfacing on dispersal fields | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | Dec 30 1899 2:23PM
01/27/2023 |  | Routine/Scheduled | S 800-19-0041 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/27/2023 | Jan 1 1900 1:50PM
11/06/2023 | Alternative | RoutineScheduled |  | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Discharge | Chlorination | 600.000000 | [] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | 12:00 AM
11/29/2023 | Alternative |  | 05-197-A4 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/29/2023 |  | 14.000000 |  |  | 7.000000 |  |  | Will be sent separately |  | BOD: 14.0 TSS: 7.00 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/29/2023 | 12:00 AM
05/17/2023 |  | RoutineScheduled | 175-18-0067 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection"] | ["BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | 7.500000 | 22.400000 |  | 0.000000 | [9 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 06/15/2023 | 12:05 PM
04/20/2023 | Alternative | RoutineScheduled | 015-STS-334622 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Gravity | Discharge | UV |  | ["Disinfection","Auxiliary Filter"] | ["Disinfection","Auxiliary Filter"] | NA | Musty | Clear | [15 empty] | no discharge during visit | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/06/2023 | 12:00 AM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance | 099-STS-88900 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Control Operation" ,"Disinfection" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Replaced UV bulb. J-box for discharge tank was full of water, vacuumed it out. Enabler float for discharge stock close, replaced. Peak float acting up, replaced. DISCHARGE: HL-19, ETM-0M PEAK CNTS-31, ETM-1568H48M. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:55 PM
03/31/2023 |  | Follow-Up | SD-12-174 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001682 | Frank | Hogan | 2.000000 | 8000 | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Dispersal System Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"Auxiliary Filter" ,"Attached Growth Medium"] | NA | Musty | Cloudy | 7.100000 | 4.870000 | [11 empty] | Will be sent separately | Inspected | 3-25-23 Advantage pumped 4,000 from Discharge chamber 3-27-23 Cleaned and replaced spinners on both AX units limned wet areas 3-29-23 Cleaned media on surface and in between sheets 3-29-23 Removed 4,000 from discharge tank 3-30-23 Low Amp Alarm recirc tank pump 6 Checked pump, is not operational but pump 5 is a backup pump still working but delivering less than full flow of 2 pumps | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/15/2023 | 07:20 PM
03/14/2023 | Alternative |  | 101-14-0214 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Bill & Sally | McClure | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/20/2023 |  | RoutineScheduled | -STS-20150 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | ATU | Polishing Sand Filter | Pump | Pressure | Discharge | Chlorination | 250.000000 | ["Control Operation","Disinfection","Distribution Pump Operation","Dispersal System Operation","Level Sensor Operation"] | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | NO | Musty | Clear | 6.400000 |  |  | 2.100000 |  | 02/21/2023 | Pump Chamber | 3.000000 |  |  | 1.000000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/06/2023 | 12:00 AM
01/12/2023 |  | RoutineScheduled | 153-STS-20272 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NO | Musty | Clear | [5 empty] | 01/12/2023 |  | 32.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
10/17/2023 | Alternative | RoutineScheduled Component Maintenance | 175-14-0071 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
09/14/2023 | Alternative | RoutineScheduled Component Maintenance | 2120-08-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | UV |  | ["Disinfection"] | ["Disinfection"] | NA |  |  | 6.800000 | 13.100000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 10/16/2023 | 12:58 PM
09/28/2023 | Alternative | RoutineScheduled | 095-STS-5064 | James City | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Peninsula | Hutchens Septic Services LLC | 1942001509 | Robert | Hutchens, Jr. | 1.000000 | 1500 | Advantex Ax-20 |  | Pump | Pressure | Pad | UV |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear | [15 empty] | Effluent is surfacing in the drain field area. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/28/2023 | 12:00 AM
01/31/2023 |  | Routine/Scheduled | 550-STS-6682 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 01/31/2023 |  | 3.000000 |  | 12.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | Jan 1 1900 8:15AM
09/15/2023 | Alternative | Reportable Incident Component Maintenance | XWP-98-643 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Complaint inspection. Customer broke riser and lid on septic tank, replaced both and sealed with ADH200 inside and tar on outside. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
05/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-10"sludge 4"scum/ Microfast-6"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ / Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-1383 ETM-128h 28m/ Pump2-1354 ETM-126h 23m On-5m 58s Off-6h/ No breakout or spongy areas on the LPD Trenches. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/09/2023 | Alternative | Routine/Scheduled | 157-03-157 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced both systems. Checked the pump, panel, and floats (ok - on both systems). Cleaned the filter in the aerator on both, cleaned one diffuser, and replaced the other diffuser. Cleaned the filter in the septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/09/2023 | 01:30 PM
09/07/2023 | Alternative | Reportable Incident | 13-137-0032 | Goochland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | All In Septic Services | 1942001442 | Dennis | Mitchell | 3.000000 | 3500 | Norweco 900 |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [14 empty] | Pumped Out | Both Aerators Replaced On, Off, Alarm Floats Replaced Septic Tank and Treatment Tank Pumped | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/07/2023 | Dec 30 1899 12:00PM
03/09/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
03/30/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 1.000000 |  | Fuji Cen 7 |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | 3.5' overall liquid, 2" scum, 15" of sludge in settling chamber. 2nd chamber 12" loose sludge. Pump tank very little sludge. Would pump out within the year. Everything working and field is dry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 09:45 AM
12/27/2023 | Alternative | RoutineScheduled | 155-STS-12090 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | 2.000000 | 2000 | ECOFLO |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] |  | Septic | Cloudy | [5 empty] | 12/27/2023 | Pump Chamber | [6 empty] | Will be sent separately | Inspected | - recommend septic tank be located for future maintenance purposes, believe septic tank is under property additions - unable to confirm pump alarm functionality at this visit | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 12:00 AM
11/13/2023 | Alternative | Routine/Scheduled | 2008-143-0014 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Flushed and cleaned effluent screen. Not due for pump out. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. Discharge pump plumbing has exceeded life expectancy. Discharge riser is damaged. -Peat Moss: Raked and tilled peat moss. Peat moss is in good condition. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Drain Field: Found no signs of surfacing on dispersal mound | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | 10:24 AM
09/29/2023 | Alternative | Initial Visit | 19-177-1019 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [17 empty] | Inspected | - replaced blower onsite | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/28/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The level of the peat is low but there are no signs of ponding failure as described by the manufacturer. Recommend leveling modules that are slightly out of level. Informed homeowner that the peat is nearly the end of its functional life and that he should plan for replacement in the future. Informed the homeowner of alternatives to peat such as aerobic treatment that would get rid of the modules. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/05/2023 | Alternative | Routine/Scheduled | 147-14-0068 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level Has 1" of solids with 11" of sludge Pulled and cleaned filter -Recirculation Tank: Recirc pump and floats functioning properly Pulled and cleaned pump -Discharge/Pump Tank: Discharge pump and floats functioning properly Pulled and cleaned pump -Media Sheets: Sheets in good shape Sprayed off sheets -Control Panel: Panel working properly Visual and audible alarms working Recirc pulling 7.88amps Discharge pulling 12.48amps -Distribution Box: Customer doesn't want the dbox dug up, he has nice grass -Drain Field: Showing no signs of surfacing or blowouts | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | Dec 30 1899 9:33AM
11/21/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-03-112 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Pumptank needs to be pumped out due to sludge levels. Recomend pumping septic tank at this time. Bushes and saplings to be removed by homeowner around pods as its allowing roots to get into the pods. Follow up visit to be made to auger pods after bushes and saplings are removed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
03/07/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic/atu needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
10/21/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 2000 | BioMicrobics MicroFast |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Third Quarter 2023 inspection. 12" solids in septic tank. 8" solids in MicroFast septic tank. 15" in treatment unit. 2" solids in discharge pump tank. Aeration is adequate. No sign of smell that has been an issue. Cleaned blower air filter. There is no pump out required at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/25/2023 | 07:03 PM
06/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/11/2023 | Alternative | RoutineScheduled | 109-16-0300 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex AX20RT |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. 10" of solids in recirculation portion of treatment unit. 2" of solids in discharge portion of treatment unit. Removed floating solids in recirculation pump chamber. Tested floats, pumps and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 07:03 PM
04/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/22/2023 | Alternative | RoutineScheduled | SD-13-058 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 65.500000 | ["Effluent Screens","SludgeScum Accumulation"] | ["Effluent Screens","Septic Tank Baffles"] | YES | Musty | Clear | [15 empty] | MicroFast Panel | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | 12:00 AM
09/29/2023 | Alternative | RoutineScheduled | 107-05-0559 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
03/28/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
01/06/2023 | Alternative | Routine/Scheduled | 073-STS-105277 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Pump | Pressure | Trenches | Not Applicable | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Dispersal Only - STE LPP Primary septic tank - normal level Pump Tank - float sensors, pump and controls operating. LPP - valves exercised. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 10:00 AM
02/09/2023 | Alternative | Reportable Incident | 115-STS-101676 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | None | None | Pump | Gravity | Trenches | Not Applicable | 750.000000 | ["Control Operation","Distribution Pump Operation"] | ["Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | COSS - Maintenance / Install - VDH Permit 157-22-0140 Primary Septic Tank - installed - riser access to grade - cannister style effluent screen in outlet baffle. Pump Tank - installed - plumbing installed - access riser to grade. Forcemain - 2" PVC - sleeved under circular drive - 4" PVC used as surge arrestor. DBox - 8 port concrete dbox installed - balanced. Header lines - 4" PVC as header lines. Absorption Laterals - 6 - 65' x 3' laterals installed - at 24" depth as amended / approved by AOSE. Pending installation of electrical service and control panel for drawdown, and full certification / commissioning of system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/13/2023 | 06:45 AM
08/07/2023 | Alternative | RoutineScheduled | 043-16-0032 | Clarke | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lord Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/11/2023 | 11:00 AM
10/19/2023 | Alternative | RoutineScheduled Component Maintenance | 139-05-0037 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
10/17/2023 | Alternative | Follow-Up Component Maintenance | 179-15-0255-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to disassemble components in recirc tank and assist pumper with proper pump out of all tanks. Reassembled components and tanks were refilled with a water truck. Replaced return vavle in the head works. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
05/03/2023 |  | RoutineScheduled | 177-07-0409-SR | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity |  | UV |  | ["Recirculation Pump" ,"Disinfection" ,"Effluent Screens" ,"Attached Growth Medium" ,"Control Operation"] | ["Disinfection" ,"Effluent Screens" ,"Attached Growth Medium" ,"Control Operation" ,"Recirculation Pump"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | On May 9, staff from EcoSeptix Alliance completed the jetting of the discharge line. We also installed a new EZ Treat UV bulb and remounted the control panels. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
09/20/2023 | Alternative | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 15000 | Large Treatment System |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Large Treatment unit Not listed in VDH list - Sludge levels--septic front zone 84" sludge and activated sludge section 24-48" sludge. Clarfier zone had 24" of sludge, System is operating good at this time and preventive fall leaf maintenace should be maintained. The tank will need pumping soon, maybe at time of sale it it occur or if usage returns. CRI's Operators onsite will be backwashing system as needed to keep suldge from getting very thick on the bottom. Both Blowers are operational and alternating as they should. Discharge Pump1 ct45,413 vs 44,390 = 1,023 cycles since last visit. etm 187,435 vs 184153min=3,282 min or 54.6 hours - Pump#2 ct41920 vs 40898 = 1,022 cycles- ETM268,966 vs 257,329 = 11,637 min. or 193 hours run time- Continue backwashing to prevent blocking up of sludge. Fallen trees have been cleaned up and repairs have been made to the wet spots in the drip drainfield by owners. as noticed. 25 psi on drip drainfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/30/2023 | 09:30 AM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 182-12-0140 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 10/10/2023 |  | 37.000000 | [5 empty] | Will be sent separately | Inspected | Repaired air supply and pressure gauges | This AOSS should now return to normal function after having provided the above state routine maintenance | 11/22/2023 | 09:18 AM
12/29/2023 | Alternative | RoutineScheduled Component Maintenance | 175-00-0023 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Needs concrete riser lid & electric box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | 01:58 PM
11/10/2023 | Alternative | RoutineScheduled | 087-STS-6190 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1000 | 250 | 750 | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles"] | YES | Pungent | Cloudy | [14 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | 12:00 AM
04/21/2023 | Alternative | RoutineScheduled | 115-19-0103 | Campbell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Biomicrobics Fast |  | Gravity | Gravity | Trenches | UV |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | Musty | [15 empty] | Inspected | Routine visit- Sludge levels-Scum layer 3" in. and 8-12" in. sludge in Septic tank - Fast unit has about 6" sludge, UV bulb working and the green light indicator is lit and UV operational. Blower is working and good aeration in treatment tank observed, CLeaned airfilter on blower. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/30/2023 | 09:30 AM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping the tank prior to next years inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/24/2023 | Alternative | RoutineScheduled Component Maintenance | 154-06-0703 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend replacing the EZ Set lid on the septic tank. Also, please be aware, roots are growing into the Puraflo modules. At some point this may make it difficult to service the peat. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | System appears to be functioning as designed. Tanks appeared the same as in past years. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | UV |  | ["SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [17 empty] | Septic/atu tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/13/2023 | Dec 30 1899 7:05AM
05/12/2023 | Alternative | Reportable Incident | 150-07-044 | King William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | High water due to failed check valve. Replaced check valve and clogged spin filter. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
09/29/2023 | Alternative | Reportable Incident | 02-120-0712A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Came out for alarm call and performed annual maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Flushed and cleaned effluent screen. Not due for pump out. Effluent screen is obsolete and discontinued -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. Structural integrity of discharge tank appears to be intact. -Peat Moss: Peat moss is failing. Noted roots within the peat moss. Structural integrity of tipping bucket appears to be intact. Checked and confirmed tipping bucket is functioning properly. Noticed no Structural issues with the tank but root growth within the peat moss indicates potential features beneath the peat moss. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | Dec 30 1899 11:07AM
11/28/2023 | Alternative | RoutineScheduled Component Maintenance | 061-STS-24415 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Completed annual inspection and routine maintenance. All 4 plastic hinges for the EZ Treat lids are broken. Will ask the manufacturer if upgraded hinges are available. Recirc pump intake was badly clogged. Recommend protecting the pump with a Simtech pump filter. Cleaned 4 EZ nozzles that were clogged. Treated effluent was clear, but perhaps will get more clear now that the recirc pump will be pushing more water (clean intake and all nozzles spraying). Several areas in zone 1 (back yard) were soft prior to starting testing. After 1 complete dose, there were about 4 spots with quarter to half-dollar sized wet spots. No moving effluent seen to suggest a bad emitter or leaking pipe. Dug up 1 wet spot, verified tubing had 11" of cover at that point. Some of the soil close to the tubing was black (anerobic conditions). Advised owner to discuss findings with the AOSE. Dripfield may correct itself over the next year as the soil begins to gain structure. Also advised owner to avoid strong anti-bacterial cleaners, especially those containing quats. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
01/04/2023 |  | Routine/Scheduled | 228-13-0516 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/04/2023 | Jan 1 1900 3:19PM
02/09/2023 |  | Pump-Out Only | 093-15-0035 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Routine Pumpout of treatment system. Primary septic tank pumped empty - effluent screen serviced. Processing Tank - pumped empty - serviced - media drapes serviced. Processing Tank - refilled with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/13/2023 | Jan 1 1900 7:30AM
04/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The anua tank and pump tank need pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
03/06/2023 |  | RoutineScheduled | 133 08 0035 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Western Virginia Water Authority | 1942001145 | Michael | Doss | [9 empty] | [] | [] | YES | None | Clear | [5 empty] | 03/06/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/12/2023 | 06:00 AM
07/03/2023 | Alternative | Routine/Scheduled | 228-03-0301 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/03/2023 | Dec 30 1899 10:30AM
10/12/2023 | Alternative | RoutineScheduled Component Maintenance | SD-08-417 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation" ,"Auxiliary Filter" ,"Recirculation Pump"] | ["Auxiliary Filter" ,"Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Pretty much the same problems that were noted last year. Low drip and flush rates are the biggest concern; drip rate is about 27% below design, and the drip flush rate is about 45% lower than rate observed at startup. Recirc RO float and discharge high level floats are not turning off completely. Those floats tested good. Vent cap for Advantex pod is broken. Owner said he has a replacement, but has not installed it yet. There were a couple of new plastic septic lids set near the tank, but they were the wrong ones and do not fit ribcore risers. Installer ran a 4" pipe through the outlet end of the pump tank as an entry point for the return to septic line (1"). Pipe has settled a fair amount. Not sure if it impedes drain-back or not. An updated repair proposal will be provided to the owner. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
02/28/2023 |  | Routine/Scheduled | 800-STS-15041 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/28/2023 | Jan 1 1900 2:18PM
02/06/2023 |  | RoutineScheduled | 193-STS-94276 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/24/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Need to investigate further but it appears there's a line possibly broken under the ground. No effluent is surfacing but ground is very soft and really green grass at that area. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
01/16/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Grease on filters | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
06/02/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
03/02/2023 |  | RoutineScheduled | 153-STS-20366 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["Disinfection","BlowerCompressorAerator Operation"] | ["Disinfection","BlowerCompressorAerator Operation"] | NA | [7 empty] | 03/02/2023 | Sample Chamber | 20.000000 |  | 1600.000000 |  |  |  | Attached to this report |  | Septic Tank-3"sludge 1"scum/ Microfast-0"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ UV-Light sleeve cleaned, light working/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-123 ETM-17h 13m On-11m 10s Off-2h 40m/ Peak-4/ High-8/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/07/2023 | Alternative |  | 14-100-0361 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 12:00 AM
12/08/2023 | Alternative | Routine/Scheduled | 145-STS-259667 | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/08/2023 | Dec 30 1899 10:00AM
06/20/2023 | Alternative | Routine/Scheduled | 234-17-0013 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | Dec 30 1899 9:40AM
05/16/2023 | Alternative |  | 08-197-A9 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 05/16/2023 |  | 6.510000 | [5 empty] | Will be sent separately |  | BOD: 6.51 TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
02/21/2023 |  | RoutineScheduled | 179-STS-89658 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Sulphitic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
06/21/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
07/05/2023 | Alternative | RoutineScheduled Component Maintenance | SD-03-308 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Level Sensor Operation" ,"Distribution Pump Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Control panel was originally installed in the basement between the outside wall and inside finished wall which subjected it to a lot of condensation. Panel is rusty inside and about 17 years old. Recommend new control panel be installed on the outside, rear wall of the house. Peat is showing its age as evidenced by the amount of compaction and lack of texture. But system gets little use and there was absolutely no ponding. Will reevaluate next year. Poor access to the septic tank lid. Asked owner to keep hedges trimmed to allow better access. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
05/18/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  |  | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/18/2023 | 12:00 AM
10/17/2023 | Alternative | Routine/Scheduled | -STS-15909 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | Dec 30 1899 9:00AM
03/20/2023 |  | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | broken zone valve and sipply line repaired repaired discharge supply | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/28/2023 | 02:17 PM
10/10/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. The septic tank needs additional risers on it to be properly inspected in the future. The timer is et to 6 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/10/2023 | Dec 30 1899 10:30AM
04/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/17/2023 | Alternative | Initial Visit Component Maintenance | 033-STS-92384 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
01/06/2023 |  | Follow-Up | 179-10-0140-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to snake sewer line to remove clogg. Removed clogg ran hose in clean out for 10 minutes and homeowner drained washing machine.No back flow of water seen. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 09:31 AM
05/11/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [7 empty] | 05/11/2023 |  | 85.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/21/2023 | 03:35 PM
04/06/2023 |  | RoutineScheduled | 93-184-5002 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Pump | Pressure | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Level Sensor Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Level Sensor Operation","SludgeScum Accumulation","Dispersal System Operation","Control Operation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/06/2023 | 12:00 AM
10/20/2023 | Alternative | RoutineScheduled | 107-00-0174 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only |  | Siphon | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The syphon tank was in good operating condition. There were no visible leaks in the leech field. (LPD) The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/09/2023 | 12:30 PM
07/31/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Ecoflo | [6 empty] | ["Attached Growth Medium","SludgeScum Accumulation"] | ["Attached Growth Medium","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/12/2023 | 01:50 PM
05/02/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
06/29/2023 | Alternative | RoutineScheduled Component Maintenance | SD-14-243 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-92238 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Attached Growth Medium" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation" ,"Disinfection"] | ["Attached Growth Medium" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation" ,"Disinfection"] | NA | Musty | Clear | [5 empty] | 09/26/2023 |  | 12.000000 |  | 17.000000 |  |  |  | Will be sent separately | Inspected | Routine inspection. Sample taken. Bad off float for discharge tank, replaced under warranty. Trash and grease starting to accumulate in septic tank, spoke to customer about it. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
01/17/2023 |  | Routine/Scheduled | 147-13-0100 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | UV | 300.000000 | Disinfection | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Routine Service - Follow-up from December Inspection. Replaced turbine pump and float sensors. Replaced failed Salcor UV system with New Norweco 1500 UV system. Pumped trash tank empty. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/18/2023 | Jan 1 1900 9:15AM
04/07/2023 |  | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 |  |  | Pump | Pressure | Drip |  | 600.000000 | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/12/2023 | 10:50 AM
10/12/2023 | Alternative |  | 179-STS-89520 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/22/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Other"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 02/22/2023 | Sample Chamber | 36.000000 | [5 empty] | Attached to this report |  | Septic Tank-12"sludge 4"scum/ Microfast-10"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-2688 ETM-652h 35m On-16m 16s Off-4h/ Watermeter-0,294,586.8/ No breakout or spongy areas on the drip field and dosing properly/ Drip areas requires mowing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Distribution box was uncovered and the dialflows were adjusted | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/08/2023 | Alternative |  | 151-16-0038 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2024 | 12:23 PM
07/03/2023 | Alternative | Routine/Scheduled | 09-120-0117A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Hoot |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/03/2023 | Dec 30 1899 9:06AM
03/31/2023 |  |  |  | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Crater | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 2250 | 1250 | 1000 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","SludgeScum Accumulation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] | YES | None | Clear | 6.000000 |  | 6.000000 | [13 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/31/2023 | Jan 1 1900 1:30PM
10/17/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level No solids with 12" of sludge Pulled and cleaned rsv -Recirculation Tank: At normal level 8" of sludge Pulled and cleaned pump, floats and filter -Discharge/Pump Tank: At normal level Has 11" of sludge Pulled and cleaned pump -Media Sheets: Lid and struts intact Sheets in good shape Brushed and flushed laterals -Control Panel: Panel working properly Visual and audible alarms working Recirc pulling 1.06amps Discharge pulling 10.10amps -Distribution Box: Dbox in good shape All lines taking water properly -Drain Field: Showing no signs of surfacing or blowouts | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | Dec 30 1899 9:54AM
07/06/2023 | Alternative | Routine/Scheduled | 2014-126-121(OSE ) | Dinwiddie | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/06/2023 | Dec 30 1899 1:28PM
02/16/2023 |  | Initial Visit | 02-172-0118A | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | AOSS - Initial Visit by Millers Services. - System in Alarm Status. Last known service provider = Coastal Plains Environmental Group System reported pumped 2 weeks prior by Virginia Septic Service & Repair - unknown number of gallons pumped - unknown if reported as required. Primary septic tank - normal level - Processing Tank - RSV clogged - recirc pump serviced - Effluent screen clogged and serviced. Treatment Module - media drapes and spray grid serviced - root intrusion into module present. Pump Tank - float sensors, pump and controls operating - DBox - above normal level (hydraulic overload) | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/20/2023 | Jan 1 1900 7:00AM
09/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and pumping | 1942001330 | Michelle | McKim | 2.000000 |  | 1500 |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 3:10PM
06/16/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/16/2023 | 12:00 AM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance | 099-18-0132 SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend replacing the lid on the Frelo Monster Box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
03/20/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | owes | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
04/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend keeping equipment off lower area of the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/02/2023 | Alternative | RoutineScheduled Component Maintenance | 107-07-0321 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced supply line pressure gauge | This AOSS should now return to normal function after having provided the above state routine maintenance | 08/23/2023 | 06:57 AM
09/19/2023 | Alternative | RoutineScheduled Component Maintenance | -STS-90228 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment looks bad due to media clogged up in remidiator, cleaned media and replaced bug bag. Cleaner air blower filter. Pump tank has to much Sludge, spoke to customer about it and she's going to schedule pump out. HL 29, LL 27. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/07/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, UC Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was replaced and the aeration component of the system appears to be functioning as designed at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
02/11/2023 | Alternative | RoutineScheduled | SD-04-190 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | septic | Microfast | Gravity | Gravity | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | YES | Musty | Clear | [15 empty] | Informal Inspection | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/15/2023 | 09:55 AM
09/11/2023 | Alternative |  | 2005-143-0315 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Disinfection" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/20/2023 | Dec 30 1899 12:57PM
08/30/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
07/14/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Disinfection"] | ["Disinfection" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | Dec 30 1899 1:44PM
01/30/2023 | Alternative | RoutineScheduled | 04-183-182 | Russell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | 12:00 AM
04/28/2023 |  | Initial Visit | VAG408298 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 1.000000 |  | FAST ATU |  | Gravity | Gravity | Discharge | Chlorination |  | ["Disinfection"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation"] |  | None | [17 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/07/2023 | 10:30 AM
06/20/2023 | Alternative |  | 10-125-158 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 06/20/2023 | [7 empty] | Will be sent separately |  | BOD: BDL TSS: BDL | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/20/2023 | 12:00 AM
03/07/2023 |  |  | 087-STS-6587 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Fuji | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [18 empty] | Replaced UV Bulb | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/01/2023 | 12:00 AM
02/09/2023 | Alternative |  |  | Buckingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Piedmont |  |  | Eric | Wilkening | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/29/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-87945 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Cleaned sheets due to sludge on top, water quality better than last year but still a little brown in recirc tank but clear in pump tank. RECIRC: HL6, LL 24, OVERRIDE 1. DISCHARGE: HL 6, 0VERRIDE 2. "R" COUNTS BACK TO ZERO. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 07:39 AM
07/18/2023 | Alternative | Routine/Scheduled | 228-18-0392 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Puraflo |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/18/2023 | Dec 30 1899 8:10AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/20/2023 | Alternative | RoutineScheduled | 127-STS-31855 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Norweco Singulair |  | Pump | Gravity | Trenches |  |  | [] | ["Auxiliary Filter","Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/19/2023 | 12:00 AM
05/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/03/2023 |  | RoutineScheduled | 04-120-0658AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 3000 | 1000 | 1000 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","SludgeScum Accumulation","Dispersal System Operation","Effluent Screens","Level Sensor Operation"] |  | None | Clear | 7.000000 |  | 7.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | Jan 1 1900 2:30PM
01/11/2023 |  |  | 2016-143-0150 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | 12:00 AM
10/29/2023 | Alternative | Reportable Incident | 2013-143-0167 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Upon arrival, I found the control panel was not receiving power. I reset the breaker and system appeared to be functioning properly. Checked and confirmed control breaker and LOGO unit are functioning properly. Informed homeowner to conserve water usage for 24 hours. Reminded Mrs. King about previous recommendations for pump and floats | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | 08:40 AM
03/09/2023 | Alternative | Reportable Incident | 159-06-0094 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | [18 empty] | COSS - Maintenance - GMP2018-02 Replaced failing DBox with new 8 port concrete DBox. Spliced to existing conveyance line Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | 07:15 AM
12/07/2023 | Alternative | Routine/Scheduled | -STS-6606 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Pressure | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/07/2023 | 01:59 PM
01/30/2023 |  | RoutineScheduled | 175-06-0431 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | On arrival, system was found to be in high level alarm status, the pump was running, and the water level was down to the bottom of the pump suction. Alarm silenced - reset. Alarm light was not on because the lightbulb was burnt out; assembly replaced. Blower and pump contactor chatter observed. The wiring had caused an issue with the contactor coils; both contactors replaced with used, but operational, contactors. Latching relay base and glass relay were shorted out, replaced. Enabling and alarm float switches failed testing, replaced. LB electrical cover at blower housing was damaged and wires exposed, replaced. Blower bearing noise observed. Air pre-filter cleaned. Applied fiberglass patch to mower-damaged access manway. Single-point aeration has developed at the access end of the tank - repair required. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
08/08/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Peat in PuraFlo's is in poor condition (6 PuraFlo Units) | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | Dec 30 1899 3:58AM
09/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Worked with Rooterman to remove grease that had accumulated int he septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
11/10/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 11/10/2023 | Dec 30 1899 8:30AM
03/31/2023 |  | RoutineScheduled | 033-07-0340-SR | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | As noted previously, we recommend replacing the Orenco riser lid on the Septic Tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
05/05/2023 | Alternative | RoutineScheduled | 109-STS-31105 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
03/20/2023 |  | Reportable Incident | 175-19-0149 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NO | [17 empty] | Service call only: Replaced faulty STEP 20 Pump Counts: Pump-130039 ETM-669992 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
04/19/2023 |  | RoutineScheduled | 107-10-0114 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 3169.000000 | [] | [] |  |  |  | 6.820000 | 2.690000 | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | 03:10 PM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance | 107-03-0526 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 10/03/2023 |  | 63.000000 | [5 empty] | Will be sent separately | Inspected | Installed remanufactured blower at time of service | This AOSS should now return to normal function after having provided the above state routine maintenance | 11/22/2023 | 09:18 AM
10/03/2023 | Alternative |  | SWP-04-936 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
06/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
09/06/2023 | Alternative | Routine/Scheduled | 05-160-0094 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 183.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | 01:15 PM
03/15/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/13/2023 | Alternative | RoutineScheduled Component Maintenance | 177-14-0093-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend treating the media in the EcoPod unit and pumping the tank afterwards. We also recommend installing a PVC pipe extension onto the pump flow collar. The two bottom floats are not working and should be replaced. Finally, we recommend replacing the heater in the headworks box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
02/06/2023 |  | RoutineScheduled | 179-06-0420-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
09/22/2023 | Alternative | Routine/Scheduled | 09-174-0084 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/22/2023 | Dec 30 1899 10:32AM
10/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
05/07/2023 | Alternative | RoutineScheduled | 001-STS-91737 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | AQUASAFE |  | Pump | Pressure | Mound | UV |  | [] | [] | [18 empty] | REPAIRED BLOWER LINE. EVERYTHING WORKING AS IT SHOULD. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/18/2023 | 02:30 PM
09/18/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Outlet tee appears to be intact. Structural integrity of tank appears to be intact. Not due for pump out -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Structural integrity of tank is deformed with signs of groundwater infiltration. -Aeration: Water level normal. Not due for pump out. -Air Pump/Blower: Checked and confirmed aerator is functioning properly. Flushed and cleaned aerator air intake filter. -Control Panel: Checked and confirmed components within control panels are functioning properly. Checked and confirmed visual alarms are functioning properly. Checked and confirmed audible alarms are functioning properly Drip Field: Flushed and cleaned disk filter. Found no signs of surfacing on the dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | Dec 30 1899 3:58PM
02/08/2023 |  | Follow-Up | 175-14-0269 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | None | Cloudy | [5 empty] | 02/08/2023 |  | 90.000000 |  |  | 32.000000 |  |  | Will be sent separately | Inspected | Influent samples were collected in the septic tank next to the inlet tee. BOD and TSS were lower than average for most American households. HEM (fats/oil/grease) tested at 7.3 mg/L. Sampling results have been forwarded to the local Microfast dealer to get his input. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
02/14/2023 | Alternative | Pump-Out Only | 07-160-0147 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 | 1000 | Ecoflo (peat moss) | [6 empty] | [] | [] | [18 empty] | - recommend tuff-tite lid be replaced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/15/2023 | 12:00 AM
11/02/2023 | Alternative | Follow-Up Component Maintenance | 179-06-0266-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced splitter box and distribution box #1 with ?monster? distribution box. Cut out root clogged/damaged sections of headers as necessary and replaced with new pipe. Replaced bad lid on distribution box #2. Added root kill to all lines. Jetted lines as necessary. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
01/09/2023 |  | Routine/Scheduled | 05-120-0329A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. BioFilter - Peat moss in fair condition - raked / turned. Pump Basin - float sensors, pump and controls operating. DBox - intact - one header line root clogged. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | Jan 1 1900 7:45AM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/21/2023 |  |  | 033-12-0097-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
08/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 08/07/2023 |  | 57.000000 | [5 empty] | Will be sent separately | Inspected | Media Cleaner added All tanks pumped | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
12/18/2023 | Alternative | RoutineScheduled Component Maintenance | SD-12-174 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001236 | Stuart | Lynn | 2.000000 | 16800 | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Dispersal System Operation" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Dispersal System Operation" ,"Attached Growth Medium"] | NA | Musty | Clear | [5 empty] | 12/18/2023 | Sample Tap | 20.000000 |  |  | 7.000000 | 23.000000 |  | Will be sent separately | Inspected | Report covers the month of December, 2023 12-1-23- Steven replaced recirc pump and pressure gauge on AX - 2 1 Steve at AQWA reset recirc rates check in 2 weeks 12-7-23 Steve at AQWA adjusted recirculation with Steven on site mrlynn - Makenzie Lynn - 12/4/2023 6:50:15 PM - Steve Barry needs to walk thru some diagnosing of low recirc alarms - give him a call when you are on site Cleaned spinners and a portion of the sheets that were bridging bad. System now does not go into low water recirc but will need to service 1 12-18-23 Sampling event 12-31-23 Pump 7 Meter reading: - 16953820 Pump 8 Meter 13390220 Return Meter Reading: - 1223642.625 Pump Outs 12-10-23, 12-12 - 23, 12-20-23, 12-29-23 16,800 Advantage | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 01/16/2024 | 01:58 PM
11/20/2023 | Alternative | RoutineScheduled | 107-08-0329 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 2.000000 |  | Advantex AX20 |  | Gravity | Pressure | Drip | Not Applicable |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | None | Clear | 6.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | 08:00 AM
07/28/2023 | Alternative | Follow-Up Component Maintenance | 177-14-0056-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"SludgeScum Accumulation"] | ["Control Operation" ,"SludgeScum Accumulation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Met local pumper (Marshall's Septic) on site and removed recirc pump & vault, floats, and biotube filter to allow for a complete pump-out of the septic/recirc tank. Rinsed off all components before reinstalling. Drip field not spongy prior to test cycles. Ran a complete cycle for zone 1 (where soft spots were found at inspection) and zone 3. Only 3 or 4 silver dollar-sized wet spots appeared in zone 1. Dug down at those spots (near the edge of the zone) and discovered tubing was only covered by 7 to 8" of topsoil, whereas the plans called for 12". Reduced drip run time by 1 min 51 sec to allow charging volume to be included as part of the dose. Suspect this along with adding additional 4" of topsoil to the spongy area will eliminate the minor malfunction. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:19 PM
05/16/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX25 RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Yearly inspection visit. Septic tank 3-4"scum, Sludge level-8-14". May want to arrange FOUTZ to pump out the septic tank-front tank light green lid. Recirc- No scum in treatment and 8" of sludge in Recirc tank and 5" in Discharge zone. Media looked good, spray pattern was good, Cleaned eflfuent filter - Sprayed off the media. All Floats switched tested good. Pumps both opperate. System has a normal odor and nothing unusual noted. Does not need pumping this year. Recirc run time 898 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance | 113-STS-25897 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
03/28/2023 | Alternative | RoutineScheduled | SD-09-81 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | A new blower control panel was installed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
12/04/2023 | Alternative | RoutineScheduled Component Maintenance | SP 97-502 | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Control Operation" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | As noted previously, we recommend replacing the alarm horn, alarm light and the concrete lid and riser. We also recommend replacing the glow meter which is not working. Finally we recommend resealing the risers that their base. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 01/02/2024 | 11:12 AM
07/07/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 | 2 | Septic / Advantex Recirculation Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | [17 empty] | Septic Tank-10"sludge 1"scum/ Advantex-6"sludge 0"scum/ Pump Tank-0"sludge 1"scum/ No pump out needed at this time/ Recirc. pump intake cleaned/ Advantex media in good condition, sample box clear/ Controls, floats, pumps, and alarms functioning properly/ Pump- On 2m 28s Off-6h/ Peak-4h 48m/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/21/2023 | Alternative | Routine/Scheduled | 199-06-0024 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump, effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | Dec 30 1899 9:30AM
01/09/2023 |  | Reportable Incident | 179-08-0123-ST | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Distribution Pump Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Distribution Pump Operation" ,"Control Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | High level alarm apparently caused by a running toilet as pump, panel and floats all working correctly. Outside alarm cleared just prior to this service call, and inside alarm cleared after doing a drawdown to confirm flow rate. Pump is around 14 years old but still running fine. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 09:31 AM
04/17/2023 | Alternative | Routine/Scheduled | 093-03-0092 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | Dec 30 1899 11:20AM
04/13/2023 |  | RoutineScheduled | 17-192-166 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","SludgeScum Accumulation","Dispersal System Operation","Control Operation"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/13/2023 | 12:00 AM
04/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/26/2023 | Alternative | RoutineScheduled Component Maintenance | 175-07-0311 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 07:39 AM
08/29/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-88276 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
03/27/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Advantex AX20 RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | RTU 123226 - Septic tank under 1 " Scum and 8" sludge, Lots of trash floating in tank- Try to minimze as it may clog the pump. In Treatment- recirc zone 8" sludge and 8" sludge on discharge. Clear effluent on top. Recirc pump and Discharge pumps both operational. Cleaned effluent filter, Alarm operational, Tested floats all good. Ran in test mode, Good spray in box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | 09:30 AM
09/13/2023 | Alternative | Reportable Incident | 2006-143-0362 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | [] | [] | [18 empty] | Installed new Microfast blower | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/15/2023 | Alternative | Reportable Incident |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Orenco Advantex | [6 empty] | Distribution Pump Operation | Distribution Pump Operation | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/29/2024 | 01:18 PM
11/29/2023 | Alternative |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ Microfast Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-12"sludge 6"scum/ Microfast-16"sludge/ Pump Tank-1"sludge/ Pump out necessary on the Septic- Microfast Tank/ Controls, pumps, floats and alarms are functioning properly/ Blower air filter cleaned and blower working properly/ Counts: Pump1-1212 ETM-35h 43m/ Pump2-1193 ETM-35h 10m/ Peak-8/ High-6/ No breakout or spongy areas in the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/15/2023 |  | RoutineScheduled | {FIPSCode}-STS-5420 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 5 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/15/2023 | 12:00 AM
11/17/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Henrico | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Was flooded due to clogged filter( hasn't been cleaned in 2+ years) Has 1" of solids with 6" of sludge Pulled and cleaned filter and allowed tank to go down -Recirculation Tank: Level came up due to septic tank being full Was able to get it back down to normal level Pulled and cleaned pump and floats -Discharge/Pump Tank: Level came up due to septic tank being full Was able to get it back down to normal level Pulled and cleaned pump and floats -Media Sheets: Sheets in good condition Sprayed off sheets Brushed lateral -Control Panel: Panel in working order Recirc pulling 8.51amps Discharge pulling 11.7amps -Drain Field: Showing no signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 10:59 AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/20/2023 | Alternative | RoutineScheduled Component Maintenance | 179-17-0237-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Auxiliary Filter"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
08/28/2023 | Alternative | Routine/Scheduled |  | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | New owner - routine service - last documented service conducted 02/02/21. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes has severe bridging, causing ponding - requires removal and pressure washing. PUmp tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/31/2023 | Dec 30 1899 8:00AM
04/18/2023 |  | Routine/Scheduled | 041-STS-260467 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/18/2023 | Jan 1 1900 4:52PM
09/12/2023 | Alternative | Routine/Scheduled | 041-STS-259578 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/12/2023 | Dec 30 1899 4:13PM
05/05/2023 | Alternative | RoutineScheduled | SD-06-81 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 43.750000 | ["SludgeScum Accumulation","Effluent Screens","Dispersal System Operation"] | ["Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [17 empty] | Ponding Puraflo | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/09/2023 | 10:00 AM
01/09/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 4.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["SludgeScum Accumulation" ,"Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Required pumping of primary septic tank 1 and secondary tank | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/18/2023 | 04:10 AM
01/17/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20469 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [5 empty] | 01/17/2023 |  | 75.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
08/23/2023 | Alternative | RoutineScheduled Component Maintenance | 182-19-0146 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced uv bulb and cord Primary tank was pumped Installed new blower | This AOSS should now return to normal function after having provided the above state routine maintenance | 09/20/2023 | 01:07 PM
01/06/2023 |  | RoutineScheduled | 065-STS-33449 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | 12:00 AM
08/30/2023 | Alternative | RoutineScheduled | 2006-143-0155 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/10/2023 | Alternative | Reportable Incident | 810-STS-3789 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to a smell. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the filter in the septic tank (filter was stopped up). Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The pressure switch on the aerator is not hooked up - needs to be. Replaced the UV ballast. The timer is set to 7 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/10/2023 | Dec 30 1899 10:00AM
10/26/2023 | Alternative | RoutineScheduled Component Maintenance | 175-14-0514 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | ATU blower very loud. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
06/07/2023 |  |  | ST-05-370 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
06/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001527 | Jacob | Hott | 1.000000 | 1250 | Septic | Advantix | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/07/2023 | Alternative | Pump-Out Only | 136-02-117 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | [17 empty] | Pumped Out | Pumped aeration tank as recommended during last service event. Refilled with fresh water for system restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/09/2023 | 07:30 AM
03/14/2023 |  | Routine/Scheduled | 145-STS-259128 | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1060 | Purasys |  | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | [17 empty] | System checked. System appears to be operating normally. Aerator 1605.28, Clearwater 106.51, discharge 32.40 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | Jan 1 1900 2:06PM
01/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Blue Ridge | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 1-3 0-5 | 0-0 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [5 empty] | 11.000000 | [11 empty] | Inspected | home owner will pump out sysyem | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/23/2023 |  | RoutineScheduled | 003-STS-29072 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Trenches | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 12:00 AM
05/18/2023 | Alternative | Routine/Scheduled | 166-10-087 | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 4500 | Microfast |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 45.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/18/2023 | 04:48 PM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Forcemain for pump to eztreat is broken at the 90 and is not pumping effluent to unit. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/15/2024 | 12:23 PM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | UV |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | 6.900000 | 12.700000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/11/2023 | Dec 30 1899 11:24AM
04/20/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Septic Tank under 1", 14" sludge, Recirc Zone 24" Sludge- Pump Tank 12-16" fine sludge - Cleaned BioFilter, RSV and brushed and flushed Sprayer Manifold. Tested both Pumps ok, Alkarm ok, Floats good. Alarms due to filter clog a few month ago and owner had cleaned the filter. All floats indicate. Recirc pump run time 3011 Hours and 75047 cycles, Discharge pump run time 1146.4 hours and 18257 cycles. Ran in test mode and all good, System is connected to monitoring | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
11/30/2023 | Alternative | RoutineScheduled Component Maintenance | 177-07-0198-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Distribution Pump Operation" ,"Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
12/01/2023 | Alternative | RoutineScheduled | C-122-08-0034 | Craig | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | King's Alternative Septic | 1942001112 | William | King, II | 1.000000 | 1000 | BioMicrobics Microfast 0.5 |  | Pump | Gravity | Trenches | Not Applicable | 250.000000 | ["None"] | ["None"] | NA | [17 empty] | System is working correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/03/2023 | 12:00 AM
10/24/2023 | Alternative | Reportable Incident | 16-142-0266 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm call: -Customer stated alarm goes off randomly Found system at normal level Ran recirc pump and found there was excessive draw down in recirc vault. Pulled biotube filter and it was 90% clogged Pulled and cleaned biotube filter, pump, rsv,and floats Tested and confirmed all components are functioning properly Customer approved Semi-annual Maintenance and inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | Dec 30 1899 4:16PM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/07/2023 |  | RoutineScheduled |  | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 2.000000 |  | none | none | Pump | Gravity |  | UV |  | ["Disinfection" ,"Effluent Screens" ,"Attached Growth Medium" ,"Control Operation" ,"Recirculation Pump"] | ["Disinfection" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Control Operation"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | Installed new Salcor UV bulb and plastic alarm horn. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
03/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/03/2023 |  |  | 04-163-0284 | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | This system does still need the yearly maintenance performed, as we only replaced the Clearstream blower. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/05/2023 | 12:00 AM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping Microfast | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
10/23/2023 | Alternative | Reportable Incident |  | Buckingham | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 2.000000 | 2000 | Eljen GSF |  | Pump | Pressure | Mound | Not Applicable | 350.000000 | ["Effluent Screens","SludgeScum Accumulation","Control Operation","Distribution Pump Operation"] | ["None"] | NO | [16 empty] | Pumped Out |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/23/2023 | Dec 30 1899 11:30AM
08/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/22/2023 | 11:22 AM
10/30/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Sandfilter, Recirculating |  | Pump | Gravity | Trenches |  | 600.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | 12:31 PM
05/19/2023 |  | RoutineScheduled | 175-15-0003 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-10"sludge 4"scum/ Microfast-18"sludge/ Pump Tank-1"Sludge/ Pump out required on the Septic-Microfast Tank/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-2084 ETM-12122/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/12/2023 | Alternative | Routine/Scheduled | 136-06-0191 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component Normal level 14 in of sludge less than 1 in of solids Pulled and cleaned filter No signs of infiltration Discharge/Pump Tank Condition of above Component Notes for above Component Normal level 6 in of suspended solids Tested floats and pump all working as should All plumbing intact and pump moving water properly No signs of infiltration Aeration Condition of above Component Notes for above Component Normal level 1 in of suspended solids Pulled and cleaned weir Pulled and cleaned diffuser Float in functional No signs of infiltration Air Pump/Blower Condition of above Component Notes for above Component 120 volts coming in Pulled and cleaned filter Air pressure sensor intact and functional Control Panel Condition of above Component Notes for above Component 120 volts coming in All visual and audible alarms functional Discharge pump pulled 8.1 amps Air pump pulled 1.6 amps All components working as should Distribution Box Condition of above Component Notes for above Component Normal level 6 lines all intact and taking water properly Speed balancers intact and functional In good condition Drain Field Condition of above Component Notes for above Component No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 12:53 PM
05/19/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Recommended to homeowner media replacement | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/22/2023 | 11:15 AM
06/05/2023 | Alternative | RoutineScheduled | C19-180-0002 | Roanoke | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Alleghany-Roanoke | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [18 empty] | - drainfield has been disturbed, referring to AOSE to assessement | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/22/2023 | 12:00 AM
03/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/08/2023 | Alternative | Reportable Incident Component Maintenance | 099-06-0342-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to blown fuse in the panel caused by a bad filter solenoid. Replaced solenoid and fuse. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
02/07/2023 |  | RoutineScheduled | SWP-04-443 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | All tanks pumped due to paint in the tanks. Cleaned pump tank. Will clean & treat ATU at the next inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
05/17/2023 | Alternative | RoutineScheduled | 154-12-0193 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | 12:00 AM
09/18/2023 | Alternative | Reportable Incident | 171-05-0584 | Pittsylvania | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Pittsylvania-Danville | Acres of Virginia, Inc. | 1922001044 | Melvin | Collins | 1.000000 | 1500 | Eco Flo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Other"] | ["Other"] | [18 empty] | Bio Filter media was replaced with new media. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/23/2023 | 12:30 PM
07/10/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-88990 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | UV |  | ["Effluent Screens" ,"Recirculation Pump" ,"Disinfection"] | ["Recirculation Pump" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The UV light is not working. A new bulb should be installed and possibly the UV cord also. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
09/05/2023 | Alternative | RoutineScheduled | ST-04-355 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Elite Onsite | 1942001726 | Drew | Saunders | 2.000000 | 2000 | 1000 | 1000 | Pump | Gravity | Trenches | Not Applicable | 350.000000 | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | 03:45 PM
11/06/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast |  | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 11/06/2023 | Sample Chamber | 35.000000 | [5 empty] | Attached to this report |  | Septic Tank-2"sludge 4"scum/ Microfast ATU Tank-18"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ Chemical cleaning and pump out required on the Septic-Microfast Tank/ Controls, pump, floats and alarms are functioning properly/ Blower air filter cleaned and blower is working correctly/ Counts: Pump-7162 ETM-1663h 6m/ On-14m 30s Off-3h/ Peak counts-20 ETM-82h 26m/ High level-68/ Watermeter-0485883.51/ No breakout or spongy areas on the drip field and dosing properly. Returned on 11/10/2023 for the chemical cleaning and pump out, completed and should now return to normal operation. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/14/2023 | Alternative | Pump-Out Only | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 1.000000 | 750 |  |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["SludgeScum Accumulation"] | NA | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | Dec 30 1899 5:20PM
02/23/2023 | Alternative | RoutineScheduled | 101-08-0022 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/25/2023 | 12:00 AM
10/13/2023 | Alternative | Follow-Up Component Maintenance | 175-15-0477 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Installed new Norewco UV unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
12/11/2023 | Alternative | RoutineScheduled | SD-03-177 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2100 | septic | Advantex | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | YES | Musty | Clear | 7.400000 |  |  | 0.990000 |  | 12/11/2023 | Sample Chamber | 2.000000 | 0.000000 |  | 7.000000 | [5 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/02/2024 | 11:20 AM
01/25/2023 | Alternative | Routine/Scheduled | 136-07-0245 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 2500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Septic Tank - Garage - normal level Pump Basin - Garage - float sensors, pump and controls operating. Processing tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes - heavy ponding - recommend replacing - spray grid serviced. Pump tAnk - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | 12:00 AM
09/19/2023 | Alternative | Routine/Scheduled | 157-18-0074 | Mathews | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The UV is not working - needs a ballast. The timer is set to 3 minutes every 2 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/19/2023 | 12:00 PM
05/31/2023 | Alternative | RoutineScheduled | 101-STS-95583 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Hutchens Septic Services LLC | 1942001509 | Robert | Hutchens, Jr. | 1.000000 | 1000 | Bio Coir NS500 |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/31/2023 | 12:00 AM
05/24/2023 |  | RoutineScheduled | 182-15-0223 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter" ,"Dispersal System Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter" ,"Dispersal System Operation"] | NA | [7 empty] | 05/24/2023 |  | 15.000000 | [5 empty] | Will be sent separately | Inspected | Replaced blower and repaired air supply Repaired 2 broken pipes in field Installed return pressure gauge Lab Sample Normal Recommend keeping horses off drainfield | This AOSS should now return to normal function after having provided the above state routine maintenance | 06/21/2023 | 03:35 PM
07/27/2023 | Alternative | Reportable Incident | 109-02-0784 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 500 | Bio Microbics-Fast |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [16 empty] | Inspected | After trouble shooting determined the old blower locked up. Old blower had bearing locked up due to age and heat. Will return to replace | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/30/2023 | 09:30 AM
10/17/2023 | Alternative | RoutineScheduled Component Maintenance | 179-15-0241-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | YES | Musty | Clear | [5 empty] | 10/17/2023 |  | 2.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Bad off float for recirc, replaced. Media need raking, raked. Drainfield needs mowing, customer has company schedule to do it next week. Recirc tank needs pumping due to sludge level on treatment side, spoke to customer about it and he said he will call pumper this week to get it done. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
03/07/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 03/07/2023 | Sample Chamber | 11.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/04/2023 |  | RoutineScheduled |  | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Blue Ridge | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Septic Tank pumped | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Pad | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
08/08/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Pending Review | EHD - West Piedmont | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Annual Inspection. Septic tank zone had 10" in sludge, 16-18" in sludge on discharge side, 8" sludge in pump tank. Box 204474- System has old phone line monitoring and is connected to new panel and new pumps and new floats. Tested all component and they are good. FLoats and alarm good. Pulled filter it was dirty cleaned it and brushed and flushed spray manifold. pulled RSV and hosed off media. Added new sahocks to the new lids on the tank and they now open and close nicely. System has not yet been pumping out and may want to have the treamtnet tank pump think winter or prior to next years visit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | 09:30 AM
10/19/2023 | Alternative | Routine/Scheduled | S06-180-0068 | Roanoke City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/19/2023 | Dec 30 1899 11:00AM
04/04/2023 |  | RoutineScheduled | 175-12-0132 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
02/27/2023 |  | RoutineScheduled | 179-14-0367-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
09/06/2023 | Alternative | Routine/Scheduled | 151-02-0120 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | [7 empty] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | 05:28 PM
02/15/2023 |  |  | 16-142-0339 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/01/2023 | 12:00 AM
03/04/2023 |  | RoutineScheduled | 175-10-0305 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.300000 |  |  | 1.900000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/07/2023 | 12:00 AM
10/10/2023 | Alternative | RoutineScheduled | 147-14-0009 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Hutchens Septic Services LLC | 1942001509 | Robert | Hutchens, Jr. | 1.000000 | 1000 | Advantex AX-20 RT |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear | [14 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 12:00 AM
03/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/31/2023 | 12:26 PM
05/01/2023 |  | RoutineScheduled | 179-09-0042-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Multiple trees are growing along the upper zone of the drip dispersal system. These should be removed. We replaced a defective bottom float in the Advantex Recirculation Tank We also cleaned water out of the recirc pump junction box. The clogged Biotube was also cleaned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
12/11/2023 | Alternative |  | 680-STS-26563 | Lynchburg | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Acres of Virginia, Inc. |  | Melvin | Collins | 4.000000 | 3040 | Septic Tank | EZTREAT | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter","Other"] | ["Auxiliary Filter","Other"] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/12/2024 | 12:00 AM
02/28/2023 |  | RoutineScheduled | 175-14-0474 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation"] | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Media is starting to clog, but treatment still looks decent. Will continue to monitor. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
04/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/28/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/09/2023 | 12:00 AM
08/14/2023 | Alternative | RoutineScheduled | 043-15-0080 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | septic | Fast | Pump | Pressure | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation","Level Sensor Operation"] | [18 empty] | 2" of Scum & 6"-10" of sludge, 48" overall liquid depth. Pump tank is clean. Field is dry with no leaks. Alarms are working, transducer and pump ae working. 263:16:24 hrs and 1515 Cycles on pump | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 09:45 AM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/15/2023 | Dec 30 1899 2:02PM
11/14/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Trenches |  | 450.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | 10:48 AM
12/05/2023 | Alternative | Reportable Incident Component Maintenance | 177-10-0205-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to burnt wires for discharge pump in junction box. Repaired wires. Inlet wedge lid leaks but conduit runs right on top of wedge lid. Outlet riser leaks as well. Pumped down septic tank and no visible leaks were found on mid seam. Follow up visit to be made to do routine maintanance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
09/26/2023 | Alternative | Reportable Incident Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Multiflo FTB | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed N163/230v Effluent pump & (3) control floats. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
03/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Clearstream | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
01/09/2023 |  | Routine/Scheduled | 234-16-201 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | Jan 1 1900 11:05AM
03/24/2023 |  | RoutineScheduled | SR-04-540 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. GPM not accurate due to system not having a water meter. Found trash in return valve solenoid, cleaned. Return solenoid for return valve was in bad conditions replaced with used good solenoid we had in truck. HL 42. 23PSI. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
03/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping Pump chamber. There is a fair amount of scum visible. Small roots were seen around the riser but does not appear to be an issue. Recommend monitoring and resealing if necessary. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/25/2023 | Alternative | Pump-Out Only |  | Lancaster | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | AOSS - Maintenance - Peatmoss biofilter changeout. Pumped septic tank for storage and to allow peatmoss media to dry. PUmpout only at this point - | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/29/2023 | 06:45 AM
01/31/2023 |  | RoutineScheduled | 175-18-0493 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Ecopod | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic-4"sludge 5"scum/ Ecopod E-75-6"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-1316 ETM-73h 29m/ High-8/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/30/2023 |  | Routine/Scheduled | 04-163-0159A | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes - ponding recommend replacing - spray grid serviced. Pump Tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | Jan 1 1900 8:00AM
01/06/2023 |  | Routine/Scheduled | 228-17-0280 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/06/2023 | Jan 1 1900 11:45AM
07/24/2023 | Alternative | Initial Visit | 015-STS-337363 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 2.000000 |  | Advantex AX20 |  | Gravity | Pressure | Drip | Not Applicable |  | ["Other","Control Operation","Effluent Screens","Dispersal System Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles"] | YES | Septic | Discolored | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/02/2023 | 05:35 PM
04/28/2023 |  | Initial Visit | VAG408299 | Rockbridge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 1.000000 |  | FAST ATU |  | Gravity | Gravity | Discharge | Chlorination |  | ["Disinfection"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] |  | None | [17 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/07/2023 | 10:30 AM
05/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/31/2023 | Alternative | RoutineScheduled | 154-05-1074 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Randy's Complete Water & Wastewater Services | 1942001335 | Randy | Gray | 1.000000 | 1000 | Norweco/Singular |  | Gravity | Pressure | Drip |  | 75.000000 | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | 12:00 AM
09/27/2023 | Alternative | RoutineScheduled | SD-13-158 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1500 | septic | Puraflo | Gravity | Pressure | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/29/2023 | 09:25 AM
09/05/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | Western Virginia Water Authority | 1942001145 | Michael | Doss |  |  |  |  | Gravity | Pressure | Drip | UV |  | ["None"] | ["None"] | YES | None | Clear | [5 empty] | 09/05/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | 03:20 PM
01/13/2023 |  | Routine/Scheduled | 228-11-0648A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | EZ Treat Sandfilter |  | Pump |  |  |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | [5 empty] | 01/24/2023 |  | 8.000000 |  | 1.000000 | 2.000000 | 58.000000 |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 10:00AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/28/2023 | Alternative | Initial Visit | 12-160-0175 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner |  |  | Microfast | [6 empty] | [] | [] | [17 empty] | Inspected | - replaced blower - completed inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/29/2023 | 12:00 AM
12/21/2023 | Alternative | Routine/Scheduled | RRAR-9UHLHF | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | Dec 30 1899 11:45AM
06/01/2023 |  | RoutineScheduled | 124-STS-2379 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Virginia Beach | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1875 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/24/2023 |  | RoutineScheduled | 167-STS-15634 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","SludgeScum Accumulation","Dispersal System Operation","Control Operation"] | ["Disinfection","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/24/2023 | 12:00 AM
03/27/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
12/05/2023 | Alternative | RoutineScheduled Component Maintenance | 047-STS-22055 | Culpeper | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity |  | Not Applicable |  | ["Recirculation Pump" ,"Disinfection" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Disinfection" ,"Effluent Screens" ,"Attached Growth Medium"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | Responded to alarm call by owner. Relay was chattering, but system was not in high level. Manufacturer recommends replacement if this reoccurs. We recommend replacing conduit for pump wiring with larger conduit to connect o junction box on outside of the pump tank, especially if system alarms again. As noted previously, we recommend replacing the EZ Treat filter media | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 01/02/2024 | 11:12 AM
04/14/2023 | Alternative | RoutineScheduled | 187130206 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 12:00 AM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
06/26/2023 | Alternative |  | 04-192-236 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 06/26/2023 |  | 3.170000 |  |  | 1.200000 |  |  | Will be sent separately |  | BOD: 3.17 TSS: 1.20 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/26/2023 | 12:00 AM
02/22/2023 |  | Routine/Scheduled | 16-120-0370AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 | Aqua Klear |  | Pump | Gravity | Trenches | Not Applicable | 150.000000 | Distribution Pump Operation | Distribution Pump Operation |  | Musty | Cloudy | [15 empty] | Effluent pump operation float replaced. Air motor filter serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | Jan 1 1900 10:30AM
09/13/2023 | Alternative | RoutineScheduled | 08-125-062 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
08/07/2023 | Alternative | Routine/Scheduled | 234-03-11158 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | Dec 30 1899 8:40AM
02/16/2023 |  | RoutineScheduled | 087-STS-6479 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Carrington Pump & Irrigation | 1942001121 | John | Carrington |  |  | Norweco |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/16/2023 | 12:00 AM
09/25/2023 | Alternative | RoutineScheduled | 175-03-0022 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [17 empty] | Septic/ atu needs pumped out | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/29/2023 | 05:15 PM
10/30/2023 | Alternative |  | 033-09-0027-sp | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/30/2023 |  | RoutineScheduled |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 1-6 0-0 | 0-0 | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear |  |  | 12.000000 | [11 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 10:00 AM
01/18/2023 |  | RoutineScheduled | SD-87-25 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | DeHaven's Backhoe Service Inc. | 1942001541 | Wayne | Edmonson | 6.000000 | 6000 | Septic tank | E Z treat | Pump | Pressure | Drip | Not Applicable | 600.000000 | ["None"] | ["None"] | NO | [17 empty] | Repair system is a drip old original is lpd since new system is in service old lpd is working well | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/25/2023 | 04:00 PM
05/11/2023 |  | Routine/Scheduled | {FIPSCode}-STS-20170 | Clarke | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 |  |  | Pump | Pressure | Trenches |  | 450.000000 | ["Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/15/2023 | 01:27 PM
01/25/2023 |  | Follow-Up | {FIPSCode}-STS-19857 | Wise | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | EHD - Lenowisco |  |  |  |  | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination | 450.000000 | ["None"] |  |  | Musty | Clear | 6.000000 | 6.000000 | [14 empty] | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 01/25/2023 | 12:00 AM
03/27/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | norweco tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
06/05/2023 | Alternative | Routine/Scheduled |  | Loudoun | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Pump | Pressure | Drip |  | 600.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/22/2023 | 01:39 PM
01/30/2023 | Alternative |  | 154-02-0942 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
07/18/2023 | Alternative | Routine/Scheduled | 550-STS-5866 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/19/2023 | Dec 30 1899 10:25AM
07/17/2023 | Alternative | Pump-Out Only | 043-10-0125 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 | 1000 Gallons Septic Tank | 1 | [6 empty] | [] | [] | NO | [16 empty] | Pumped Out | Pumping Only | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 12:00 AM
04/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
05/16/2023 |  | RoutineScheduled | SWP-04-351 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. peat moss showing its age, evaluate next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance | 175-15-0078 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | 11:24 AM
01/09/2023 |  | Routine/Scheduled | 234-18-003 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | Jan 1 1900 8:10AM
06/28/2023 | Alternative | Routine/Scheduled | 234-14-80 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | Dec 30 1899 10:00AM
03/22/2023 |  | Initial Visit | 015-STS-338141 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip |  |  | ["Other"] | ["Other"] | [18 empty] | start up | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/22/2023 | 12:00 AM
10/04/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-26549 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Advantex |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","Auxiliary Filter","Recirculation Pump","Control Operation","Level Sensor Operation","Distribution Pump Operation"] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | 12:00 AM
10/02/2023 | Alternative | RoutineScheduled Component Maintenance | 175-04-0857 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance | 182-18-0010 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | pumped | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
02/27/2023 |  | RoutineScheduled | 09-125-142 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/27/2023 | 12:00 AM
02/16/2023 | Alternative | RoutineScheduled | SD-14-246 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Inside of air filter housing was wet from rain earlier in the day. Metal mesh air filter was hard to clean as it was rusty. Recommend moving air filter assembly into the blower housing and replacing the air filter. Atu tank will probably need pumping by next year's inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
06/20/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | UV Bulb replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/14/2023 | Alternative | RoutineScheduled | 107-14-0044 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
05/10/2023 |  |  | SP-04-409 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
04/13/2023 |  | RoutineScheduled | 17-192-166 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/13/2023 | 12:00 AM
09/26/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | DeHaven's Backhoe Service Inc. | 1942001541 | Wayne | Edmonson | 2.000000 | 2500 | Advantex |  | Pump | Pressure | Drip | Not Applicable | 200.000000 | ["Attached Growth Medium","Auxiliary Filter"] | ["Attached Growth Medium","Auxiliary Filter"] | NA | [17 empty] | Cleansed textile sheets | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/01/2023 | 12:00 PM
07/06/2023 | Alternative | Initial Visit |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20RT |  | Pump | Gravity | Trenches |  |  | ["Control Operation"] | ["Control Operation"] | NA | [17 empty] | Initial start-up inspection. Programmed recirculation pump timers, standard and override times. Verified proper installation of equipment. Repositioned recirculation and discharge float switches per Orenco service memorandum. Set recirculation pump flow rate. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/17/2023 | 07:03 PM
01/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
07/25/2023 | Alternative |  | 08-195-219-DIS | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/25/2023 |  | 3.430000 |  |  | 2.200000 |  |  | Will be sent separately |  | BOD: 3.43 TSS: 2.20 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/25/2023 | 12:00 AM
02/28/2023 | Alternative |  | 18-142-0067 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | EZ Treat | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
07/26/2023 | Alternative |  | 07-195-132-DIS | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/26/2023 |  | 5.640000 |  |  | 2.600000 |  |  | Will be sent separately |  | BOD: 5.64 TSS: 2.60 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/26/2023 | 12:00 AM
03/08/2023 |  | RoutineScheduled | 04-120-0399A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Elite Onsite | 1942001726 | Drew | Saunders | 2.000000 | 1500 | 1000 | 500 | Pump | Gravity | Trenches | Not Applicable | 350.000000 | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/26/2023 | Jan 1 1900 2:40PM
01/23/2023 |  | Reportable Incident |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation"] | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced DF-60 compressor,(3) Rhombus control floats & 10 Dial A Flows in distribution box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 11:08 AM
01/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Was unable to open pods. Pile of brush over pods. Home owner is clearing and we will go out once pods are clear. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
11/01/2023 | Alternative | Follow-Up |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Hooked up the pressure switch, turned the UV back on, and flushed out the drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/01/2023 | Dec 30 1899 12:00PM
01/12/2023 | Alternative | Reportable Incident | 157-02-132 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the alarm and red light being on - installed an aerator rebuild kit. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the filter in the septic tank. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/12/2023 | 05:30 PM
01/13/2023 | Alternative | RoutineScheduled | 166-09-197 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1250 | Microfast |  | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation","BlowerCompressorAerator Operation"] | ["Distribution Pump Operation","BlowerCompressorAerator Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/07/2023 | 12:00 AM
04/10/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 12:00 AM
05/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance | 177-16-0226-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | ["Recirculation Pump" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
11/11/2023 | Alternative | RoutineScheduled | SD-03-331 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1500 | septic | Puraflo | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | YES | Musty | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/19/2023 | 08:50 AM
08/08/2023 | Alternative | Routine/Scheduled |  | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Delta Environmental Products, UC Series |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. LPP Field - no indications of surfacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | 08:30 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/01/2023 | Alternative | Pump-Out Only | 147-13-0056 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 3000 | EZ Treat Sandfilter | EZ Treat Sandfilter | Pump | Pressure | Pad | UV | 1500.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | NO | [16 empty] | Pumped Out | system flooded - toilet fixture or other leak in facility. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | Dec 30 1899 6:15AM
02/21/2023 |  | RoutineScheduled | 14-197-A4 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Fast |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/21/2023 | 12:00 AM
04/26/2023 | Alternative |  | 101-18-0213 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Mike | Ginsburg | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/23/2023 | Alternative | RoutineScheduled | 109-13-0339 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex AX20RT |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. Septic tank - First section - 15" of accumulated solids. Second section- 13" of accumulated solids. 18" of solids in recirculation portion of treatment unit. 2" of solids in discharge portion of treatment unit. Flushed treatment unit spray manifold. Removed and cleaned recirculation pump intake screen. Cleaned both drip manifold disk filters. Tested floats, pumps and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2024 | 07:03 PM
09/12/2023 | Alternative | RoutineScheduled | 128.13.0046 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | system check okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/30/2023 | Alternative | RoutineScheduled | 97-184-211 | Scott | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  | ["Disinfection","Other"] | [20 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
08/10/2023 | Alternative | Follow-Up Component Maintenance | 179-07-0199-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Whitewater ATU | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | New air pump installed. Repaired cracked plumbing in pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
03/02/2023 | Alternative | Routine/Scheduled | 136-02-0336 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | [18 empty] | Serviced Pura-Flo. Raked out the peat. Pump floats and alarms all good. Cleaned filter in the septic tank. Does not need to be pumped. The timer is set to 1.75 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/02/2023 | 03:30 PM
02/13/2023 | Alternative |  | SD-14-50 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan |  |  | Larry & Susan | Kennedy | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/24/2023 |  | Routine/Scheduled | 550-STS-6635 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [19 empty] | 01/24/2023 |  | 17.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 9:16AM
04/14/2023 |  | Routine/Scheduled | 133 10 0137 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 11:45 AM
10/18/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/30/2023 | 12:00 AM
04/28/2023 |  | RoutineScheduled | 2006-143-0255 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C & E Mechanical Corporation | 1942001339 | Louis | Timberlake | 1.000000 | 1250 | PremierTech |  | Pump | Pressure | Trenches | Not Applicable |  | ["Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Attached Growth Medium"] | ["Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Attached Growth Medium"] | NA | [6 empty] | Peatmoss will require replacement in approx 3 to 4 years | [9 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 02:45 PM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | 175-05-0974 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] |  | NO | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Effluent filter missing from septic tank. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | 12:58 PM
02/01/2023 |  |  | 02-120-0670A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | [9 empty] | [] | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Recirculation Pump"] | YES | Musty | Clear | 6.000000 |  | 6.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/01/2023 | Jan 1 1900 11:00AM
01/03/2023 | Alternative | Reportable Incident | 157-06-0072 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Control Operation","Level Sensor Operation","Recirculation Pump"] | [18 empty] | Conducted component upgrade - Replaced recirc pump, float sensors and controls | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/04/2023 | 09:15 AM
08/23/2023 | Alternative | Reportable Incident | 151-15-125 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the alarm light. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream. Installed an aerator rebuild kit. Changed the filter in the aerator. Replaced the UV light bulb and replaced the UV ballast. The timer is set to 2.5 minutes every 4 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/23/2023 | 01:30 PM
10/12/2023 | Alternative | Reportable Incident | 136-06-0001 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm Call: -Came out for an alarm call. Found bad pump causing system to be flooded. Replaced pump under warranty exchange. Customer paid 289 by check. Tested upon completion all components working as they should | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/27/2023 | 02:23 PM
07/19/2023 | Alternative | Routine/Scheduled | 550-STS-7046 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | Dec 30 1899 9:05AM
01/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
03/02/2023 |  |  | SP-04-341 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/06/2023 | Alternative | Routine/Scheduled | 166-11-019 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Basing - float sensors, pump and controls operating. Biofilter - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | 07:00 AM
01/26/2023 |  | Follow-Up | 179-10-0079-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Bionest | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Removed media. Treatment tank pumped out by Marshalls. Inspected and replaced diffusers. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
04/01/2023 |  | RoutineScheduled | 133 15 0124 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Pump | Pressure | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 10" of accumulated solids in septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. 0" of solids in recirculation portion of treatment unit. 0" of solids in discharge portion of treatment unit. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/16/2023 | 07:03 PM
09/18/2023 | Alternative | RoutineScheduled Component Maintenance | 033-STS-90511 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | The pump tank is leaking at the base of the riser. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
06/26/2023 | Alternative | Reportable Incident | 228-13-0311 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [17 empty] | Replaced float and pump | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/26/2023 | Dec 30 1899 9:00AM
07/19/2023 | Alternative | Reportable Incident | 800-08-0040 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/19/2023 | Dec 30 1899 9:00AM
08/10/2023 | Alternative | Routine/Scheduled | 550-STS-6440 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | Dec 30 1899 8:40AM
05/02/2023 |  | RoutineScheduled |  | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Disinfection"] | ["BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Sulphitic | Cloudy |  | 7.100000 |  |  |  | 05/02/2023 | Sample Chamber | 14.000000 |  | 1.000000 | 14.300000 |  |  | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
11/24/2023 | Alternative | RoutineScheduled | 15-192-042 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 16 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/24/2023 | 12:00 AM
05/31/2023 | Alternative | Follow-Up | 061-17-217 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Replaced failed blower alarm. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/29/2023 | Alternative | RoutineScheduled | SD-06-l83 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 62.500000 | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | Septic | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/16/2023 |  | RoutineScheduled | SWP-05-130 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Roots in cleanout by D-box, treated with RootX. Customer said if roots get bigger dig it next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
03/29/2023 |  | RoutineScheduled | 08-192-039 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Disinfection","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/29/2023 | 12:00 AM
03/20/2023 | Alternative | RoutineScheduled | SD-13-115 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Gravity | Gravity |  | UV |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Attached Growth Medium"] | NA | Musty | Clear |  | 11.410000 | 0.000000 |  |  | 03/20/2023 | Sample Chamber | 2.000000 |  | 1.000000 | 1.600000 |  |  | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
03/31/2023 |  | RoutineScheduled | 179-06-0256-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Control Operation"] | ["Level Sensor Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Control Operation"] | YES | Musty | Dark Brown | [13 empty] | Will be sent separately | Inspected | Routine inspection. Customer just got off medication everything in septic tank and pump tank looks dead (black water). Recommended to get pumped both tanks pumped out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
04/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/15/2023 |  | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | [28 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 01:36 PM
11/27/2023 | Alternative | RoutineScheduled Component Maintenance | 165-STS-335114 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | UV |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Effluent filter was clogged but able to clean Please keep discharge pipe clear | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
01/10/2023 |  | Routine/Scheduled | 06-142-0130 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Control Operation","Level Sensor Operation","Recirculation Pump"] | ["Control Operation","Level Sensor Operation","Recirculation Pump"] | NO | [17 empty] | The pump vault filter was checked. The Advantex manifold was flushed with the RSV pulled. Average overrides per day in past 30 days = 0.8. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | Jan 1 1900 12:44PM
04/11/2023 |  | RoutineScheduled | SWP-04-317 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment looks way better than last year. tank might need pump out next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
04/21/2023 |  |  | 11-163-0028 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Norweco | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 12:00 AM
11/06/2023 | Alternative | Routine/Scheduled |  | Surry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 600 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | Dec 30 1899 9:30AM
12/12/2023 | Alternative |  | 94-184-5003 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/12/2023 |  | 11.000000 |  |  | 5.200000 |  |  | Will be sent separately |  | BOD: 11.0 TSS: 5.20 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 12:00 AM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
01/31/2023 |  | Routine/Scheduled | 550-STS-6361 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/30/2023 | Jan 1 1900 2:45PM
07/03/2023 | Alternative | Routine/Scheduled | 228-18-0019 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/03/2023 | Dec 30 1899 9:25AM
04/10/2023 |  |  | 05-163-0188 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
04/21/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | 12:00 AM
10/07/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20 |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 4" of accumulated solids in septic tank. 4" of solids in discharge pump tank. Cleaned recirculation pump solids basket filter. Flushed treatment unit spray manifold. Cleaned treatment unit spray heads. Sprayed off treatment unit sheets. Tested floats, pumps and alarm. Excellent treatment. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 07:03 PM
07/06/2023 | Alternative | Routine/Scheduled | 147-09-0099 | James City | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 2500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 1000.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Alarm Service - Compressor is not operating - contacting BioMicrobics! Primary septic tank - pumped for storage. Aeration Tank - compressor and controls appear to have failed. Pump Tank - float sensors, pump and controls operating. DBox - Intact | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/10/2023 | Dec 30 1899 7:15AM
03/21/2023 |  | RoutineScheduled | 165-STS-333626 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/21/2023 | 12:00 AM
02/07/2023 |  | Routine/Scheduled | {FIPSCode}-STS-1358 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/07/2023 | Jan 1 1900 1:00PM
07/25/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | None | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/01/2023 | 12:00 AM
12/06/2023 | Alternative | Routine/Scheduled | 136-15-0219 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component Normal Level 12" of sludge and 6" of solids Inlet intact. No signs of infiltration Discharge/Pump Tank Condition of above Component Notes for above Component Above normal Level due to upstairs toilet running Used pump and timer and pumping system down. Pulled and cleaned pump and floats Pump and floats functioning properly however they are Aged Air Pump/Blower Condition of above Component Notes for above Component 120v Air pump pulling 1.3amps Pulled and cleaned filter Air pump is Aged but functioning properly Control Panel Condition of above Component Notes for above Component 120v All audible and visual alarms are functioning properly Pump is pulling 8.4amps Panel is aged. Distribution Box Condition of above Component Notes for above Component Above Normal Level Plastic distribution box in good condition all lines taking water Drain Field Condition of above Component Notes for above Component No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 10:18 AM
10/09/2023 | Alternative | Routine/Scheduled | 157-13-0146 | Mathews | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The UV is not working - needs a ballast, cord, and a bulb. The septic tank needs to be pumped out and when doing so pump the trash out of the Clearstream tank. The timer is set to 4 minutes every 2 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/09/2023 | 02:00 PM
05/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/09/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Delta Whitewater DF Series |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 8" of accumulated solids in septic tank. Cleaned blower air filter. Adequate aeration. 1" of solids in treatment unit. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/22/2024 | 07:03 PM
11/30/2023 | Alternative |  |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | 12:00 AM
12/28/2023 | Alternative | RoutineScheduled | 085-STS-31588 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/12/2024 | 12:00 AM
11/04/2023 | Alternative | RoutineScheduled | 109-14-0163 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20RT |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 14" of accumulated solids in septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. 12" of solids in recirculation portion of treatment unit. 6" of solids in discharge portion of treatment unit. Tested floats, pumps and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 07:03 PM
12/08/2023 | Alternative | Follow-Up | 09-197-A6 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination | [9 empty] | -1.000000 | [11 empty] | no tablet | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
08/02/2023 | Alternative | Initial Visit | 133-STS-96291 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an orange light on. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the filter in the aerator. Changed the diffuser in the Clearstream. Fixed the grade on the pipe in the Clearstream. Owner wants to raised the aerator - put on a stand. The timer is set to 4 minutes every 4 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | 12:15 PM
08/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium"] | ["Auxiliary Filter" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Air vent cap repaired | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
04/23/2023 | Alternative | RoutineScheduled | SD-11-01 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1000 | Multi-flo |  | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/26/2023 | 03:55 PM
09/01/2023 | Alternative | Routine/Scheduled | 041-STS-259676 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/01/2023 | Dec 30 1899 9:21AM
04/27/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Effluent Screens" ,"Disinfection"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | ATU needs pumping & UV unit repair. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | Jan 1 1900 12:48PM
08/11/2023 | Alternative | RoutineScheduled | 015-STS-333860 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
03/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-8"sludge 3"scum/ Microfast-6"sludge Pump Tank-0"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-178 ETM-11h 58m/ Pump2-170 ETM-11h 39m/ Peak-7/ High-64/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/17/2023 | Alternative |  | 124-STS-2379 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Blue Ridge | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/11/2023 |  | Routine/Scheduled | 17-172-0041A | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches | UV |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/11/2023 | Jan 1 1900 1:08PM
04/26/2023 |  | Routine/Scheduled | 06-142-0485 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1250 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [17 empty] | Air filter replaced. Scum layer in clarifying chamber stirred. Weir cleaned. System appears to be operating normally. Audible alarm not working and will need to be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | Jan 1 1900 9:06AM
11/27/2023 | Alternative | RoutineScheduled | C-03-111-0047 | Botetourt | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Level Sensor Operation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | [18 empty] | Replaced blower and float | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/27/2023 | 12:00 AM
06/12/2023 | Alternative | Follow-Up Component Maintenance | SWP-05-145 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to camera drainfield and check treatment. Treatment has improved. Header lines had bellies in them and was not allowing all lines to get equal flow. Adjusted speed dials to correct this. One header line had a crush in it but is still allowing proper flow. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
02/03/2023 |  | RoutineScheduled |  | Rockbridge | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Peat ponding | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/18/2023 | 04:10 AM
01/13/2023 |  | Routine/Scheduled | 550-STS-6437 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/13/2023 | Jan 1 1900 4:42PM
06/16/2023 | Alternative | Reportable Incident | 151-14-0076 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Repair - Installed new Clearstream control panel. Installed new diffuser - repaired compressor. Installed new float sensors, Installed new high head turbine pump Restored system to proper operation. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/22/2023 | 08:45 AM
01/16/2023 |  | RoutineScheduled | 179-13-0286-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | The area around the Advantex module is overgrown and there are roots growing into the Advantex module. We recommend removing the vegetation and maintaining the area in a mowed condition. We also recommend replacing the fabric sheets in the Advantex module. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
04/06/2023 |  | Initial Visit | 550-STS-6650 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 8.000000 |  | 1.000000 | [5 empty] | This report was submitted under the physical # 2400 it should've been # 2345 - it is now corrected to reflect that. Owner called due to red light on since Saturday - lost power. Serviced system. Need to pump and clean out the tanks due to them having paint in them. The grade on the pipe in the Clearstream is not okay - needs to be addressed. Replaced the diffuser in the Clearstream, replaced the filter in the aerator, and replaced the mesh screen in the spinfilter (full of paint). Fixed the UV. Re-wired the buzzer. The timer is set to 9 minutes every 1 hour. Took initial BOD and Fecal samples. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/06/2023 | Jan 1 1900 9:30AM
08/01/2023 | Alternative | RoutineScheduled | 171-13-0250 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | Sludge level-1" scum-14" sludge in Septic tank -Recirculation/ Discharge zone of tank 12" sludge, Clear Effluent on top, Cleaned Biofilter, Brushed and flushed manifold,pulled and cleaned RSV, sprayed off media, tested float switches, ran in test mode, Recirc Pump has ran 1225.7 hrs vs 1128.9 Hrs lastyear, about 100 hours and and 14,279 cycles which clocked over since 95,737 cycles (99,999 cycles over) in computer history about 20,000 cycles. Working good | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | 09:30 AM
08/29/2023 | Alternative | Reportable Incident | 193-STS-103749 | Westmoreland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | Attached Growth Medium | Attached Growth Medium | YES | [17 empty] | Replacement of Peatmoss based biofilter media with new BioCoir media. Replaced access risers on septic tank and pump tank. Reparged septic tank and pump tank. Replaced / upgraded spray distribution grid in treatment modules. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/06/2023 | 07:45 AM
01/27/2023 |  | Routine/Scheduled | 16-120-0010AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Processing Tank - recirc - recirc pump, media drapes & spray grid servcied. Processing Tank - discharge - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | Jan 1 1900 9:15AM
03/23/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
09/15/2023 | Alternative | RoutineScheduled | 11-125-010 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Pump | Pressure | Drip | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Septic Tank Baffles","Recirculation Pump","Level Sensor Operation","Effluent Screens","Distribution Pump Operation","Dispersal System Operation","Disinfection","Control Operation","BlowerCompressorAerator Operation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/15/2023 | 12:00 AM
11/29/2023 | Alternative | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/29/2024 | 02:36 PM
01/31/2023 | Alternative | Routine/Scheduled | 159-02-182 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex | PremierTech, EFX | Pump | Pressure | Pad | Not Applicable | 300.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/01/2023 | 12:15 PM
02/22/2023 |  | RoutineScheduled | 181-17-0146 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | AdvantexAX20RT | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The recirculating pump was pulled and cleaned. The textile sheets were sprayed. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | 08:50 AM
06/19/2023 | Alternative | RoutineScheduled | SD-11-391 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 45.000000 | ["Attached Growth Medium","SludgeScum Accumulation"] | ["Attached Growth Medium","Effluent Screens","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 04:55 PM
10/09/2023 | Alternative | RoutineScheduled Component Maintenance | 182-06-0394 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 10/09/2023 |  | 71.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance | 179-07-0350-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | YES | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
03/07/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Moving our annual inspections to between March and October. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | 12:00 AM
03/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
12/14/2023 | Alternative | Routine/Scheduled | 015-STS-338731 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | 09:00 AM
09/05/2023 | Alternative | RoutineScheduled Component Maintenance | 061-16-033 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Replaced one of the disc filter o-rings (closer to the house) that was leaking. Airline coming out of the blower had settled and the sch 80 union was leaking air (fitting was deformed). Replaced the pvc male adapter and union with a galvanized nipple and union, adjusted vertical pipe length to correct the settling. Blower is original and sounds okay, but amp draw is above the rated maximum. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
02/21/2023 |  | Follow-Up | 179-14-0301-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to disassemble components in recirc tank and assist pumper with proper pumpout. Reassembled components and Recirc tank was refilled back to proper levels with a water truck. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
07/31/2023 | Alternative | RoutineScheduled Component Maintenance | 179-16-0316-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EZ Treat Sandfilter | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend mowing the drainfield area and maintaining it in a mowed condition to prevent root intrusions into the drainfield lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
04/05/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 04/05/2023 |  | 37.000000 | [5 empty] | Will be sent separately | Inspected | air supply repaired Spongy spots in field recommend mow closer and have us come evaluate | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
10/09/2023 | Alternative | RoutineScheduled |  | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chickahominy | Hutchens Septic Services LLC | 1942001509 | Robert | Hutchens, Jr. | 2.000000 | 4000 | Microfast 4.5 |  | Pump | Pressure | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","Effluent Screens"] | YES | None | Clear |  | 7.000000 | 10.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | 12:00 AM
04/26/2023 |  |  | 04-197-A17 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 04/26/2023 |  | 10.300000 |  |  | 2.900000 |  |  | Will be sent separately |  | BOD: 10.3 TSS: 2.90 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | 12:00 AM
04/10/2023 |  |  | 09-163-0081 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex | [6 empty] | ["Control Operation","Attached Growth Medium","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
01/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
08/02/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20508 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [5 empty] | 08/02/2023 |  | 41.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
07/31/2023 | Alternative | RoutineScheduled | 166-09-331 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned atu and spin filter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/03/2023 |  | Follow-Up | 05-160-0071 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [18 empty] | - replaced tipping tray in the Ecoflo | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2023 | 12:00 AM
02/27/2023 |  |  | 18-142-0088 | Goochland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 1.000000 | 1000 | 1000 |  | Pump | Pressure | Drip | UV |  | [] | ["Control Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Level Sensor Operation"] |  | None | Discolored | 9.000000 |  | 6.000000 | [13 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/27/2023 | Jan 1 1900 11:30AM
10/07/2023 | Alternative | RoutineScheduled | 109-15-0012 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex AX20RT |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 14" of accumulated solids in septic tank. 0" of solids in recirculation portion of treatment unit. 6" of solids in discharge portion of treatment unit. Cleared roots from treatment unit that had gotten in under the lid. Cleaned septic tank solids filter. Cleaned recirculation pump intake screen. Adjusted timers slightly, to allow for more daily flow. Flushed treatment unit spray manifold. Removed floating solids from recirculation pump area. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/29/2023 | 07:03 PM
07/23/2023 | Alternative | RoutineScheduled | SD-08-072 | Orange | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 |  | ATU | Gravity | Pressure | Discharge | Chlorination |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | YES | Musty | Clear | 7.060000 |  |  |  |  | 07/23/2023 | Sample Chamber | 2.000000 |  |  | 1.100000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/02/2023 | 08:45 AM
05/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/09/2023 |  | RoutineScheduled | 01-197-416 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/09/2023 | 12:00 AM
12/13/2023 | Alternative | Routine/Scheduled | 127-STS-34822 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 10:00AM
06/29/2023 | Alternative | Reportable Incident | 18-118-0054 | Charles City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches |  | 300.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Alarm Event Response Trash Tank - sludge scum level high - recommend pumpout. Aeration Tank - replaced compressor with new HiBlow 60/80 - restored aeration operation / mixing. Restored alarm connections for compressor operation. Pump Tank - serviced pump, float sensors, and controls. System will need follow-up in one or two weeks to conduct full service and evaluate operation - FOIA Filed for permit documents. Extreme wet area noted downslope of where we believe absorption laterals are located. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/05/2023 | Dec 30 1899 7:45AM
10/26/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-03-519 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens" ,"SludgeScum Accumulation" ,"Disinfection" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | ["BlowerCompressorAerator Operation" ,"Disinfection" ,"SludgeScum Accumulation" ,"Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
03/07/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Ecoflo |  | Gravity | Pressure | Trenches |  |  | ["Septic Tank Baffles"] | ["Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | 12:00 AM
05/31/2023 | Alternative | RoutineScheduled | 107-98-0273 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 480.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/13/2023 | 02:30 PM
01/24/2023 |  | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 01/24/2023 |  | 49.000000 | [5 empty] | Will be sent separately | Inspected | Replaced effluent pump | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
02/22/2023 |  | Routine/Scheduled | 234-17-440 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | Jan 1 1900 1:20PM
11/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | zone valve repaired Effluent pump replaced replaced timer | This AOSS should now return to normal function after having provided the above state routine maintenance | 01/15/2024 | 10:39 AM
06/02/2023 | Alternative | RoutineScheduled | 133 06 0436 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Western Virginia Water Authority | 1942001145 | Michael | Doss |  |  |  |  | Gravity | Pressure | Drip | UV |  | ["None"] | ["None"] | NA | None | Clear | [5 empty] | 06/02/2023 | Sample Chamber |  | 0.000000 |  |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | 01:50 PM
04/04/2023 |  | RoutineScheduled | 07-113-163 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/04/2023 | 12:00 AM
04/19/2023 |  |  | 08-163-0159 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 2.000000 |  | Norweco Singulair |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/19/2023 | 12:00 AM
11/09/2023 | Alternative | RoutineScheduled Component Maintenance | 175-02-0229 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 10:33 AM
03/11/2023 |  | Routine/Scheduled | 036-STS-32806 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 1250 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/11/2023 | Jan 1 1900 10:30AM
07/25/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 | ["None"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | 12:00 AM
07/28/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Other"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Septic and advantex needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/06/2023 | 12:00 AM
05/11/2023 | Alternative | RoutineScheduled | 061-15-364 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Aquasafe ATU/ Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | NA | [17 empty] | Septic Tank-4"sludge 2"scum/ Aquasafe-4"sludge 12"scum/ Pump out of the Aquasafe required/ On & Off floats require replacement/ Counts: Pump-19962 ETM-2707h 32m/ No breakout or spongy areas on the drip field. Returned on 6/15/2023 for the pump out of the ATU and replaced on & off floats/ Controls, pump, floats and alarms now functioning properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
01/11/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
01/09/2023 |  | Routine/Scheduled | NYII-ATHKUK | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | Jan 1 1900 12:55PM
01/26/2023 |  | Routine/Scheduled | 550-STS-6409 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | Jan 1 1900 12:45PM
08/24/2023 | Alternative | Routine/Scheduled | 07-174-0050 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Ecoflo |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/24/2023 | Dec 30 1899 12:01PM
03/09/2023 |  | Routine/Scheduled | 05-142-0260 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/09/2023 | Jan 1 1900 4:34PM
12/19/2023 | Alternative | Routine/Scheduled | 093-07-0157 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Trash Tank Condition of above Component Notes for above Component Water level normal. Inlet tee appears to be intact. Not due for pump out. Recirculation Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats. Flushed and cleaned effluent screen. Recirculation pump has exceeded life expectancy. Recirculation pump plumbing has exceeded life expectancy. Recirculation floats have exceeded life expectancy. Riser lids are damaged. RSV (Recirculating Splitter Valve) Condition of above Component Notes for above Component Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly. RSV design is known for frequently clogging and causing alarm issues within other systems Discharge/Pump Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Discharge pump has exceeded life expectancy. Discharge pump plumbing has exceeded life expectancy. Discharge floats have exceeded life expectancy. Media Sheets Condition of above Component Notes for above Component Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Checked and confirmed spray height is good. Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Control panel has exceeded life expectancy. Distribution Box Condition of above Component Notes for above Component Water level normal. Structural integrity of distribution box appears to be intact. Drain Field Condition of above Component Notes for above Component Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/22/2023 | Dec 30 1899 8:25AM
04/24/2023 | Alternative | Initial Visit | 800-STS-14841 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer was set backwards - fixed. The inlet tee is backgrading - 12' from house less than 12" deep - needs to be address and/or fixed. Did not take sample. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/24/2023 | Dec 30 1899 3:45PM
08/01/2023 | Alternative | RoutineScheduled | 133-STS-100802 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/17/2023 | Alternative |  | 154-18-0291 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
01/17/2023 | Alternative | Routine/Scheduled | 103-STS-93150 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2600 | Clearstream |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 10.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/17/2023 | 06:53 PM
04/07/2023 |  | Reportable Incident | 177-15-0243-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to look at wet area between tanks and drainfield. All drip and flush rates were normal. Wet area is due to run off from neighboring properties. Replaced failed return ARV. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
02/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic-12"sludge 4"scum/ Microfast-10"sludge 0"scum/ Pump Tank-1"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower functioning properly/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-247 ETM-13h 12m/ Pump2-238 ETM-12h 31m/ Peak-13/ High-12 On-3m 26s/ Standard off-9h 56m/ Peak off-7h 56m/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/14/2023 | Alternative | RoutineScheduled | 109-06-0001 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 11500 | Biomicrobics Fast 3.0 |  | Pump | Pressure | Trenches | Not Applicable |  | ["Level Sensor Operation","Control Operation"] | ["Level Sensor Operation","Control Operation"] | NA | [16 empty] | Inspected | Replaced all 3 float switched and instaled a new pump timer and counter to see how often it runs. System was working normally afterwards confirmed by manager. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/30/2023 | 09:30 AM
07/24/2023 | Alternative | Routine/Scheduled | 550-STS-5881 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | Replaced aerator and UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | Dec 30 1899 5:00PM
07/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2500 | Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["Auxiliary Filter"] | NA | Musty | Clear | 6.000000 |  |  |  | Alkalinity 180, Temp 23c | [9 empty] | Inspected | Sludge/Scum Accumulation - Septic 5", Treatment 0", Pump Station 8" Pump Amperage - Discharge 10.8, Recirculation 12.6 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | 10:00 AM
01/18/2023 |  | RoutineScheduled | 001-STS-92393 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | AQUASAFE |  | Pump | Pressure | Pad | UV |  | [] | [] | [18 empty] | REPLACED COMPLETE UV LIGHT-EVERYTHING ELSE WORKING PROPERLY. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/21/2023 | 02:25 PM
10/16/2023 | Alternative |  | {FIPSCode}-STS-75886 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/08/2023 | Alternative | RoutineScheduled | SD-06-54 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Randy's Complete Water & Wastewater Services | 1942001335 | Randy | Gray | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable | 75.000000 | ["None"] | ["None"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | 01:25 PM
06/08/2023 | Alternative | Routine/Scheduled | 136-06-0143 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Renew Service Agreement - Long while since system was serviced. Primary septic tank - high level - clogged effluent screen - serviced. Aeration tank - high level - clogged weir - mixing present - compressor serviced. Pump tAnk - float sensors, pump and controls operating. DBox - plastic - intact - saplings growing in absorption field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:30 PM
09/28/2023 | Alternative | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | 01:51 PM
05/05/2023 | Alternative | Routine/Scheduled | 149-STS-10941 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 2.000000 | 1000 |  |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [16 empty] | Recommend a pump out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/05/2023 | Dec 30 1899 11:30AM
08/31/2023 | Alternative | RoutineScheduled | 151-11-0091 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | KC Forge Environmental Service, LLC | 1942001034 | Kent | Cuthbertson | 4.000000 | 45000 | 15000 | 15000 | Pump | Gravity | Trenches | UV | 19984.000000 | ["None"] | ["None"] | YES | [8 empty] | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/31/2023 | 03:00 PM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Norweco Singulair ATU | Norweco Singulair ATU | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/23/2023 | Alternative | RoutineScheduled | VAG401067 | Rockbridge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | Norweco |  | Gravity | Gravity | Discharge | Chlorination |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The rotating blower was pulled and cleaned. The effluent filter was pulled out and cleaned. The tablet feeders were pulled and inspected. They had the right amount of tablets in them. There were no visible leaks in the discharge line. There were no samples drawn because there were no discharge at the time of visit. The lids were secured. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/11/2023 | 08:45 PM
06/23/2023 | Alternative | Follow-Up | 175-14-0164 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Disinfection"] | ["Disinfection"] | [18 empty] | Service call only: Replaced faulty Salcor UV-Light with a Jet UV-Light. Tested and functioning properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Added media cleaner | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
05/15/2023 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 |  |  | Pump | Pressure | Trenches |  | 600.000000 | ["Effluent Screens","SludgeScum Accumulation"] | ["Effluent Screens","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/23/2023 | 11:37 AM
11/16/2023 | Alternative | RoutineScheduled | SD-09-309 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation","Distribution Pump Operation","Dispersal System Operation"] | [] | YES | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/04/2023 | 09:50 AM
07/12/2023 | Alternative | Routine/Scheduled | 06-172-0156AR | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/12/2023 | Dec 30 1899 11:29AM
07/17/2023 | Alternative | Routine/Scheduled | 234-17-444 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | Dec 30 1899 1:05PM
12/13/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 RT |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles","Attached Growth Medium","Recirculation Pump","Dispersal System Operation"] | ["Auxiliary Filter","Septic Tank Baffles","Attached Growth Medium","Recirculation Pump","Dispersal System Operation"] | [18 empty] | Recirc pump intake clogged with tampons. Recommend pumping to remove from tanks. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/13/2023 | 12:00 AM
02/14/2023 |  | RoutineScheduled | 13-100-0387 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 500 | AQUASAFE |  | Pump | Gravity | Trenches | UV | 300.000000 | [] | [] | [18 empty] | REPLACED BLOWER REBUILD KIT AND MUSHROOM VENT AND UV LIGHT UNIT | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/20/2023 | 09:50 AM
09/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | J&G Septic Service |  | James | Kleindl | 2.000000 | 4000 | Mirco fast .9 |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] |  | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | Dec 30 1899 7:40PM
09/13/2023 | Alternative | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Hott's Septic Service LLC | 1942001301 | Joshua | Hott | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
10/04/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20194 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | 180 Inspection and sampling | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
01/04/2023 |  | Initial Visit | VAG408283 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  |  | Discharge | Chlorination |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation"] | [17 empty] | Pumped Out | tank pumped out, line unclogged, blower replaced | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/10/2023 | 12:00 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance | 182-07-0034 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | new pump tank lid | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
12/19/2023 | Alternative | Routine/Scheduled | 041-STS-260992 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 750 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | Dec 30 1899 12:00PM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 10/15/1970 (LEGACY SEPTIC) | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Rejected | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"Attached Growth Medium" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Primary septic tank pumped due to plastics in tank | This AOSS should now return to normal function after having provided the above state routine maintenance | 11/22/2023 | 09:18 AM
09/12/2023 | Alternative | Routine/Scheduled | 199-03-0042 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | -Recirculation Tank: At normal level Pulled and cleaned pump, floats and filter Has about 7" of sludge -RSV: At normal level Has less than 1" of solids with about 2" of sludge Pulled and cleaned rsv -Pump Tank: At normal level Pump and floats working properly -Media Sheets: Brushed and flushed laterals Sprayed off sheets Sheets in good shape -Control Panel: Visual and audible alarms are working Recirc pump pulling 12.6amps Discharge pump pulling 11.2amps -Distribution Box: Concrete dbox just below grade At normal level, all lines taking water properly Removed minor grass roots coming through lid -Drain Field: Showing no signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | Dec 30 1899 12:47PM
08/03/2023 | Alternative |  | 18-100-0018 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/31/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-928 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Media showing its age but still ok. Peat level 4" below manifold may need replacement in the next 2 years. Small grass roots on wedge lid of septic tank but no water coming in. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:19 PM
04/01/2023 |  | RoutineScheduled | 067-STS-38685 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | Modified Extended Aeration |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [7 empty] | 03/22/2023 | Pump Chamber | 0.000000 |  |  | 1.200000 | 6.500000 |  | Will be sent separately |  | Total flow to drain fields March 2023 -118,730 gallons. Average 4,240 gallons per day. All aspects of the system are operational. Wasting of settled mixed liquor from the clarifier to the digester and decanting of supernatant from digester are occurring regularly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | 07:03 PM
01/05/2023 | Alternative | Routine/Scheduled | 157-04-091 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - plasit - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 07:45 AM
04/26/2023 | Alternative | Routine/Scheduled | S-175-16-0038 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | Dec 30 1899 3:53PM
08/31/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/01/2023 | 12:00 AM
02/21/2023 |  | Pump-Out Only | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 1.000000 |  |  |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/27/2023 | Jan 1 1900 11:30AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance | 182-17-0030 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 2.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Added media cleaner wipes | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
05/16/2023 | Alternative | RoutineScheduled | SD-05-137 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | 2 |  | Pump | Gravity | Trenches |  | 65.620000 | ["Effluent Screens","Attached Growth Medium"] | ["Effluent Screens","SludgeScum Accumulation","Attached Growth Medium"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 03:25 PM
05/12/2023 | Alternative | Routine/Scheduled | 093-10-0107 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | Replaced pump, pump relay, UV ballast & UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/12/2023 | Dec 30 1899 11:45AM
06/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/12/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Trenches |  |  | ["Septic Tank Baffles"] | ["Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/12/2023 | 12:00 AM
06/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/12/2023 | 02:06 PM
03/29/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, UC Series | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air line was repaired. System should resume functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 182-10-0016 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 10/10/2023 |  | 18.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
01/05/2023 | Alternative | Routine/Scheduled | 159-16-0103 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | EZ Treat Sandfilter |  | Pump | Gravity | Pad | UV | 450.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level Processing Tank - RSV, recirc pump serviced. Treatment Module - media & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 08:00 AM
08/15/2023 | Alternative | Reportable Incident Component Maintenance | SD-02-812 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Control Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | Chirping noise coming from the septic control panel. High level alarm float was intermittently partially closing and causing the low volume alarms. Replaced the blue Connery float with an Orenco float and the chirping stopped. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
10/30/2023 | Alternative | RoutineScheduled | 159-06-0358 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | system check okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/15/2023 | Alternative | Routine/Scheduled |  | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Biofilter - minor compaction - peatmoss in fair condition - raked / turned. Pump Basin - bulging noted - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | 07:00 AM
08/21/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [17 empty] | Cleaned effluent filter. Flushed manifold. Cleaned rsv. System appears to be operating normally. 2 average overrides per day. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | Dec 30 1899 10:49AM
09/20/2023 | Alternative | Follow-Up Component Maintenance | SD-04-210 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | Puraflo | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump tank has cracks and needs to be replaced. Added inlet riser on septic tank in order to waterproof and allow maintenance. Reattached junction box to riser. Septic tank and pump tank pumped out by other prior to peat replacement. Degraded peat was removed by hand with pitch forks and new peat was installed. Peat was purchased from Wrights Ready Mix, degraded peat was disposed at Spotsylvania Refuse. Replaced 7 spreader bars. Proposal to replace pump tank emailed to homeowner. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/02/2023 | 05:18 AM
05/30/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  | 600.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Distribution Pump Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/27/2023 | 02:01 PM
08/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced blower panel | This AOSS should now return to normal function after having provided the above state routine maintenance | 09/20/2023 | 01:07 PM
11/08/2023 | Alternative | RoutineScheduled Component Maintenance | 179-15-0106-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Attached Growth Medium"] | ["Distribution Pump Operation" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Attached Growth Medium"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
09/19/2023 | Alternative | Reportable Incident Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced 3 control floats. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
03/13/2023 |  | Follow-Up | 179-12-0098-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [7 empty] | 03/14/2023 |  | 29.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
08/23/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-99-149 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Annual inspection. Finally located the ARV for zone 2 by digging up the ends of the top couple runs of tubing and following them to the ARV valve box (under a fallen tree). Zone 2 drip rate was initially high at 5.6 gpm. Replaced the check valve on zone 1 and the drip rate dropped to 3.7 gpm. Both zones are overgrown with trees and weeds. Owner agreed to clear off everything but the mature trees this fall. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
01/05/2023 |  | RoutineScheduled | 175-15-0238 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Bio Barrier | none | Pump | Gravity | Mound | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/17/2023 | 01:27 PM
11/06/2023 | Alternative | RoutineScheduled | 109-STS-31876 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 3.000000 | 2500 | Aquasafe |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Other"] | NA | Musty | Clear | [14 empty] | Inspected | Sludge/Scum Accumulation - Septic Tank 8", ATU 12", Pump Station 0" Pump Amperage 9A. D-Box Re-Timed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | 03:00 PM
10/14/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 2.000000 | 4000 | EZ Treat Filter |  | Pump | Gravity | Trenches |  |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [17 empty] | Third Quarter 2023 inspection. Grease trap #1 - First section- 1" crust, 4" in bottom, Second section - 2" crust, 6" in bottom. Grease trap #2 - First section- 2" crust, 14" in bottom. Second section - 4" crust, 14" in bottom. Septic Tank- First section- 4" crust, 14" in bottom. Second section- skim crust, 16" bottom. Anoxic tank/Septic tank #2- first section -skim crust, 10" on bottom. Second section- skim crust, 10" on bottom. Recirculation Tank- First section- 0"crust, 0" on bottom. Second section- 0" crust, 0"" on bottom. EZ Treat Tank #1- 0" crust, 0" on bottom. EZ Treat Tank #2- 4" crust, 12" on bottom. Discharge pump tank- 0" crust, 0" on bottom. Cleaned septic tank filters. Cleaned 80% of spray nozzles. Grease traps recently pumped out. Replaced discharge pump tank middle float. Discharge pump was short cycling and would have damaged pump with out repair. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/10/2023 | 07:03 PM
06/21/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-88664 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"SludgeScum Accumulation"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Advantex sheets were scraped. Tanks & distribution box pumped by Marshall's Septic Tank Cleaning Service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
11/30/2023 | Alternative | Follow-Up | 199-STS-7018 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [20 empty] | 19.000000 |  | 1.000000 | [5 empty] | Took initial BOD and Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/30/2023 | Dec 30 1899 12:00PM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
09/12/2023 | Alternative | Pump-Out Only | 18-160-0132 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [17 empty] | Pumped Out | Pumped/cleaned septic tank; everything appears to be functioning at this time. This can in no way be construed as a guarantee that septic system will continue to function in the future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
04/25/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
08/28/2023 | Alternative | Initial Visit | 165-STS-337267 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  |  | Discharge | UV |  | ["Other"] | ["Other"] | [18 empty] | Start up | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/28/2023 | 12:00 AM
01/12/2023 | Alternative |  | 154-18-0193 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Aqua Safe | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
01/20/2023 |  | Reportable Incident | 179-STS-87780 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Homeowner called in stating system was in high level due to failed pump. We did not do any testing to verify. Homeowner purchased the pump for us and decided to install the pump himself. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
11/08/2023 | Alternative | RoutineScheduled | 14-197-A3 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | CLEARSTREAM |  | Pump | Pressure | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 8 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/08/2023 | 12:00 AM
03/29/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | DeHaven's Backhoe Service Inc. | 1942001541 | Wayne | Edmonson | 3.000000 | 2500 | Puraflo |  | Pump | Pressure | Drip | Not Applicable | 275.000000 | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/02/2023 | 12:00 AM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Uncovered distribution box due to what appeared to be nitrification around the box area. The box and surge box are functioning as designed. Recommend re-parging them to protect from future issues. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Lines were not receiving equal dose. Distribution box was uncovered and dial flows adjusted | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/13/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 12:00 AM
05/09/2023 |  | RoutineScheduled | 177-18-0367-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 2.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. HL 11, LL 2. "R" counts back to zero. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/10/2023 | 05:56 AM
09/09/2023 | Alternative | RoutineScheduled | 2110-06-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | 7.700000 |  |  | 1.800000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
02/28/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Puraflo |  |  | Gravity | Trenches |  |  | ["Septic Tank Baffles","Dispersal System Operation"] | ["Septic Tank Baffles","Dispersal System Operation"] | [18 empty] | adjust timers in dbox. CP door cracked bottom side | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/28/2023 | 12:00 AM
03/27/2023 |  | RoutineScheduled | 177-17-0018-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Inlet T in septic tank was completely clogged up with wipes and hard grease, unclogged T and spoke to customer about pumping tank out. Customer called pumper and schedule for this Friday. HL 9, LL 16. Blower 2.88 amps. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
09/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Lab sample normal Please keep drainfield mowed and maintained | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
01/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Cleaned air pre-filter as a matter of preventative maintenance. Very minor root penetration observed at access manway seal. Does not appear to be allowing infiltration. Will continue to monitor. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
06/10/2023 |  |  |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 1.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 12:00 AM
10/14/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | BioMicrobics MicroFast |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 24" of accumulated solids in septic tank. 12" of solids in MicroFast treatment unit. Cleaned blower filter. 1" of solids in discharge pump tank. Adequate aeration. Excellent treatment quality. The blower control panel is alarming due to a defective amperage sensor. The small rheostat has failed. The blower is operating fine. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/17/2023 | 07:03 PM
01/10/2023 |  | Routine/Scheduled | C 800-17-0109 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service - due for lab sampling. Trash Tank - normal level - recommend pumpout. Aeration tank - mixing present - compressor serviced - recommend pumpout. UV system - bulb and housing serviced. PUmp tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/11/2023 | Jan 1 1900 12:00PM
02/15/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 2.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
04/03/2023 |  | Initial Visit |  | Newport News | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Sandfilter, High rate |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Visit Primary septic tank - normal level - recommend pumpout. Flow Equal / SF Dosing Tank - float sensors, pump and controls operating - require original permit documents to determine if dosing is correct. Sand Filter - appears to be high rate - sand is "mud" and has serious ponding issues - Slow drain, but functioning. Require original permit documents to determine type of sand to use for replacement. Pump Tank - float sensors, pump and controls operating. LPP Field - located, no surfacing present - did not exercise valving. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | Jan 1 1900 6:45AM
06/22/2023 | Alternative | RoutineScheduled | 043180134 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 1.000000 |  | Septic | Norweco | Gravity | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | NA | [17 empty] | 3.5' of liquid depth, 12" of sludge zero scum. 30 min setting. System looks really good and clean. Drainfield is dry. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | 03:30 PM
04/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
04/27/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
11/10/2023 | Alternative | Routine/Scheduled |  | Sussex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/10/2023 | Dec 30 1899 12:34PM
11/27/2023 | Alternative | RoutineScheduled Component Maintenance | 2105-11-153 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity |  | UV |  | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Disinfection"] | ["Control Operation" ,"Level Sensor Operation"] | NA | Musty | Clear | 6.800000 | 1.800000 | [11 empty] | Will be sent separately | Inspected | UV Bulb needs replacing. ATU blower needs replacing. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 12/06/2023 | 09:34 AM
01/12/2023 | Alternative | Routine/Scheduled | 159-12-050 | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Cajun Aire ATU |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - normal level aeration Tank - normal level - compressor failed - requires replacing. DBox - intact 01/16/2023 - Compressor replaced. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/17/2023 | 07:30 AM
05/01/2023 |  | Routine/Scheduled | 03-172-0364A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level Processing tank - RSV, recirc pump and effluent screen serviced. Treatment Module - media drapes and spray grid serviced. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | Jan 1 1900 7:15AM
11/14/2023 | Alternative | RoutineScheduled |  | Clarke | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | McKim Septic and pumping | 1942001330 | Michelle | McKim | 2.000000 | 750 |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Other"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | An alternative septic system inspection for a sale. When we arrived, we found that the house breaker for the septic system was off. We turned the breaker back on so that we could inspect the septic system. The exterior septic control panel is a time dose. There are three 4" pvc clean outs from the house to the septic tank that we ran a camera snake thru to look at the sewer line. We found that the sewer line is bellied outside the septic tank which is causing the inlet pipe to be angled up wards. The concrete septic tank has plastic risers on both inlet and outlet sides of the tank and a filter that the manufacture recommends be cleaned every 6 months. The septic tank was sludge judged and does not need pumped out at this time. The conveyance line between the septic tank and the pump tank is bellied which has caused the outlet pipe in the septic tank to be angled up. That means that the effluent level in the septic has to get higher than normal to allow the effluent to get out. The concrete pump tank, plastic risers and lids, electric box, float tree and floats, force main and pump were inspected. The inlet pipe is angled up and the pipe was not cut like it should have been it extends past the inlet riser about 3 feet and the float tree is broken. The E-Z Treat green square pod lid is broken. The plastic monster box is at ground level and the speed levelers will need to be replaced the effluent is leaking around them. The concrete 10 port d-box is also at ground level. When opened found the d-box was cracked and not holding effluent. The drain field was probed and dry. At time of inspection this septic system is not in working condition. This inspection does not guarantee the life of any component. | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/15/2023 | 11:00 PM
03/29/2023 |  | RoutineScheduled | 177-STS-90483 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | 90-Day Inspection. When the pump runs, the ground gets damp, but more grass cover is needed in the dispersal area. A follow-up visit is planned for the summer. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/07/2023 |  | RoutineScheduled | 179-08-0005-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Pump tank needs to be pumped out due to sludge levels. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
12/27/2023 | Alternative | RoutineScheduled | 06-192-022 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 8 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/27/2023 | 12:00 AM
05/02/2023 | Alternative | RoutineScheduled | 171-15-0232 | Pittsylvania | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Pittsylvania-Danville | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Auxiliary Filter","Control Operation","Other"] | ["Auxiliary Filter","Control Operation","Other"] | [18 empty] | System needed on sprayed nozzle cleaned was done at time of inspection | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/23/2023 | 01:45 PM
02/09/2023 | Alternative | Reportable Incident | 115-STS-94661 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Delta Environmental Products, UC Series |  | Pump | Pressure | Trenches | UV | 450.000000 | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Repair / Maintenance Relocated blower and assembly to higher elevation Replaced Salcor UV system (no longer in business) with new Orenco UV system. Added 6" extensions to riser access. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/13/2023 | 07:30 AM
06/09/2023 | Alternative | RoutineScheduled | 2016-143-0208 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Replaced blower and installed blower housing. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
04/27/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/18/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/21/2023 | 03:35 PM
07/18/2023 | Alternative | RoutineScheduled | 154-13-0068 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | 12:00 AM
06/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump chamber concrete lid was replaced. Recommend pumping ATU and possibly the pump chamber as there is some scum. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/28/2023 | Alternative | RoutineScheduled | 107-10-0021 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Cloudy | 7.270000 |  |  |  |  | 11/28/2023 |  | 54.000000 |  |  | 42.400000 |  |  |  |  | Cleaned filters and will return to resample. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/13/2023 | 11:30 AM
05/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend moving the newer tree that is in close proximity to the drainfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/09/2023 | Alternative | RoutineScheduled | 163-STS-335166 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | AdvantexAX20RT | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The textile sheets were sprayed off. The recirculating and discharge pumps were both pulled and sprayed off. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | 01:25 PM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/01/2023 |  |  | 177-06-0287-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
01/09/2023 |  | Initial Visit | 121-STS-12465 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Southwest Soils, Inc. | 1942001494 | Stephen D. | Dalton | 1.000000 | 1000 | AS 600 | None | Gravity | Gravity | Trenches | UV | 600.000000 | [] | ["Other"] | NA | Musty | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 03:00 PM
03/29/2023 | Alternative | Follow-Up | 093-STS-14533 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [20 empty] | 4.000000 |  | 1.000000 | [5 empty] | Took initial BOD and Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | Dec 30 1899 12:00PM
06/26/2023 | Alternative | Routine/Scheduled | 154-18-0379 | Louisa | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Blue Ridge | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/26/2023 | 01:11 PM
10/17/2023 | Alternative | Routine/Scheduled | 800-08-0419 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Puraflo |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | [15 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | Dec 30 1899 3:00PM
04/26/2023 |  | Routine/Scheduled |  | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | ["Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Per real estate inspection notes / report. Pumped processing tank empty - 3 compartments - cleaned / serviced all compartments. Replaced failed pump and float sensors in pump tank. Refilled with fresh water for restart. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/27/2023 | 07:15 AM
09/15/2023 | Alternative | Initial Visit Component Maintenance | 177-STS-92436 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
04/04/2023 |  | Routine/Scheduled | 11-142-0297 | Hanover | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1500 | Multiflo ATU |  | Pump | Pressure | Drip | Not Applicable | 350.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation"] | N/A | [7 empty] | 04/04/2023 | Pump Chamber | 28.000000 | [5 empty] | Will be sent separately |  | System needs to be pumped out and refilled. System should be resampled after pumping out and refilling treatment tank | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/05/2023 | Jan 1 1900 11:19AM
02/10/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2023 | Dec 30 1899 3:45PM
04/06/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Dispersal System Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Dispersal System Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Pressure gauge replaced and solution added to media Zone valve to be replaced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
03/10/2023 |  | RoutineScheduled | 033-STS-91614 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/03/2023 |  | RoutineScheduled |  | Cumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 2.000000 | 2000 | Septic | Clearstream | Pump | Pressure | Mound | Not Applicable | 350.000000 | ["SludgeScum Accumulation","Distribution Pump Operation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | Jan 1 1900 10:30AM
12/19/2023 | Alternative | Reportable Incident | 150-04-050 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | [] | [] | [18 empty] | Replaced pump | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/05/2023 | Alternative | Routine/Scheduled | 149-STS-10940 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [16 empty] | Recommend pump out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/05/2023 | Dec 30 1899 11:00AM
02/28/2023 |  | RoutineScheduled | 177-STS-88728 | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Disinfection" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | The EZ Treat UV bulb is no longer working and should be replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/03/2023 | 08:19 AM
10/27/2023 | Alternative |  | VAG408422 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 1.000000 |  | FAST |  | Gravity | Gravity | Discharge | Not Applicable |  | [] | ["BlowerCompressorAerator Operation"] | NA | None | [16 empty] | Not Discharging at time of inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/12/2023 | 10:00 AM
03/13/2023 | Alternative | RoutineScheduled | 154-08-0384 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | MicroFast |  | Gravity | Pressure | Drip | Not Applicable | 450.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/19/2023 | 12:00 AM
12/12/2023 | Alternative | RoutineScheduled Component Maintenance | 061-STS-24383 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Owner stated that the installer did come back and work on the various discrepancies. Vericomm electronic log showed last alarm as occurring on 7/16/23. Fairly significant rain 2 days ago. No signs of infiltration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
04/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Some of the lines are slightly wet in the gravel. No surfacing effluent. Recommend checking back in a few months. Advised homeowner to monitor water usage and notify us if there is any change in the field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/21/2023 | Alternative | RoutineScheduled | 159-00-285 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001302 | Charles | Langford | 2.000000 | 1000 |  |  | Pump | Pressure |  |  |  | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/25/2023 | 12:00 AM
04/12/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/23/2023 | Alternative | RoutineScheduled | 07-113-073 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","SludgeScum Accumulation","Dispersal System Operation","Control Operation"] | NA | Musty | Clear | [15 empty] | 4 Blue Crystal tablets added 8 Bio Max tablets added | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/23/2023 | 12:00 AM
04/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Gravity | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
10/03/2023 | Alternative | Routine/Scheduled | 136-09-0242 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level Has 1" of solids with 10" of sludge Pulled and cleaned filter Riser is about 4" below grade and has no baseplate -Discharge/Pump Tank: At normal level Riser is leaking Conduit and plumbing coming through riser are not sealed properly. Floats are aged Plumbing is aged and leaking -Aeration: At normal level Has about 30" of settled suspended solids Alarm float has no wire running to it Pulled and cleaned weir and defuser Defuser was very clogged and causing the air pump to get hot -Air Pump/Blower: Working properly Pulled and cleaned filter -Control Panel: Working properly Discharge pump pulling 10amps Air pump pulling 1.49amps -Drain Field: Unable to locate, somewhere in the woods Pumped Septic 10/05/23 and refilled to appropriate level Repairs 10/05/23: -Installed 6"-12" riser -installed 3 new floats -installed a float tree assembly -did conduit and wiring -installed a diffuser -Tested all components upon completion and everything is working as it should | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 01:48 PM
10/26/2023 | Alternative | Reportable Incident Component Maintenance | SD-05-268 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Complaint inspection. Blower fail alarm, blower alarm was going off for 2 reasons. Reason number 1 clogged septic filter, water level was higher than normal putting back pressure on blower. Reason number 2 there was a clogged fitting on pressure switch line. Cleaned septic filter and water level went back to normal, recommend to clean Septic filter more often. Replaced clear tubing for pressure switch and unclogged fitting, tested pressure switch and everything was working good after that. Blower 1.06 amps. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
06/13/2023 | Alternative | Routine/Scheduled | 085-STS-34715 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | UV | 450.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | 180 day system inspection / service. Primary septic tank - normal level - effluent screen serviced. Processing Tank - recirc - recirc pump, media drapes & spray grid serviced. U.V. - bulb and housing serviced. Processing Tank - discharge - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | Dec 30 1899 9:15AM
07/05/2023 | Alternative | Pump-Out Only |  | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 2.000000 | 5000 | [7 empty] | [] | [] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | 12:00 AM
05/05/2023 | Alternative | Routine/Scheduled | 149-STS-10371 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/05/2023 | Dec 30 1899 10:30AM
05/30/2023 | Alternative | RoutineScheduled Component Maintenance | 175-18-0235 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Control Operation" ,"Disinfection" ,"Auxiliary Filter" ,"Level Sensor Operation" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Disinfection" ,"Auxiliary Filter" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Completed annual inspection and replaced uv lamp as maintenance. Septic tank needs pumped. Owner to make arrangements. Effluent is starting to turn a little cloudly. If the pump-out doesn't correct that, media may require a chemical cleaning next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Clearstream | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | System appears to be functioning as designed at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
11/19/2023 | Alternative | RoutineScheduled Component Maintenance | 165-STS-335680 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | " | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
06/14/2023 | Alternative | Routine/Scheduled | 800-STS-13809 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | Dec 30 1899 12:46PM
10/04/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | Western Virginia Water Authority | 1942001145 | Michael | Doss |  |  |  |  | Gravity | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | NA | None | Clear | [5 empty] | 10/04/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | 06:55 AM
06/13/2023 | Alternative | RoutineScheduled Component Maintenance | 177-06-0365-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
03/15/2023 | Alternative | RoutineScheduled | 159-10-0016 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | [null] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
03/29/2023 |  |  | 2018-143-0130 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Aquaklear | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/12/2023 | 12:00 AM
12/13/2023 | Alternative | RoutineScheduled Component Maintenance | 175-06-0071 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Owner stated he would be calling local pumper to set up pumping out the tank. Gast blower running at 2.09 amps, sounds ok. Lenses for indicator lights are rather faded, recommend replace. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
08/18/2023 | Alternative | Routine/Scheduled | 157-09-0144 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the filter in the septic. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the aerator motor (new serial # 22050116). Installed a new alarm assembly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/18/2023 | 12:00 PM
11/13/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | Replaced aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | Dec 30 1899 1:55PM
02/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | advantex needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
09/25/2023 | Alternative | RoutineScheduled | 04-183-280 | Russell | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | [] | NA | [17 empty] | No power on system. Sewer line cut into | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/25/2023 | 12:00 AM
12/08/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/08/2023 | Dec 30 1899 8:55AM
06/02/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty |  | 7.390000 | 7.290000 |  |  |  | 06/02/2023 |  | 6.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/15/2023 | 09:00 AM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
07/24/2023 | Alternative |  | 033-08-0149-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
09/25/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | Dec 30 1899 2:10PM
10/19/2023 | Alternative | RoutineScheduled Component Maintenance | 033-07-0340-SR | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
04/21/2023 | Alternative | RoutineScheduled | 154-13-0195 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
02/02/2023 |  | Routine/Scheduled | 234-17-342 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | Jan 1 1900 9:01AM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Sample box is cracked. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/15/2023 | Dec 30 1899 2:02PM
08/01/2023 | Alternative | Initial Visit |  | Middlesex | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit - ALARM EVENT Primary septic tank - normal level - effluent screen serviced. Aeration Tank - normal level - NO MIXING - compressor failure - has "aftermarket" compressor - need to install proper compressor, wiring and controls. Pump Tank - float sensors, pump and controls operating. DBox - Plastic - intact - all laterals accepting effluent. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/02/2023 | 07:30 AM
08/22/2023 | Alternative | Pump-Out Only |  | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Distribution Pump Operation | ["Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NO | [16 empty] | Pumped Out | Discharge pump failure - float failure. Pump tank pumped empty for repair and replacement of pump and float sensors. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/28/2023 | 06:30 AM
05/15/2023 |  | RoutineScheduled | 2086-04-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Attached Growth Medium","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.800000 |  |  | 2.100000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/18/2023 | 12:00 AM
10/04/2023 | Alternative | Routine/Scheduled | 036-STS-31931 | Charles City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Pressure | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/04/2023 | Dec 30 1899 3:13PM
12/06/2023 | Alternative |  | 128.12.053 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Laneview Environmental, LLC | 1942001775 | James | Boone | 2.000000 |  |  |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/18/2023 | Alternative | Reportable Incident | 136-07-0177 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Customer started yesterday Found panel in alarm. Audible alarm wouldn't silence Opened pump tank and found at normal level Alarm float was faulty, on/off float was Aged. Noted there was root intrusion around forcemain and under riser. Also noted the alarm box was Aged Presented solutions to customer and she approved to replace alarm float only. Replaced alarm float on site and tested and confirmed all components are functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | 02:12 PM
05/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
10/10/2023 | Alternative | RoutineScheduled | 2005-143-0225 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Ecoflo |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Control Operation","Level Sensor Operation","Auxiliary Filter","Distribution Pump Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/10/2023 | 12:00 AM
08/30/2023 | Alternative | Routine/Scheduled | 800-STS-13179 | Suffolk | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/30/2023 | Dec 30 1899 1:15PM
11/15/2023 | Alternative | Routine/Scheduled | 085-STS-33679 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1060 | Orenco Advantex |  | Pump | Pressure | Drip | UV |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [17 empty] | Effluent filter cleaned, manifold flushed, uv bulb changed, disc filter cleaned, drip field flushed. Pressure reset to 20 psi. Risers were sealed. System appears to be operating normally. Effluent Filter was clogged. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/15/2023 | Dec 30 1899 11:17AM
07/03/2023 | Alternative | Reportable Incident | 18-118-0054 | Charles City | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 300.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Supervised pump out of trash tank. Compressor operating properly. Pending receipt of FOIA Documents for continued evaluation. Still unknown if wet area downslope of absorption laterals is related to a failure or a possible spring has surfaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/05/2023 | Dec 30 1899 12:00PM
04/24/2023 | Alternative | Initial Visit | 800-STS-13765 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm - muted it - red light on. Serviced system. Checked the pump, panel, and floats (ok). Changed the filter in the aerator. The aerator should be raised - full of ants. The Clearstream tank needs to be pumped and cleaned and the septic tank needs to be pumped out. The timer is set to 2 minutes every 2 hours. Did not take samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/24/2023 | Dec 30 1899 2:00PM
04/13/2023 |  | Reportable Incident |  | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | ["Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | COSS - Maintenance - GMP2018-02 Installed access risers on septic tank Installed cannister style effluent screen in septic tank. Replaced dilapidated DBox with new 8 port concrete DBox. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 09:15 AM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/18/2023 |  | Routine/Scheduled | {FIPSCode}-STS-3708 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | Replaced UV unit | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | Jan 1 1900 10:00AM
11/07/2023 | Alternative | RoutineScheduled | 109-14-0066 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | AdvantexAX20RT | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The recirculating and discharge pumps were both pulled and sprayed off. The textile sheets were sprayed off. The lateral pipe was flushed. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/27/2023 | 10:00 PM
05/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/12/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Pressure | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Septic Tank minimal scum, 8" sludge,(pumped prior to sale last year) Treatment unit recirc zone 6-7" sludge layer- Discharge basin trace sludge. good aeration, cleaned, flushed and brushed sprayer manifold, RSV and biofilter. Discharge pump running non sto on arrival and alarm continued to sound after running in test mode. Returned to repair burned up wire nuts and got float and alarm to function correctly after follow up visit. Ran in test mode. Discovered the internet monitoring was unplugged from a switch isndie the home at time of sale and new owner is replacing it for continued monitoring. Float alert issue began 3-14-23 based on computer history- now corrected. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
01/03/2023 |  | Routine/Scheduled | 234-17-198 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [13 empty] | The UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/03/2023 | Jan 1 1900 3:00PM
12/15/2023 | Alternative | RoutineScheduled | 05-118-0018 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/18/2023 | Alternative | Pump-Out Only | 147-13-0056 | James City | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 3000 | EZ Treat Sandfilter | EZ Treat Sandfilter | Pump | Gravity | Pad | UV | 1000.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Pump out only - system has not had routine service due to no contract in place ! | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/30/2023 | Dec 30 1899 12:00PM
04/07/2023 |  | Reportable Incident | 157-14-0085 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | We received a call about an alarm - could not get it to mute. Serviced system. Checked the pump and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. Replaced the UV light bulb and replaced the mute button on the control panel. The timer is set to 5 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/07/2023 | 09:30 AM
03/15/2023 |  | Routine/Scheduled | 550-STS-6314 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | Jan 1 1900 1:46PM
03/15/2023 |  | RoutineScheduled | 03-100-0615 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Pete | Duer | 1.000000 | 1250 | Septic Tank | Ecoflo Peat Biofilter | Gravity | Pressure | Pad | Not Applicable | 600.000000 | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/16/2023 | 01:00 PM
09/06/2023 | Alternative | RoutineScheduled Component Maintenance | 175-14-0372 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
07/12/2023 | Alternative | RoutineScheduled Component Maintenance | 099-STS-89723 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Dispersal System Operation" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for routine inspection. Peat had some ponding. Augered peat moss. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
07/07/2023 | Alternative | RoutineScheduled | 150-07-0218 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 3.000000 | 2900 gallons | septic tank | Delta Whitewater | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Level Sensor Operation","Control Operation","Distribution Pump Operation","BlowerCompressorAerator Operation"] | YES | Musty | Clear |  |  | 40.000000 | [12 empty] | Septic tank 6" fog, 4" sludge. Delta Whitewater 40% S. Cleaned effluent filter. Pump, alarm, floats, controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/23/2023 | 06:35 PM
10/13/2023 | Alternative | Routine/Scheduled | 2009-143-0063 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Outlet tee appears to be intact. Not due for pump out -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed water sensors are functioning properly. -Aeration: Water level normal. Checked and confirmed it's receiving aeration -Air Pump/Blower: Checked and confirmed aerator is functioning properly. Flushed and cleaned aerator air intake filter. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Distribution Box: Did not excavate. Trailer parked in dispersal area was blocking access to it -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 08:06 AM
12/19/2023 | Alternative | Routine/Scheduled | 17-142-0419 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Type of System Alternative Type of AOSS System Norweco ATU to Netafim Drip Dispersal Trash Tank Condition of above Component Notes for above Component Water level normal. Inlet tee appears to be intact. Outlet tee appears to be intact. Not due for pump out. Discharge/Pump Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Aeration Condition of above Component Notes for above Component Water level normal. Flushed and cleaned effluent screen assembly. Not due for pump out. Air Pump/Blower Condition of above Component Notes for above Component Checked and confirmed aerator is functioning properly. Cleaned aerator shaft Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Drip Field Condition of above Component Notes for above Component Flushed and cleaned disk filter. Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/22/2023 | Dec 30 1899 8:31AM
02/23/2023 |  | RoutineScheduled | 099-17-0068 SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump" ,"Control Operation"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The conduit has pulled out of the control panel and insects are getting into the control panel. We recommend repairing & reconnecting the conduit. We also recommend resealing the conduit where it reconnects to the pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
05/10/2023 |  | RoutineScheduled | 182-10-0140 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  |  | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Dispersal System Operation","BlowerCompressorAerator Operation","Auxiliary Filter"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 12:00 AM
09/22/2023 | Alternative | RoutineScheduled | 17-142-0278 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/05/2023 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Pressure | Drip |  | 300.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | 10:23 AM
07/26/2023 | Alternative | Reportable Incident | {FIPSCode}-STS-3973 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | [18 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/26/2023 | Dec 30 1899 7:30AM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance | SR 03- | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
02/23/2023 |  | Routine/Scheduled | 234-15-166 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | Replaced UV bulb and ballast. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/23/2023 | Jan 1 1900 8:50AM
03/31/2023 | Alternative | RoutineScheduled | 154-07-0230 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | 12:00 AM
07/13/2023 | Alternative | Pump-Out Only | 166-14-059 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Pump out of biomicrobics FAST as recommended during last service visit. System refilled with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 06:45 AM
02/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | Dec 30 1899 2:21PM
03/02/2023 |  | Routine/Scheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] | N/A | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/07/2023 | 09:48 AM
10/13/2023 | Alternative | RoutineScheduled Component Maintenance | 177-18-0398-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
03/06/2023 | Alternative | Reportable Incident | {FIPSCode}-STS-81758 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | COSS - Maintenance - GMP2018-02 Replaced Dbox with new 8 port concrete DBox. Spliced to existing conveyance line. Spliced to existing header lines. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/07/2023 | 08:45 AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/30/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-21317 | Clarke | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Rejected | EHD - Lord Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Gravity | Pressure | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | NA | [17 empty] | Septic tank plastic riser has a crack in it that ground water is getting into. Camlock is leaking on the force main. Force main at valve box is leaking | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/01/2023 | 07:45 AM
12/19/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-87577 | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001236 | Stuart | Lynn | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Attached Growth Medium" ,"Disinfection" ,"Control Operation" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Control Operation" ,"Disinfection" ,"Recirculation Pump"] | NA | Musty | Cloudy | [5 empty] | 12/27/2023 | Pump Chamber | 89.000000 |  | 122.000000 | 23.000000 | 61.000000 |  | Will be sent separately | Inspected | 10-3-23 Lot 1 pump alarm, ARV stuck, cleared WWTP Routine service Flows Last 7 Days: High 8463 gal. Low : 6249 gal. AVG 7237 gal. 10-31-23 WWTP Routine service Flows Last 7 Days: High 7,025 gal. Low : 5324 gal. AVG 6,219 gal. walked over drainfield, grass needs mowed, some small trees cleared on edges, no issues 11-3-23 Email from Tommy Thompson possible wet area 1/2 way down on left side, please check 11-7-23 WWTP Routine service Flows Last 7 Days: High 9,068 gal. Low : 6,511 gal. AVG 7,3747 gal. Investigated wet area, reduced flow to zone 1 to dry and see if reason for Tommy's email 11-15-23 Alarm?: Yes - 3. Filters 'Pressure Differential', 'Flow Catastrophic' - Zone 2, and 'Flow Variance' - Zone 2. re set corrected. Reduced flow zone 4, turned zone 1 back on High flow last 7 days 8960 gal. Low : 7300 gal. AVG: 8000 gal. 11-28-23 Tommy emailed VDH visiting site 11-29-23 12-5-23 Return Valve on drip skid leaking, Recirc pump 2 not working in Auto 12-14-23 All UV Sleeves are clean. Replaced two bulbs and one sleeve. Still need to clean UV Bulbs Chamber. 12-18-23 Routine service Peak Flow Last 7 days: 9293 gal. Low Flow Last 7 Days : 7345 gal. AVG Flow Last 7 Days : 8184.9 gal. High BOD & TN likely due to recirculation pump on unit 2 EZ treat not working just prior to sample, replace pump re sample | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 01/16/2024 | 01:58 PM
02/08/2023 |  | Reportable Incident | 179-13-0363-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Control Operation"] | ["Recirculation Pump" ,"Control Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | High level alarm for recirc tank started 3 days ago. Recirc pump was not running. Cut and stripped wires for pump connection to power (in Orenco splice box) and replaced the original wire nuts. Put Vericomm panel in test mode and observed several pump cycles with normal amp draw of 11.56 amps. No other problems detected. Alarm condition should clear within 24 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
04/24/2023 |  | RoutineScheduled | 133 15 0113 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20-RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | Sludge level-3" scum layer on top-8" sludge on bottom in Septic tank zone - Recir zone 6" sludge - Pump tank - light Trace sludge, Pulled out and Cleaned RecircSplitterValve, Biofilter, and Brushed and flushed spray Manifold and sprayed off media. Float switches tested good, alarm test good. Alarm float on discharge did not reposnd and will return to repair soon.- RTU132756 Recirc pump run time 1008.2 hours and 29413 cycles and discharge pump has 132.0 hours run time and 11241 cycles, some alerts in May june july august, Alarms in history on 7/9/22,6/26/22 and 5/30/22 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
03/16/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic / Ecopod ATU Treatment Tank | Pump Tank | Pump | Pressure | Mound | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-6"sludge 0"scum/ Ecopod-3"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working properly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-24816 ETM-3211h/ High-32/ Watermeter-0026038 On-7m 56s Off-11h 52m/ No breakout or spongy areas at the drip mound areas. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/24/2023 |  | RoutineScheduled | 133 06 0619 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Superior septic service | 1942001081 | Nathan | Crews | 3.000000 | 1000 | 1500 |  | Pump | Gravity | Trenches | Not Applicable | 250.000000 | ["Effluent Screens","Attached Growth Medium"] | ["Attached Growth Medium","Effluent Screens"] | YES | None | Black | [15 empty] | System should be pumped out as soon as weather permits | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/25/2023 | 12:00 PM
09/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and pumping | 1942001330 | Michelle | McKim | 2.000000 | 1250 |  |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 4:40PM
01/24/2023 |  | RoutineScheduled | 101-07-0082 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/28/2023 | 12:00 AM
10/18/2023 | Alternative | RoutineScheduled | 06-118-0021 | Charles City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Advantex AX20 |  | Pump |  |  |  |  | [] | ["Attached Growth Medium","Recirculation Pump","Control Operation","Distribution Pump Operation","Level Sensor Operation"] |  | Musty | Cloudy | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/18/2023 | 12:00 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/10/2023 | 11:17 AM
07/13/2023 | Alternative | Routine/Scheduled | 01-172-0468A | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/13/2023 | Dec 30 1899 4:45PM
07/10/2023 | Alternative | Routine/Scheduled | 800-12-0100 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | Dec 30 1899 11:30AM
01/09/2023 |  | RoutineScheduled | 165-STS-333329 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Dispersal System Operation"] | ["Effluent Screens","Dispersal System Operation"] | YES | Musty | Clear | [15 empty] | repaired leak in dripline | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/09/2023 | 12:00 AM
08/16/2023 | Alternative | Routine/Scheduled | 06-160-0080 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable | 58.000000 | SludgeScum Accumulation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/16/2023 | 01:15 PM
08/08/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 500 | Delta, DF Series |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 14" of accumulated solids in septic tank with a 2" solids crust. 22" of solids in treatment unit, no solids crust. Good aeration. Cleaned blower filter. Tested alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/24/2023 | 07:03 PM
11/01/2023 | Alternative | Initial Visit |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to a light on. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream and cleaned the UV light bulb. Changed the filter in the aerator and changed the mesh screen in the spinfilter. Re-plumbed the air lines in the Clearstream tank. Meet with the pumping company and pumped and cleaned the pump tank and pumped the scum out of the Clearstream tank. The buttons were backwards for the mute button. The timer is set to 4 minutes 15 seconds every 2 hours. Did not take initial samples. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/01/2023 | Dec 30 1899 11:30AM
07/19/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | routine annual | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | 12:00 AM
12/04/2023 | Alternative | Routine/Scheduled | 136-07-0169 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level Has no solids with 2ft of sludge Top riser section is damaged but customer has patched it. There is dirt falling through the concrete Inlet lid and has created a hole. -Discharge/Pump Tank: At normal level Pump and floats working properly Riser has dirt and some root intrusion and the cords are not in conduit. -Aeration: At normal level Has 1" of sludge Pulled and cleaned defuser and wier Riser is leaking Alarm float aged but working -Air Pump/Blower: Working properly Pulled and cleaned Air pump -Control Panel: Panel is aged but working properly Discharge pump pulling 6.88amps -Distribution Box: Plastic dbox at grade At normal level All three seals have dirt coming through them -Drain Field: Showing no signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 09:30 AM
03/16/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
11/06/2023 | Alternative | RoutineScheduled | 154-03-0877 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 3.000000 | 3000 | Puraflow |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Auxiliary Filter","Effluent Screens","Other"] | YES | Musty | Clear | [14 empty] | Inspected | Sludge Scum Accumulation - Septic Tank 16", Pump Recirculation Tank 6", Pump Tank 0" Pump Amperage 9A Peat Media looks freshly replaced Light Drip around the air relief valves | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | 09:00 AM
03/30/2023 |  | Routine/Scheduled | {FIPSCode}-STS-3329 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | Jan 1 1900 12:30PM
03/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
10/23/2023 | Alternative | Routine/Scheduled | 166-04-431 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal level 10 in of sludge 1 in of solids Pulled and cleaned filter Riser showing signs of leaking -Discharge/Pump Tank: Normal level Less than 1 in of suspended solids Tested floats and pump all working as should All plumbing intact and pump moving water properly Riser is showing signs of leaking -Aeration: Normal level 10 in of suspended solids Pulled and cleaned weir Air line not serviceable Float does not work Riser showing signs of leaking -Air Pump/Blower: 120 volts coming in Pulled and cleaned filter Air pressure sensor intact and properly working Dog box intact -Control Panel: 120 volts coming in All visual and audible alarms functioning properly Discharge pump pulled 10.2 amps Air pump pulled 1.1 amps All components properly working -Distribution Box: Customer did not want us to dig up at this time -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 02:23 PM
06/02/2023 | Alternative | RoutineScheduled | 154-16-0014 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Norweco 960 |  | Pump | Pressure | Mound | Not Applicable | 150.000000 | [] | [] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | 11:30 AM
07/15/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | YES | Septic | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/27/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Advatex | Pump | Pressure | Drip | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","Recirculation Pump"] | [18 empty] | 36" liquid depth, Average of 6" of sludge and very little sludge in the inlet side of septic tank, 2" average of sludge in the outlet side. some loose sludge in Advantex tank. Alarms, pump, floats are operational. Field looks good with no leaks, Flushed the spin filter, adjusted pressure. There was no return. Discharge pump cycles 6267, run time 302 47m Recirculation pump cycles 98419, run time 1174h 25m | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/27/2023 | 03:15 PM
03/13/2023 | Alternative | Routine/Scheduled | 800-06-0399 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex | Orenco Advantex | Gravity | Gravity | Trenches | Not Applicable | 750.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service - residence not occupied. Septic tank - normal level. Processing tank - RSV, recirc pump & effluent screen serviced. Effluent screen 100% clogged, causing low level alarm events. Treatment Modules (2) - media drapes & spray grids serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | Dec 30 1899 7:15AM
06/06/2023 |  | Initial Visit |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex AX20RT |  | Pump | Gravity | Trenches |  |  | ["Control Operation"] | ["Control Operation"] | NA | [17 empty] | Initial start-up visit. Set recirculation pump timers. Set recirculation pump flow rate. Tested floats, pumps and alarm. Verified correct installation and wiring. The septic tank needs risers and lids installed, there is only the inspection port available. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 07:03 PM
04/19/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
09/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Ponding in Puraflo Modules and all 4 modules need peat replacement | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 09/20/2023 | 01:07 PM
03/27/2023 |  | Routine/Scheduled | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | Jan 1 1900 9:00AM
12/05/2023 | Alternative | Reportable Incident | 179-13-0013 | Richmond | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | replaced compressor, system check okay | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
12/11/2023 | Alternative | RoutineScheduled | 179-STS-91626 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 13642.000000 | [] | [] |  |  |  | 7.130000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/12/2024 | 07:03 PM
11/06/2023 | Alternative |  |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | Western Virginia Water Authority | 1942001145 | Michael | Doss | [9 empty] | ["None"] | ["None"] | YES | None | Clear | [5 empty] | 11/06/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/02/2024 | 01:35 PM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Hydro-Action ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/08/2023 | Alternative | RoutineScheduled | 108-03-0088 (LEGACY ALT. SYSTEM) | Bath | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | 12:00 AM
10/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Removed roots from septic tank Recommend media replacement | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance | VAG408343 | Rockingham | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Pad | Chlorination |  | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Control Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | ET Bed has heavy roots and tree stumps needs repaired Floats not operating properly | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/11/2023 | 11:17 AM
02/22/2023 | Alternative | Pump-Out Only | 159-12-104 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 4000 | Clearstream | Clearstream | Pump | Gravity | Trenches | Not Applicable | 2000.000000 |  | ["Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Pumped septic tank for "The Chinese Restaurant" empty as recommended during previous service visit - Replaced damaged effluent screen. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/23/2023 | 08:30 AM
06/03/2023 | Alternative | Routine/Scheduled | 041-STS-260811 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/03/2023 | Dec 30 1899 11:00AM
02/24/2023 |  | Initial Visit | 182-09-0064 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | Drip field overgrown | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/24/2023 | 12:00 AM
01/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
08/02/2023 | Alternative | RoutineScheduled | 132-06-0116 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1500 | Advantex |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 | ["Effluent Screens"] | ["Attached Growth Medium","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | 10:00 AM
06/08/2023 | Alternative | Reportable Incident Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Responded to call for conduit and wiring damaged by a post hole digger. Control power breaker was tripped off, and wiring was ripped from connections. Removed wiring and repaired conduit. Replaced 13 strands of wire and connected into control panel and junction box at tank. Replaced damaged J channel cover. Did a 5 minute drawdown to verify pump operation, then powered up the blower. Noted 3 spots of heavier aeration which have the potential of deteriorating to single point aeration in the future. Cleaned the air pre-filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 06:43 AM
02/01/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Found area's in D/F that are soft. 2/1/2023 (snow on the ground) | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/14/2023 | Jan 1 1900 8:41AM
09/26/2023 | Alternative | Routine/Scheduled | 18-118-0001 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1060 | Orenco Advantex |  | Pump | Gravity | Trenches | UV | 150.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [17 empty] | Uv bulb changed. Manifold flushed. Effluent Filter cleaned. System averaged 5.8 overrides per day. Recirc off time changed to 23 minutes. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/26/2023 | Dec 30 1899 11:01AM
11/10/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 11/10/2023 | Dec 30 1899 12:40PM
04/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/11/2023 | Alternative | RoutineScheduled Component Maintenance | 175-18-0295 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
02/24/2023 |  | Reportable Incident |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Lord Fairfax | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The high level alarm light was on, but the alarm buzzer was not operating. There was an indication that the pump was running but there was no amp draw and the water level was high. The blower housing was flooded and the blower inoperable. The spin filter disc was clogged. Removed the water from the blower and housing. Removed the soaked air filter and allowed the blower to run independent of the system to dry out. Replaced the filter element for the blower canister filter. After cooling down, the pump started and ran, dropping the water level about 3.5" in 20 minutes. Pump was stopped to allow the Krain distribution valve to rotate to the next zone. Pump would not restart. High level alarm had cleared, but water level still high. Advised owner to check water level in the morning. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
03/22/2023 |  | RoutineScheduled | 16-183-005 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Pump | Pressure | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Auxiliary Filter","Control Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Auxiliary Filter","Control Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/22/2023 | 12:00 AM
01/06/2023 |  | Routine/Scheduled | 234-17-0075 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/06/2023 | Jan 1 1900 7:25AM
08/10/2023 | Alternative |  | 003-STS-31580 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Karen & Michael | Nelson | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/12/2023 |  |  | 2004-143-0275 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Ecoflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
11/08/2023 | Alternative | Routine/Scheduled | 127-STS-34653 | Goochland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 2.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/08/2023 | Dec 30 1899 3:42PM
06/27/2023 | Alternative | RoutineScheduled | 179-STS-91626 | Stafford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 9356.000000 | [] | [] |  |  |  | 7.320000 | 1.730000 |  |  |  | 06/29/2023 |  | 38.000000 |  |  | 14.200000 | 34.220000 |  |  |  | BOD is over the regulatory limit. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/13/2023 | 02:00 PM
03/28/2023 | Alternative |  | 109-STS-30758 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Daniel | Slovis | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-8"sludge 3"scum/ Microfast-6"sludge/ Pump Tank-0"sludge/ No pump out needed at this time/ Blower air filter cleaned and working properly/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-416 ETM-32h 59m/ Pump2-400 ETM-31h 38m/ Peak-6/ High level-8/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/12/2023 | Alternative | Reportable Incident |  | Petersburg | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Crater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Replacement of plumbing to include flow inducer - the plumbing was snapped off at the flow inducer | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/04/2023 | Dec 30 1899 2:08PM
01/03/2023 |  | RoutineScheduled | 177-19-0036-SR | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Pump | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | 12:00 AM
01/23/2023 |  | Reportable Incident | 196-07-098 | Westmoreland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 300.000000 | Control Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Alarm Event - Found contactor failed for discharge pump and high level alarm float not functioning (No Audible Alarm) - replaced high level float sensor and replaced contactor. Have system pumped on following day. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/24/2023 | 07:30 AM
10/11/2023 | Alternative | Routine/Scheduled | 136-16-0310 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Normal level 5 in of sludge less than 1 in of solids No signs of infiltration -Recirculation Tank: Normal level Less than 1 in of suspended solids Pulled floats and tested pump all working as should Pulled and cleaned pump Pulled and cleaned filter Pump moving water properly plumbing and filter housing intact No signs of infiltration -RSV: Pulled cleaned and flushed till clear Intact and working as should -Discharge/Pump Tank: Normal level 4 in of suspended solids Pulled floats and tested pump all working as should Plumbing intact and pump moving water properly No signs of infiltration -Media Sheets: Flushed and brushed laterals Cleaned and sprayed media sheets clean Flushed module until water ran clear Media sheets are bridging No safety support on media module lid -Control Panel: 120 volts coming in All visual and audible alarms functioning properly Recirculation pump pulled 11.9 amps Discharge pump pulled 7.3 amps -Distribution Box: 3 lines all intact and taking water properly Speed balancers intact and functioning as should Pulled minor roots from sidewall of box otherwise nothing major -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 03:33 PM
01/17/2023 |  | RoutineScheduled | 177-STS-91823 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The control panel for the blower does not have a functioning alarm. Replacement is recommended. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
02/23/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | BioMicrobics -Fast |  | Pump | Pressure | Trenches |  |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [16 empty] | Inspected | Septic Tank 1"scum, 8" Sludge trace In Front Fast Septic, Fast Side port 16" Sludge trace, Pump Tank 8-10" light sludge trace. Recently pumped. Owner installed New blower last Fall- running good, Cleaned air filter. Tested the pump and checked all sprinklers- good spray. Owner recentrly cleared a clogged sprinkler. Condition of control box is rusty but fully operational. Timed to run at midnightt 2 am and 4 am for 13 minutes per time as needed. Owner replaces chlorine tablets monthly as needed-. Pump cycle count 4976 vs 4671 last year - Pump time 460hours vs 436hours 27 min - peak 117 - High - 65 - Both floats tested operational - control boxes are aged and corroded but still functioning- Pumped last year, will need pumping this next year, maybe arrange prior to next years inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/24/2023 | 09:30 PM
05/30/2023 | Alternative | Routine/Scheduled | 166-04-461 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. LPP valving exercised. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 01:15 PM
04/07/2023 | Alternative | RoutineScheduled | SD-13-221 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Blower had gotten very noisy and was headed to eventual bearing failure. Replaced at owners request. Also replaced the first 2" pvc elbow as it had gotten deformed from settling and replaced the power supply wires from the Microfast panel as they had insulation damage. Media is clogged which has greatly reduced treatment and caused the effluent level to be 2" to 3" higher than normal (which works the blower harder). Media will need to be cleaned and the tank pumped out per Biomicrobics directions. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
03/16/2023 |  | RoutineScheduled | 179-12-0317-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Septic tank had heavy wipes and signs of fabric softner use. Recommended pumping out septic tank homeowner will make arrangements. Distribution boxhad new growth roots in 3 header lines not allowing equal follow. Removed roots and added root-x monitor next year. Spinners in Rt unit were clogged from the use of fabric softner. Cleaned spinners and pump intake. Recirc pump is struggling but in working order at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
06/15/2023 | Alternative | RoutineScheduled | 150-06-0373 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 2.000000 | 1900 gallons | septic tank | Delta Whitewater | Gravity | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation","BlowerCompressorAerator Operation","Effluent Screens"] | ["SludgeScum Accumulation","Effluent Screens","BlowerCompressorAerator Operation"] | YES | Musty | Clear |  |  | 40.000000 | [12 empty] | Septic tank 0" fog, 3" sludge. Delta Whitewater 40% SS. Cleaned effluent filter. Serviced aerator. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/23/2023 | 07:15 PM
10/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 4.000000 |  | Septic Tank to Pump Tank to Drainfield | Septic Tank to Pump Tank to Puraflo Modules to Field. | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank #1-4"sludge 0" scum/Pump Tank #1-0"sludge/ Septic Tank #2-3"sludge/ Pump Tank #2 (To Puraflo Modules) -0"sludge/ No pump out needed at this time/ Puraflo Peat was turned and in good condition at this time/ Counts: Pump (Tank#1) Pump1-070622 ETM-0044057/ Pump2-070103 ETM-0034774/ Pump (Tank #2) Pump1-844 ETM-8h 10m/ Pump2-785 ETM-7h 40m/ No breakout or spongy areas on the drainfields. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/31/2023 | Alternative | RoutineScheduled | 07-100-0433 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1250 | ECOFLO |  | Pump | Gravity | Pad |  | 600.000000 | [] | [] | YES | [17 empty] | EVERYTHING WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/01/2023 | 10:00 AM
04/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/19/2023 | Alternative | Routine/Scheduled | 166-10-149 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/19/2023 | 05:46 PM
10/17/2023 | Alternative | RoutineScheduled Component Maintenance | 061-16-250 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"SludgeScum Accumulation"] | ["Control Operation"] | NA | Musty | Clear | 7.650000 |  |  |  |  | 10/17/2023 | Pump Chamber | 4.000000 |  |  | 3.000000 | 21.120000 |  | Will be sent separately | Inspected | Completed biweekly inspection and routine influent/efflent sampling. Influent, collected in primary septic tank: BOD = 102mg/L, TSS = 46; TKN = 4.49; Nitrite-Nitrate (N-N) = 31.7; D.O. = .3; pH = 7.31; temp = 19.8* C. Effluent sampling, collected in drip tank: BOD = 4 mg/L; TSS = 3; TKN = 3.82; N-N = 17.3; D.O. = 5.8; pH = 7.65; temp = 19.7* C, and settleable solids = nothing visible. Recommended pumping out the primary septic tank. Drip tank high level count at 52, low level count at 499. In the past 13 days, system has pumped an average of 1732.1 gals/day at 285.0 gals/cycle (avg.) for a total of 22,518 gallons. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
04/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/08/2023 |  | RoutineScheduled | 179-STS-91736 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [5 empty] | 02/08/2023 |  | 12.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Settlement around tanks and on drain field lines, Spoke to installer about it. Gave customer a Copy of Do's and Dont's. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
08/10/2023 | Alternative | RoutineScheduled Component Maintenance | SD-11-312 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Recirculation Pump" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | None | Clear | [5 empty] | 08/10/2023 | Pump Chamber | 12.000000 | [5 empty] | Will be sent separately | Inspected | Annual inspection and maintenance completed. The effluent sample collected for a 5-year BOD test only missed the mark by 2 mg/L. Considering appearance of effluent in recent years, this is very good. All soggy areas on mounds and in between are gone, undoubtedly aided by a long period of well-treated effluent. This has allowed more consistent grass-cutting. Briars and tall weeds recently cut back to the ends and edges of the mounds - this will also help in keeping the mounds firm. Recirc override float had failed (off), replaced it. Pressure gauge in headworks for return line is stuck at zero, needs replaced. On arrival, three out of four air release valves were being held open by standing water in the drip manifolds. This standing water is interfering with the operation of the check valves, and encourages a regrowth/slime in the drip manifolds. The manifolds need to be raised an inch or two above the tubing to allow any remaining water to drain out and to allow for proper venting. Without proper venting, the highest emitters will act as vents and likely suck in sand fines during that process. Both zone check valves were replaced 10/13/20. At that time, it was suspected that the drip rates were very low. Three weeks later when the flow meter was added, it was confirmed: zone 1 tested at 1.5 gpm and zone 2 tested at only .8 gpm. This is almost certainly due to improper venting and clogged emitters. Today's higher rates are due to simultaneous dosing of both zones (bad ck valves). Recommend raising the drip manifolds and check valves to allow for proper venting, bleach flushing the piping and tubing, and putting in true union ball/spring check valves to allow for inspection and cleaning (current swing check valves are 2 feet in the ground). Drip tubing may need to be replaced if the drip rates don't return to close to start-up rates. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
03/23/2023 |  | Routine/Scheduled | 03-142-0460 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Pumpout of processing tank as recommended last service visit. Pump out conducted by Commonwealth Waste Solutions, supervised by Millers staff. Processing tank refilled with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | Jan 1 1900 7:00AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/29/2023 | Alternative | Routine/Scheduled | 234-17-311 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/29/2023 | Dec 30 1899 3:44PM
12/13/2023 | Alternative | RoutineScheduled Component Maintenance | 177-13-0163-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
10/20/2023 | Alternative | Routine/Scheduled | 128-05-204 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Inlet tee had excessive Fats/ Oil/ Grease build up. Flushed and cleaned effluent screen. No riser access for effluent screen. Effluent screen is obsolete and discontinued -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. Noted minor deformity within the tank but structural integrity is intact -Peat Moss: Peat moss has failed. Structural integrity of tank appears to be intact. Structural integrity of tipping bucket appears to be intact. Checked and confirmed tipping bucket is functioning properly. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 01:52 PM
08/21/2023 | Alternative | RoutineScheduled Component Maintenance | 179-08-0017-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for routine inspection. Tanks were pumped prior to site visit. Intstalled inlet riser on septic tank, sealed outlet risers on septic tank and pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
10/12/2023 | Alternative | RoutineScheduled | SD-06-77 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 65.000000 | ["Effluent Screens"] | ["Effluent Screens","Dispersal System Operation"] | YES | Sulphitic | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 07:40 AM
11/14/2023 | Alternative | Initial Visit | 085-STS-34528 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 81.000000 |  | 37.000000 | [5 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. Took initial BOD and Fecal samples. NOTE - BOD sample high - system should function properly after service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | Dec 30 1899 1:20PM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/16/2023 | Alternative | Routine/Scheduled | 12-174-0011 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Puraflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/16/2023 | Dec 30 1899 3:29PM
03/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1500 | Septic | pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/17/2023 |  | RoutineScheduled | 087-STS-6230 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 2.000000 |  | Norweco Singulair |  | Gravity | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/17/2023 | 12:00 AM
06/22/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-12"sludge 2"scum/ Microfast-10"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ May need a pump out of the Septic-Microfast Tank next year/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump1-4591 ETM-33h 21m/ Pump2-568 ETM-23h 10m On-3m 16s Off-9h 57m/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/17/2023 |  | Reportable Incident | 179-13-0153-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | High level alarm in the recirc tank, effluent level up into the risers. Pumped level down enough to see a steady flow of water from the house. Owners' son found one toilet upstairs running due to stuck flapper, and one in basement that was out of adjustment (water level even with top of overflow tube). Checked operation of septic control panel and found a discrepancy between it and the tablet used to connect to it. Control panel led's were lit for all 3 floats, and voltage on terminal strip confirmed that floats were floating and electrically closed. The tablet, however, indicated that the middle float was stuck down (off). Reloaded Vericomm run program per Orenco tech support request. Also cycled power for panel, then put panel in test mode. Issue did not resolve. Will check back next week and connect with a different tablet to see if issue is still present. May need a new motherboard. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
06/29/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/05/2023 | Alternative |  | 101-11-0383 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Robert & Jessica | Knight | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/29/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/28/2023 | 12:00 AM
03/16/2023 |  | Routine/Scheduled | {FIPSCode}-STS-2720 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/16/2023 | Jan 1 1900 8:00AM
04/16/2023 | Alternative | Routine/Scheduled | 149-STS-10454 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/16/2023 | Dec 30 1899 9:00AM
04/27/2023 | Alternative | Initial Visit | S-14-111-0015 | Botetourt | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | BioMicrobics MicroFast |  | Gravity | Gravity | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation","Other"] | ["BlowerCompressorAerator Operation","Other"] | NA | [17 empty] | Initial inspection visit. Replaced blower. Delivered chlorine and dechlor tablets. Instructed homeowner on how to replenish the tablets as needed. 12" of accumulated solids in septic tank. 20" of solids in the treatment unit. Good aeration after the blower was installed. Tested alarm. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/10/2023 | Jan 1 1900 7:03PM
12/13/2023 | Alternative | Routine/Scheduled | 127-STS-35085 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 600 |  |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 12:00PM
03/06/2023 |  | RoutineScheduled | 00-197-173 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Clearstream |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/06/2023 | 12:00 AM
05/18/2023 |  | Routine/Scheduled | 550-STS-6670 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/18/2023 | Jan 1 1900 11:45AM
01/18/2023 |  | Routine/Scheduled | 234-08 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [14 empty] | Replaced diffuser | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | Jan 1 1900 11:47AM
12/03/2023 | Alternative | Routine/Scheduled | 093-13-0058 | Isle Of Wight | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Control Panel: Control panel is not receiving power from local power source | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/13/2023 | Dec 30 1899 9:12AM
03/28/2023 |  | Routine/Scheduled | 234-08 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | Jan 1 1900 8:10AM
01/06/2023 |  | RoutineScheduled | 04-163-0070 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Parsley Septic Tank , Inc. | 1942001106 | James | Parsley | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/20/2023 | 12:00 AM
02/27/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | keep area maintained | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/30/2023 | Alternative | RoutineScheduled | 147-STS-22699 | Prince Edward | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Pura System |  | Pump | Pressure | Mound | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","SludgeScum Accumulation","Recirculation Pump","Level Sensor Operation"] | NA | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | Dec 30 1899 2:15PM
10/20/2023 | Alternative | Follow-Up Component Maintenance | 179-18-0350-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired break at end of top line in upper zone. Checked gal/min after repair completed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
10/12/2023 | Alternative | RoutineScheduled Component Maintenance | 179-12-0187-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend pumping the septic/ATU tank and pump tank due to sludge accumulation in the tanks. Our staff should be present to remove the components to assist the pumper. Please contact our office when you would like for us to coordinate this for you. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
05/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/28/2023 |  | Reportable Incident | 182-00-0381 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | NA | Pungent | Clear | [15 empty] | replaced and moved flooded blower. Replaced control box | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/08/2023 | 12:00 AM
08/23/2023 | Alternative | RoutineScheduled Component Maintenance | VAG408262 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Blower replaced | This AOSS should now return to normal function after having provided the above state routine maintenance | 09/20/2023 | 01:07 PM
02/27/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:22 PM
08/15/2023 | Alternative | RoutineScheduled | 136-06 0128 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001302 | Charles | Langford | 2.000000 | 1000 |  |  | Pump | Pressure |  |  |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/25/2023 | 12:00 AM
08/18/2023 | Alternative | RoutineScheduled Component Maintenance | SP-04-860 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
03/28/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | pumped 1 & 2 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
10/20/2023 | Alternative | RoutineScheduled | 12-113-109 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/20/2023 | 12:00 AM
02/20/2023 |  | RoutineScheduled | 153-STS-20160 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Recirculating Sand Filter |  | Siphon | Gravity | Discharge | Chlorination | 250.000000 | ["Disinfection","Dispersal System Operation"] | ["Disinfection","Dispersal System Operation"] | NA | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/23/2023 | 12:00 AM
08/03/2023 | Alternative | RoutineScheduled Component Maintenance | {FIPSCode}-STS-17159 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Clarity of treated effluent in d-box was excellent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
04/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Gravity | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
10/06/2023 | Alternative | RoutineScheduled | 07-197-A2 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.000000 | 7.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/12/2023 | Alternative | Routine/Scheduled | 800-05-0108 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Flushed and cleaned effluent screen. Not due for pump out -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. -Aeration: Water level normal. Diffuser air line is damaged. Flushed and cleaned weir. Flushed and cleaned diffuser. Checked and confirmed high level alarm float is functioning properly -Air Pump/Blower: Checked and confirmed aerator is functioning properly. Flushed and cleaned aerator air intake filter. -Control Panel: Checked and confirmed components within control panels are functioning properly. Checked and confirmed audible alarms are functioning properly. Checked and confirmed visual alarms are functioning properly. -Drain Field: Found no signs of surfacing on dispersal field. Repairs (10/18): -Replaced damaged diffuser air line and diffuser. Checked and confirmed that it was aerating properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/27/2023 | Dec 30 1899 2:31PM
09/15/2023 | Alternative | RoutineScheduled | 15-125-020 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/15/2023 | 12:00 AM
04/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Strongly recommend pumping Norweco tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/13/2023 | Alternative | Routine/Scheduled | 196-05-791 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. BioFilter - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 08:00 AM
05/24/2023 | Alternative |  | 101-10-0357 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Chrish | Erkel | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/27/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | Dec 30 1899 2:02PM
08/17/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | MicroFast | Pump | Pressure | Drip |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | [17 empty] | 4" overall liquid depth with 3" of scum & 10' of sludge. Blowers and pumps not working when I arrived. Breakers were off. Reset Breakers everything is working now. Field dry no pressure on supply and return to drip field. Suspect a leak in the force main. Owners had the leak repaired on 9/11/2023. Everything is good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 10:30 AM
04/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
06/27/2023 | Alternative | Pump-Out Only | 234-17-473 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/27/2023 | Dec 30 1899 3:00PM
05/02/2023 |  | RoutineScheduled | 003-STS-30861 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 1000 | Aquasafe 1000 |  | Pump | Pressure | Drip |  | 300.000000 | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation","Distribution Pump Operation","Auxiliary Filter"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation","Distribution Pump Operation","Auxiliary Filter"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | 09:10 AM
03/07/2023 | Alternative | RoutineScheduled Component Maintenance | 175-09-0459 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | 11:24 AM
01/20/2023 |  | Reportable Incident | 177-13-0276-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced failed blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
03/01/2023 |  | RoutineScheduled | 153-STS-20291 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity |  | Not Applicable |  | ["Disinfection"] | ["Disinfection"] | NA |  |  | 2.100000 | 2.100000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 03/31/2023 | 12:26 PM
09/21/2023 | Alternative | Reportable Incident | -STS-93807 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 2-3 0-5 | 0-3 | Pump | Pressure | Drip | UV |  | ["Auxiliary Filter","Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","SludgeScum Accumulation","Level Sensor Operation"] | YES | None | Clear |  |  | 9.000000 | [11 empty] | Inspected | replaced UV Bulb unit/melted | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/21/2023 | 10:00 AM
01/23/2023 | Alternative | Routine/Scheduled | 166-09-177 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. BioFilter - 4 Modules - peatmoss in fair condition - standing water in sampling port. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 08:30 AM
10/25/2023 | Alternative |  | 01-197-A1 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 7.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/19/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/19/2023 | Dec 30 1899 10:15AM
01/11/2023 |  | Routine/Scheduled | 14-172-0185A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/11/2023 | Jan 1 1900 2:59PM
05/07/2023 | Alternative | RoutineScheduled | 001-STS-92841 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | AQUASAFE |  | Pump | Pressure | Mound | UV | 300.000000 | [] | [] | [18 empty] | EVERYTHING WORKING AS SHOULD. CLEANED HIGH PRESSURE FILTER. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | 01:25 PM
11/17/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 12:00 AM
10/10/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 10/10/2023 | Sample Chamber | 3.000000 |  | 33.000000 |  |  |  | Attached to this report |  | Septic Tank-4"sludge 4"scum/ Microfast-6"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and woking correctly/ Controls,pump,floats and alarms are functioning properly/ Counts: Pump=4938 ETM=1299h 15m/ Watermeter=0342246.3 On-16m 55s Off-3h/ High level-30/ Jet UV-Light Sleeve cleaned/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/01/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [12 empty] | Pumped Out | Replaced UV control panel | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | Dec 30 1899 7:30AM
04/05/2023 |  | Routine/Scheduled | 02-0381A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 2.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/05/2023 | Jan 1 1900 3:00PM
06/07/2023 | Alternative | Routine/Scheduled | 199-07-0049 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Pump tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | Dec 30 1899 10:30AM
03/04/2023 | Alternative | RoutineScheduled | SD-06-312 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2000 | septic | Advantex | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | YES | Musty | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/11/2023 | 07:35 AM
05/02/2023 |  | RoutineScheduled | 179-10-0108-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
04/06/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-4"sludge 8"scum/ Microfast-12"sludge 0"scum ( May need pump out next year) Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-405 ETM-21h 31m/ Pump2-399 ETM-21h 19m On-3m 14s Off-12h Pump 55gpm/ Peak cnts-10/ High cnts-6/ No breakout or spongy areas on the drainfield and dosing correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/24/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 01/24/2023 |  | 14.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample normal Recommend cutting trees get more sunlight on field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired leak in drainfield | This AOSS should now return to normal function after having provided the above state routine maintenance | 08/23/2023 | 06:57 AM
05/12/2023 |  | RoutineScheduled | 177-18-0166-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
03/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic/atu needs pumped out it has a lot of grease in the tank. The Inlet T was clogged when we got there. We unclogged the grease from the Tee. Also there clean out cap was missing and we installed a new one. We told the home owner to stop driving over his sewer line with his truck. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
12/18/2023 | Alternative | RoutineScheduled | SWP-05 390 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | [8 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] |  | None | Clear |  |  | 7.000000 | [11 empty] | Inspected | system pumped out | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 10:00 AM
03/28/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Disinfection"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Microfast needs pumping & UV unit needs bulb, ballast & glass housing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/15/2023 | Jan 1 1900 7:20PM
07/17/2023 | Alternative | Routine/Scheduled | 13-163-0028 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Trash Tank - normal level Aeration tank - normal level - mixing present - aspirator serviced. Clarifier - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. DBox - concrete - intact - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/18/2023 | Dec 30 1899 7:30AM
09/22/2023 | Alternative | Routine/Scheduled | 19-174-0001 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Aqua Klear |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/22/2023 | Dec 30 1899 10:55AM
03/22/2023 |  | Routine/Scheduled | 041-STS-257801 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/22/2023 | Jan 1 1900 2:59PM
04/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/19/2023 |  |  | 2014-143-0131 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Ecopod | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Inspected | Septic tank needs to be pumped | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/02/2023 | 12:00 AM
12/11/2023 | Alternative | RoutineScheduled Component Maintenance | 179-08-0117-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
02/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/21/2023 |  | RoutineScheduled | S-12-111-0081 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 2.000000 | 4500 | Septic Tank Only | Ecopod | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The blower filter was cleaned. The dosing and discharge pumps were operating as designed. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | Jan 1 1900 10:40AM
01/24/2023 |  | Pump-Out Only | 2015-143-0013 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip | UV |  | SludgeScum Accumulation | ["Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Pumped out the septic tank which was backed up due to the filter being clogged. Changed out filter for the correct filter for the plastic tank. The system should return to normal operation. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/24/2023 | 11:48 AM
05/26/2023 | Alternative | Follow-Up Component Maintenance | SD-12-174 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001236 | Stuart | Lynn | 2.000000 | 12000 | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Report covers weekly events for the month of May 5-6-23 Pump 4,000 Shayne Carder 5-9-12-11 2023 Backhoe, soils work and mow drainfield areas, Lime wet areas 5-11-23 Pump 4,000 gallons Shayne Carder Advantage 5-17-23 Pump 4,000 gallons Freddie Perez Advantage 5-19-23 Justin Little Clean AX Max Spinners and flush lines, hose off media 5-19-23 Calibrated zones and adjusted run times 5-23-23 Weed eat inside fence and Lime wet areas Meet building inspector to sign off on Garage Permit 5-24-23 Reviewed consent order with attorney and Lance Gregory requesting amendments 5-30-23 Checked and unclogged air transfer line between AX Max 1 & 2 Cleaned clog at carbon filter should improve air transfer Steve Barry at AQWA recommends leaving one lid on each AX max cracked open to improve oxygen transfer skimmed floatables off top of pump chamber | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/30/2023 | 12:47 PM
05/02/2023 |  | RoutineScheduled | 179-STS-91718 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 0-0 0-00-0 |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear | [14 empty] | Inspected | new home looks good | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | 12:00 AM
06/07/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-2"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Puraflo peat turned and fluffed in all 5 modules , peat in good condition/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-022516 ETM-0024830/ Pump2-022686 ETM-0022714 On-43s Off-2h/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/26/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-3325 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/26/2023 | Dec 30 1899 10:35AM
03/15/2023 |  | Follow-Up | 175-15-0427 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Clearstream | none | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed K4000 Zoner. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
12/04/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20376 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Disinfection"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Odor coming from UV light and sample box 24 inch riser on septic tank has a broken flang Note: Microfast has settled about 4 to 5 inches and flow is restricted flow in UV piping do to settling. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/18/2023 | 08:36 AM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/28/2023 | Alternative | Reportable Incident | 234-15-421 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/28/2023 | Dec 30 1899 1:00PM
08/18/2023 | Alternative | RoutineScheduled |  | Warren | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation","Attached Growth Medium"] | YES | [17 empty] | septic and pump tank need pumped out | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:20 PM
05/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
02/02/2023 |  | Initial Visit | 550-STS-6531 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Tenant had called due to the light - no alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream, cleaned the filter in the aerator, and cleaned the UV light bulb. Installed a 3/4" brass check valve on the headworks. Fixed the UV - the fittings were not glued - tube was full of H20. Meet with the pumping company and pumped out the pump tank. Visible wetness on the drainfield - most likely from rain - once it dries need to keep an eye on it. The timer is set to 5 minutes every 2hours. Did not take initial samples due to the system being flooded on arrival. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/02/2023 | Jan 1 1900 1:50PM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Aerator motor broke PVC fittings inside the blower housing. ATU was not receiving aeration. Homeowner has contacted someone for repair. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/04/2023 | 06:02 AM
04/17/2023 | Alternative | Routine/Scheduled | 093-11-0164 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | Dec 30 1899 12:30PM
11/08/2023 | Alternative | Routine/Scheduled | 166-10-133 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Found 2in of sludge and less than 1in of solids. Pulled and cleaned filter. -Discharge/Pump Tank: Found at normal level, teste floats and pump all working as they should. Alarm can be heard inside -Peat Moss: Tipping bucket and trays are in working order. Raked out peat on both sides. Peat still good. Some compaction. -Distribution Box: Found on right side of drive way 15in deep. 3 lines balanced and taking water. No roots or cracks. -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 12:40 PM
02/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation"] | ["Attached Growth Medium","SludgeScum Accumulation"] | NA | [17 empty] | Septic Tank Side-4"sludge 1"scum/ Microfast-16"sludge and media is clogging, requiring pump out and spray the media/ Pump Tank-1"sludge/ Controls, pumps, floats and alarms functioning properly/ Blower air filter cleaned and blower is working correctly/ Counts: Pump1-856 ETM-45h 10m/ Pump2-827 ETM-44h 0m/ Peak-12/ High-13/ On -3m 14s Standard Off-10h Peak Off-8h/ No breakout or spongy areas on the drainfield. Owner had the tanks pumped on 4/19/2023 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
12/13/2023 | Alternative | Routine/Scheduled | 166-99-002 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Puraflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 45.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 06:54 PM
04/04/2023 |  | Reportable Incident |  | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Alarm Event. Discharge pump failure - pumped septic tank and pump tank empty - replaced pump with new Zoeller N98. Peatmoss modules have failed - Peatmoss spent - requires replacement of Biofilter. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/05/2023 | 09:45 AM
08/29/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-2346 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/29/2023 | Dec 30 1899 12:10PM
09/09/2023 | Alternative | RoutineScheduled | 2095-04-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.800000 |  |  | 1.400000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
06/06/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
09/26/2023 | Alternative | RoutineScheduled | 07-113-243 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5- Blue Crystal tablets installed 10 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/26/2023 | 12:00 AM
12/13/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Cloudy | 7.560000 |  |  |  |  | 12/13/2023 |  | 4.000000 |  |  | 2.400000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 10:15 AM
03/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The system appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/27/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Pump | Gravity | Trenches |  | 450.000000 | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/28/2023 | 10:16 PM
12/28/2023 | Alternative | Routine/Scheduled | 033-17-0183-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component Water level normal. Structural integrity of tank appears to be intact. Inlet tee appears to be intact. Due for pump out Discharge/Pump Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Aeration Condition of above Component Notes for above Component Water level normal. Not due for pump out Air Pump/Blower Condition of above Component Notes for above Component Checked and confirmed aerator is functioning properly. Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Distribution Box Condition of above Component Notes for above Component Water level normal. Structural integrity of distribution box appears to be intact. Drain Field Condition of above Component Notes for above Component Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2024 | 09:27 AM
07/05/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.300000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 02:30 PM
07/14/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Needs UV bulb & chord. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 08/15/2023 | Dec 30 1899 1:44PM
03/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/06/2023 |  | Routine/Scheduled | 2014-143-0089 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/06/2023 | 10:39 AM
07/27/2023 | Alternative | RoutineScheduled | SD-06-82 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Septic Tank | Puraflo | Pump | Gravity | Trenches | Not Applicable | 57.200000 | ["SludgeScum Accumulation","Effluent Screens"] | ["SludgeScum Accumulation","Effluent Screens"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | 12:00 AM
07/13/2023 | Alternative | RoutineScheduled | 085-STS-33646 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/23/2023 |  |  | 132-05-0123 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Virginia Soils Inc, dba VSI Supply / AG Onsite | 1942001291 | Archie | Arnold | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/15/2023 | 12:00 AM
01/17/2023 |  | RoutineScheduled | 177-06-0309-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | House is not occupied at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
03/06/2023 | Alternative | RoutineScheduled | 04-160-0388 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Southwest Soils, Inc. | 1942001494 | Stephen D. | Dalton | 1.000000 | 1000 | Whitewater DR 60 |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 | ["Other","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Other"] | NA | Musty | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/06/2023 | 12:50 PM
01/25/2023 |  | Routine/Scheduled | 19-120-0201A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/25/2023 | Jan 1 1900 8:15AM
02/28/2023 |  | Routine/Scheduled | 228-12-0301 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/28/2023 | Jan 1 1900 11:55PM
04/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
02/21/2023 |  | RoutineScheduled | 18-100-0069 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | AquaSafe |  | Pump | Pressure | Mound | UV | 900.000000 | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | [17 empty] | Pumped Out | Installed a new sewage pump and replaced 3 control floats and wire between panel and pump station. Pumped out to be able to do the repair. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/29/2023 | 01:25 PM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance | 175-15-0477 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Salcor UV unit is burned up and whole UV needs replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | 12:58 PM
09/19/2023 | Alternative | RoutineScheduled | SD-99-232 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1500 | septic | Multi-flo | Gravity | Pressure | Discharge | Chlorination |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [5 empty] | 09/19/2023 | Pump Chamber | 2.000000 | 1.060000 |  | 1.000000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/02/2023 | 09:10 AM
06/20/2023 | Alternative | RoutineScheduled | VAG408192 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | ["Auxiliary Filter"] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/13/2023 | 01:00 PM
09/29/2023 | Alternative | Initial Visit |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream and cleaned the UV light bulb. Replaced broken fitting on diffuser assembly. Changed the filter in the aerator and changed the mesh screen in the spinfilter (was stopped up). There is no inlet tee in the septic tank. Need to pump and clean the pump tank and Clearstream tank. The timer was set at 30 seconds every 2 hours changed it to 8 minutes every 2 hours. Did not take samples. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/29/2023 | Dec 30 1899 2:45PM
11/29/2023 | Alternative | Follow-Up | S 800-18-0154 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Meet with the pumping company and pumped the septic tank, Clearstream tank, and pump tank. The septic tank was full of grease. Changed the mesh screen in the spinfilter screen. Need to go back to hook up the pressure switch due to the pumping of the tanks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/29/2023 | Dec 30 1899 12:30PM
03/25/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 4.000000 | 8500 | EZ Treat |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Septic tank #1 - 10" of accumulated solids. Septic tank #2 - 10" of accumulated solids. Recirculation Tank - 12" of accumulated solids. Discharge Pump Tank - 1"of accumulated solids. Cleaned septic tank filter. Cleaned EZ Treat spray nozzles. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/07/2023 | 07:03 PM
02/15/2023 |  | RoutineScheduled | 10-118-0034 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1500 | Clearstream |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/15/2023 | Jan 1 1900 2:05PM
08/10/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-8"sludge 0"scum/ Pump Tank-2"sludge/ No pump out needed at this time/ Controls, pumps, floats and alarms functioning properly/ Puraflo Peat was turned and is in good condition/ Counts: Pump1-004943 ETM-0068533/ Pump2-004898 ETM-0008183 On-1m 7s Off-2h/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/29/2023 | Alternative | RoutineScheduled | S102-08-0014 | Alleghany | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | [7 empty] | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The blower and spin filters were both pulled and cleaned. The controls were operating as designed. There were return effluent returning to the pump chamber from the drip field, so the drip field is operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/17/2024 | Dec 30 1899 4:55PM
07/20/2023 | Alternative | RoutineScheduled | 02-163-0115 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Advantex |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Recirculation Pump","Control Operation","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | 12:00 AM
05/16/2023 | Alternative | RoutineScheduled | 001-STS-92304 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn |  |  | FUJICLEAN CEN-5 |  | Pump | Pressure | Mound | UV |  | [] | [] | [17 empty] | Pumped Out | EVERYTHING WORKING AS IT SHOULD. CLEANED HIGH PRESSURE FILTER. PUMPED SLUDGE. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 12:40 PM
03/13/2023 | Alternative | Follow-Up | 159-01-056 | Middlesex | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 2000 | Clearstream |  | Pump | Pressure | Trenches | Not Applicable | 1500.000000 | ["Control Operation","Distribution Pump Operation"] | ["Control Operation","Distribution Pump Operation"] | [18 empty] | System in high level condition - needs to have complete drawdown conducted, timer settings adjusted and there is still a fixture leak in the building causing hydraulic overload of the system. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/14/2023 | 08:00 AM
05/11/2023 |  | RoutineScheduled | 2014-143-0166 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
03/28/2023 |  |  | 06-142-0453 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | ecoflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
09/26/2023 | Alternative | RoutineScheduled | 12-197-A2 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 |  | ATU |  |  |  |  | Chlorination |  |  |  |  | None | Clear | 6.500000 | 5.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
01/27/2023 |  | Routine/Scheduled | 234-14-280 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/27/2023 | Jan 1 1900 10:20AM
11/20/2023 | Alternative | Reportable Incident Component Maintenance | SWP-01-271 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | On site for system in alarm due to failed timer float. Replaced failed float and light bulb for the alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
02/22/2023 |  | RoutineScheduled |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 3.000000 | 1500 | 1-8 0-0 | 0-0 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] |  | None | Clear |  |  | 16.000000 | [11 empty] | Inspected | replaced 2 floats in recirc tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | 12:00 PM
07/17/2023 | Alternative | Reportable Incident | 234-03-10843 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [17 empty] | Replaced pump and timer enable float | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/17/2023 | Dec 30 1899 5:00PM
02/28/2023 |  | RoutineScheduled |  | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
12/26/2023 | Alternative | Routine/Scheduled | 136-17-0182 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Trash Tank Condition of above Component Notes for above Component Pumped and cleaned at service No signs of infiltration Inlet and outlet tees intact Discharge/Pump Tank Condition of above Component Notes for above Component Normal Level All floats and pump are functioning properly Shrink wrap splice with uf wire connections in tank No signs of infiltration Aeration Condition of above Component Notes for above Component Pumped and cleaned at service agreement Pulled and cleaned bio kinetic filter and housing Air Pump/Blower Aerator/ aspirator Condition of above Component Notes for above Component Pulled and cleaned aspirator Functioning properly Control Panel Condition of above Component Notes for above Component 120v to panel All audible and visual alarms are functioning properly Pump pulled 4.42amps Distribution Box Condition of above Component Notes for above Component Unable to locate Drain Field Condition of above Component Notes for above Component No signs of surfacing in drainfield Pumped and refilled | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 07:59 AM
09/11/2023 | Alternative | Reportable Incident | 2005-143-0048 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm Call - Upon arrival, I found the discharge tank in high level. Checked and found the discharge pump had failed. Replaced discharge pump under warranty. Checked and confirmed there was a weep hole. Checked and confirmed check valve was functioning properly. Checked and confirmed control panel was functioning properly. Checked floats and found that the timer enable had failed. Homeowner gave approval to upgrade floats. I upgraded floats while on site with float tree. Checked and confirmed floats are functioning properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | 10:51 AM
09/12/2023 | Alternative | RoutineScheduled | 2015-143-0066 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Distribution Pump Operation","BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/19/2023 | Alternative | RoutineScheduled | 10-100-0526 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | Bio-Coir |  | Pump | Pressure | Mound | UV | 600.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | Shared system with 4387 Ridge Rd. Sludge judge test revealed 4-5 in of accumulation at the bottom of the septic tank. No pumping was needed. System and components are working as designed. UV light is working. Sprayer nozzles were cleaned. Media was in at the right level and in good condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 09:10 AM
01/18/2023 |  | RoutineScheduled | 179-STS-90122 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Our technicians noted that your drip dispersal area is on a steep slope that is difficult to mow. We would advise you that maintaining the disposal area is important to prevent roots from interfering with the drip tubing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/16/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 08/29/2023 | Dec 30 1899 3:58AM
02/07/2023 |  | RoutineScheduled | 179-STS-90250 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | NA | Musty | Cloudy | [5 empty] | 02/07/2023 |  | 68.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Water was a little cloudy due to media having filamentus bacteria but not clogged up yet. will check next visit. Gave customer copy of Do's and Don'ts. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
01/03/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 2.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
12/01/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 1.000000 | 1000 | Ecoflo premiere tech |  | Gravity | Pressure | Drip | Not Applicable | 100.000000 | ["Distribution Pump Operation","Effluent Screens"] | ["Auxiliary Filter","Distribution Pump Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | System is operating as intended and is in compliance with the health department regulations! | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/01/2023 | 02:45 AM
03/15/2023 |  | Routine/Scheduled | 228-15-0296 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | Jan 1 1900 10:48AM
11/06/2023 | Alternative | RoutineScheduled | 182-05-0099 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","SludgeScum Accumulation"] | ["Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [14 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
06/08/2023 | Alternative | Routine/Scheduled | 166-16-0078 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash Tank - normal level Aeration Tank - normal level - mixing present - compresso rserviced. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 01:00 PM
11/16/2023 | Alternative | Reportable Incident Component Maintenance | SWP-00-586 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to failed enable float and clogged spin filter. Filter flush and field flush valves were both turned off. Replaced failed float and crushed spin filter. Cleaned both valves and replaced filter flush solenoid with a used one. Panel has been rewired. If panel gas anymore issues it will neeed to be replaced. Proposal to be sent to replaced leaking outlet riser on septic tank and bleach flush drip tubing to try to increase the flush rate. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
02/21/2023 |  | Routine/Scheduled | 550-STS-6595 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/21/2023 | Jan 1 1900 1:10PM
12/28/2023 | Alternative |  | 87-183-170 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/28/2023 |  | 3.180000 |  |  | 3.070000 |  |  | Will be sent separately |  | BOD: 3.18 TSS: 3.07 SV | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/28/2023 | 12:00 AM
06/29/2023 | Alternative | Reportable Incident Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced EZ Treat pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/30/2023 | 10:30 AM
10/24/2023 | Alternative | Routine/Scheduled |  | Dinwiddie | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/24/2023 | Dec 30 1899 3:24PM
02/21/2023 |  | RoutineScheduled | 101-08-0055 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | MicroFast |  | Gravity | Pressure | Drip | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/25/2023 | 12:00 AM
08/02/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 540 | Multiflo FTB |  | Gravity | Gravity | Trenches |  | 600.000000 | None | None | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 02:14 PM
08/30/2023 | Alternative | RoutineScheduled | 06-183-254 | Russell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Advantex should be pumped and manifold needs to be cleaned to function properly. Air release valve in the field is broken and there is effluent surfacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
02/19/2023 |  | Routine/Scheduled | 041-STS-259216 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [16 empty] | Recommend pump out | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/19/2023 | Jan 1 1900 12:00PM
12/20/2023 | Alternative |  | 14-197-070 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/20/2023 |  | 5.870000 |  |  | 7.600000 |  |  | Will be sent separately |  | BOD: 5.87 DC TSS: 7.60 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 12:00 AM
07/28/2023 | Alternative | Reportable Incident | 093-13-0104 | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/28/2023 | Dec 30 1899 12:05PM
04/01/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/09/2023 | 12:00 AM
06/28/2023 | Alternative | Routine/Scheduled | 177-STS-89303 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 600 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 11:00 AM
10/24/2023 | Alternative | RoutineScheduled | 05-192-199 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | WHITEWATER |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 4 - Blue Crystal tablets installed 4 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/24/2023 | 12:00 AM
03/22/2023 |  | Pump-Out Only | 153-STS-20161 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | McKimSeptic & Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | [] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | 03:30 PM
06/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
11/09/2023 | Alternative | RoutineScheduled Component Maintenance | 175-05-0408 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 09:34 AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Inspection was performed. System components need to be updated. Will re-file once components are updated. System appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
04/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/22/2023 |  | Routine/Scheduled | 228-19-0010 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/22/2023 | Jan 1 1900 9:30AM
02/09/2023 | Alternative |  |  | Buckingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Piedmont |  |  | Eric | Wilkening | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/26/2023 | Alternative | RoutineScheduled Component Maintenance | 099-14-0063-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
08/10/2023 | Alternative | Pump-Out Only | 234-12-12 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | Dec 30 1899 12:30PM
04/19/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | septic and atu tank need pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
08/22/2023 | Alternative | RoutineScheduled | 179-STS-92503 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 0-0 0-0 | 0=0 | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/22/2023 | 12:00 PM
02/23/2023 |  | RoutineScheduled | 179-STS-90578 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Peat has shrunk to 4" or 5" below the grids, but otherwise in good condition. Briars and saplings are gone from drainfield, but not a blade of grass is growing. Recommended planting grass to prevent erosion. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
02/06/2023 |  | RoutineScheduled | 196.02.632 | Westmoreland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Repaired faulty splice to control panel. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
11/29/2023 | Alternative | RoutineScheduled | 181-05-0422 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | SEPTIC TANK ONLY | ADVANTEXAX20 | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | THE SYSTEM DID NOT NEED TO BE PUMPED. THE EFFLUENT FILTER WAS PULLED AND CLEANED. THE TEXTILE SHEET WERE SPRAYED OFF. THE LATERALS WERE CLEANED. THE RECIRCULATING PUMP WAS PULLED AND CLEANED. THE CONTROLS WERE OPERATING AS DESIGNED. THERE WERE NO VISIBLE LEAKS IN THE LEECH FIELD. THE LIDS WERE SECURED. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | 12:30 PM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/05/2023 | Alternative | RoutineScheduled Component Maintenance | 182-03-0417 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Recommend timer upgrade | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
04/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/27/2023 | Alternative |  | 033-17-0136-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
06/30/2023 | Alternative | Reportable Incident Component Maintenance | 175-03-0441 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed effluent pump 1 1/2 hp/230v, 4 control floats & new bulbs for control panel. Blower needs replacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
08/10/2023 | Alternative | RoutineScheduled | 182-12-0234 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Dispersal System Operation","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","Dispersal System Operation","BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | 12:00 AM
04/08/2023 | Alternative | Reportable Incident | 015-STS-334083 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Distribution Pump Operation"] | ["Effluent Screens","Distribution Pump Operation"] | YES | Musty | Clear | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/06/2023 | 12:00 AM
04/26/2023 |  | Reportable Incident | 234-13-50 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/25/2023 | Jan 1 1900 11:00AM
11/17/2023 | Alternative | RoutineScheduled | 175-05-0109 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank | Delta ATU to Discharge Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | NA | [17 empty] | Septic Tank-4"sludge 0"scum/ Delta ATU-4"sludge 2"scum/ Discharge Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower functioning correctly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-162355 ETM-631h/ High-869/ Hand-92/ Watermeter-1650200/ Repaired leak in the Delta Zoner/ No breakout or spongy areas on the drip field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/18/2023 | Alternative | Initial Visit | 181-15-0034 | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Siphon | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","SludgeScum Accumulation","Septic Tank Baffles"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","SludgeScum Accumulation","Septic Tank Baffles"] | NA | [16 empty] | Pumped Out | The 1500 Gal MicroFast tank was pumped out and cleaned. The exit pipe was clogged leaving the treatment unit. The lid was taken off and the unit was sprayed off and cleaned. The blower was getting hot and cutting off, but cleaning the treatment unit repaired the problem. The syphon tank was pumped and cleaned. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/08/2023 | 02:55 PM
05/03/2023 | Alternative | Routine/Scheduled | 136-09-0098 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating - bulging noted. BioFilter - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/04/2023 | 06:45 AM
04/06/2023 |  | RoutineScheduled | 157-13-0132 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1500 | Microfast |  | Pump | Gravity | Mound | Not Applicable |  | ["Distribution Pump Operation"] | [] | [18 empty] | Spin filter needs replacing. Cleaned and reinstalled old spin filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 12:00 AM
06/13/2023 |  | Initial Visit | 165-STS-339084 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 1.000000 |  | Advantex RT |  | Gravity | Pressure | Drip | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] | NO | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 03:30 PM
02/16/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/06/2023 |  | RoutineScheduled | 175-02-0654 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
10/19/2023 | Alternative | RoutineScheduled | 121-STS-11979 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner |  |  | INFILTRATOR |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | YES | [16 empty] | Inspected | - major root infiltration in septic tank - recommend all maple trees near tank be removed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/27/2023 | 12:00 AM
01/26/2023 |  | Routine/Scheduled | 800-09-0260 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | Jan 1 1900 3:09PM
04/03/2023 |  | RoutineScheduled | 132-18-0055 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | 12:00 AM
12/22/2023 | Alternative |  |  | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1750 | 1000 | 750 | Pump | Gravity | Pad | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Level Sensor Operation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/22/2023 | Dec 30 1899 1:00PM
09/15/2023 | Alternative | RoutineScheduled Component Maintenance | 175-12-0412 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
05/17/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-3134 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | Dec 30 1899 2:00PM
06/16/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | UV bulb and ballast were replaced. The system should return to proper function. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/05/2023 |  | RoutineScheduled | 132-03-0068 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Advantex |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/08/2023 | 12:00 AM
05/11/2023 |  | Routine/Scheduled | 16-120-0269A conditional | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/11/2023 | Jan 1 1900 9:27AM
06/06/2023 |  | RoutineScheduled | 124-STS-2379 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Virginia Beach | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1875 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/02/2023 | Alternative | RoutineScheduled | 067-STS-39434 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex AX20RT |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. Adjusted recirculation pump timers, recirculation pump flow rate and position of recirculation pump float switches due to manufacturer service update. This unit fell within a specific serial number range that required these changes to avoid recirculation tank high levels. 4" of accumulated solids in first section of the septic tank. 10" of accumulated solids in the second portion of the septic tank. Cleaned septic tank solids filter. 0" of solids in recirculation portion of the treatment unit. 0" of solids in the discharge portion of the treatment unit. Flushed treatment unit spray manifold. Tested floats, pump and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/22/2024 | 07:03 PM
03/09/2023 |  | RoutineScheduled | 175-18-0040 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic / Advantex ATU Treatment Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | [18 empty] | Septic Advantex Recirc Tank-6"sludge 4"scum/ Pump Tank-0"sludge/ No pump out needed at this time/ Controls, pumps, floats and alarms functioning properly/ Counts: Recirc pump cycles-81721.0/ Recirc run time-418.4/ Discharge pump cycles-1700.0 Discharge pump run time-57.7/ Recirc. pump intake cleaned/ Media in good condition/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/21/2023 |  | RoutineScheduled | 17-100-0507 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
03/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was off at time of inspection. It was turned on and appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/12/2023 |  |  | 2018-143-0035 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Aqua Klear |  | Pump | Pressure |  |  |  | [] | ["Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/12/2023 | 12:00 AM
12/19/2023 | Alternative | RoutineScheduled | 001-STS-93038 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1500 | PURASYS |  | Pump | Pressure | Trenches | Not Applicable | 600.000000 | [] | [] | NA | [17 empty] | SLUDGE JUDGE OF SEPTIC TANK REVEALED 2-3" FROM BOTTOM EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/15/2024 | 09:55 AM
11/06/2023 | Alternative | RoutineScheduled | 107-09-0176 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles"] | ["Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | 12:00 AM
01/09/2023 | Alternative | Reportable Incident | 136-03-654 | Gloucester | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | Effluent Screens | YES | [17 empty] | Property owner not interested in having required service conducted - claims system is grandfathered and no service necessary. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/10/2023 | 11:00 AM
03/27/2023 | Alternative | Routine/Scheduled | 151-17-031 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 10.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/27/2023 | 05:56 PM
04/07/2023 |  | Routine/Scheduled | 15-137-0070 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1250 | Multiflo ATU |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | Effluent filter cleaned. Disc filter cleaned. Drip field flushed. System checked. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/07/2023 | Jan 1 1900 11:50AM
05/02/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1200 |  |  | Pump | Gravity | Pad | Not Applicable | 600.000000 | ["None"] | ["None"] | NO | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | Dec 30 1899 4:15PM
12/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] |  | NO | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities .Repair to biotube basket has not been completed and makes servicing bio tube filter non serviceable. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/13/2024 | 11:49 AM
02/02/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced concrete casing lid & electrical junction box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
05/31/2023 | Alternative | RoutineScheduled | 182-04-0113 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | Drip field overgrown | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/31/2023 | 12:00 AM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Fittings that connect blower to downshaft are damaged | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
08/03/2023 | Alternative | RoutineScheduled | 06-192-080 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | WHITEWATER |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/03/2023 | 12:00 AM
06/14/2023 | Alternative | RoutineScheduled | 150-08-0229 | King William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 3.000000 | 2900 gallons | septic tank | Delta Whitewater | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Level Sensor Operation","Distribution Pump Operation","Control Operation","BlowerCompressorAerator Operation"] | NA | Musty | Clear |  |  | 20.000000 | [12 empty] | Septic tank 4" fog, 8" sludge. Delta Whitewater original aerator not working, previously rebuilt, installed new aerator, 20% SS. Pump, alarm, floats, controls operating properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/23/2023 | 05:40 PM
10/12/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | 12:00 AM
12/01/2023 | Alternative | RoutineScheduled | DTAR-999PPS | Craig | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | King's Alternative Septic | 1942001112 | William | King, II | 1.000000 | 1500 | BioMicrobics Microfast 0.5 |  | Gravity | Gravity | Trenches | Not Applicable | 250.000000 | ["None"] | ["None"] | NA | [17 empty] | System is working correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/03/2023 | 12:00 AM
03/16/2023 |  | RoutineScheduled | 05-192-199 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 2 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/16/2023 | 12:00 AM
08/07/2023 | Alternative | RoutineScheduled | 09-192-184 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 10 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/07/2023 | 12:00 AM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity |  | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection"] | ["BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | 7.200000 | 10.400000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 10/16/2023 | 12:58 PM
07/31/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Trenches |  | 300.000000 | ["Attached Growth Medium","Effluent Screens"] | Effluent Screens | YES | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/13/2023 | 01:12 PM
11/01/2023 | Alternative | RoutineScheduled | 03-142-0078 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Recirculation Pump","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/07/2023 | Alternative | Routine/Scheduled | 234-17-0075 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | UV not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/07/2023 | Dec 30 1899 2:26PM
09/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and pumping | 1942001330 | Michelle | McKim | 3.000000 | 1500 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 4:40PM
08/04/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-89026 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. HL-5, LL-16, OVERRIDE-0. Blower 2.98 amps. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
02/28/2023 |  | Routine/Scheduled | 16-174-0190 | Prince George | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Crater | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service - Owner has had "others" maintain the system. Primary septic tank - normal level - effluent screen serviced. Biofilter - peatmoss has failed - ponding / holding effluent - tipping bucket broken and requires replacing. Pump Basin - float sensors, pump and controls operating. DBox - intact | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/01/2023 | Jan 1 1900 10:15AM
03/14/2023 |  |  | 2006-143-0346 | Henrico | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 3000 | 1000 | 1000 | Pump | Pressure | Mound | Not Applicable |  | [] | ["Attached Growth Medium","Effluent Screens","Level Sensor Operation","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | YES | None | Clear | 6.000000 |  | 6.000000 | [13 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/14/2023 | 12:00 PM
03/08/2023 |  | RoutineScheduled | 179-STS-91612 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Septic Tank Baffles" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | None | Clear | [5 empty] | 03/08/2023 |  | 6.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Blower 3.26 amps. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
10/18/2023 | Alternative | RoutineScheduled | 027-STS-17146 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | CLEARSTREAM |  | Pump | Pressure | Drip | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Recirculation Pump","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Recirculation Pump","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | 12:00 AM
10/09/2023 | Alternative | RoutineScheduled | 04-160-0071 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 3.000000 |  | Ecoflo (peat moss) |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | 12:00 AM
08/17/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20199 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
05/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/16/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["Other"] | ["None"] | YES | [17 empty] | Customer peat moss needs to be replaced. All 5 modules. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/25/2023 | Dec 30 1899 4:05PM
06/14/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Visual alarm was replaced. Issues could not be replicated when troubleshooting and the system appears to be functioning as designed at this time. Advise homeowner to monitor alarms and notify if there are any changes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/02/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | Dec 30 1899 2:02PM
10/17/2023 | Alternative | Follow-Up Component Maintenance | 175-17-0122 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced ballast, chord & glass housing in UV Unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
06/09/2023 | Alternative | Routine/Scheduled | 2005-143-0020 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump and effluent screen serviced - recommend pumpout and refill Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact - lid is fractured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 07:00 AM
03/17/2023 |  | RoutineScheduled | 132-04-0159 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Drip | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/19/2023 | 12:00 AM
06/01/2023 |  |  | 085-STS-32437 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Norweco | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [18 empty] | We are pumping the septic tank on 6/12/23 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/02/2023 | 12:00 AM
03/14/2023 |  | RoutineScheduled | 175-02-0691 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] |  | NO | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
02/09/2023 | Alternative | Pump-Out Only | 15-160-0158 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 | 1500 gal | Microfast | [6 empty] | [] | [] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/02/2023 |  | RoutineScheduled | 153-STS-20237 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/31/2023 | 12:26 PM
05/24/2023 | Alternative | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced E294 effluent pump. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/15/2023 | Dec 30 1899 12:05PM
09/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | replaced 2 pressure gauges recommend replacing pod lid | This AOSS should now return to normal function after having provided the above state routine maintenance | 10/13/2023 | 01:07 PM
03/27/2023 |  | RoutineScheduled | 154-08-0267 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 12:00 AM
11/14/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 11/14/2023 | Dec 30 1899 9:00AM
09/29/2023 | Alternative | RoutineScheduled | SD-05-42 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation","Distribution Pump Operation","Dispersal System Operation"] | ["SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/29/2023 | 10:00 AM
05/25/2023 |  | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 |  |  | Pump | Pressure | Trenches |  | 300.000000 | Control Operation | Control Operation | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 10:31 AM
07/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | This system failed inspection. They need to install alarm bell, repair header lines, and pump out tanks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/04/2023 | 12:57 PM
10/09/2023 | Alternative | RoutineScheduled | 08-160-0244 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 3.000000 | 2500 | Ecoflo (peat moss) |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | YES | Septic | Cloudy | [14 empty] | Inspected | -alarm is not working -peatmoss needs to be replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/17/2023 | 12:00 AM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance | 107-07-0448 | Augusta | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | ET BEd Failing let us know if want us to repair | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/06/2023 | 08:40 AM
07/05/2023 | Alternative | Routine/Scheduled | 228-14-0002 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | Dec 30 1899 11:17PM
09/28/2023 | Alternative |  |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 RT |  |  | Pressure | Drip | Not Applicable |  | ["None"] | [] | [18 empty] | Start up | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/28/2023 | 12:00 AM
04/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/18/2023 |  | RoutineScheduled |  | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Level Sensor Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Media to be replaced Discharge tank lid to be replaced Recommend to have water softner not discharge into septic system Repaired Recirc Alarm float | This AOSS should now return to normal function after having provided the above state routine maintenance | 05/22/2023 | 11:15 AM
08/19/2023 | Alternative | Pump-Out Only |  | Middlesex | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Fuji |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Pump and Haul for repairs Gas company trenched through absorption field. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/21/2023 | 11:00 AM
04/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/14/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantes AX20RT |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 10" of accumulated solids in septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. 8" of solids in recirculation portion of treatment unit. 0" of solids in discharge portion of treatment unit. Tested floats, pump and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 07:03 PM
01/19/2023 |  | Routine/Scheduled | 03-172-0262AR | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing tank - RSV, Recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. DBox - Intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/19/2023 | Jan 1 1900 7:00AM
07/22/2023 | Alternative | RoutineScheduled | 136-05-0737 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Virginia Septic Solutions LLC | 1942001500 | Justin | Barker | 1.000000 |  | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | Musty | Clear | [15 empty] | Removed old media from biofilter and replaced with new media. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/22/2023 | 12:00 AM
08/18/2023 | Alternative | RoutineScheduled Component Maintenance | 099-06-0328-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection, leak on septic tank inlet riser. D-box got small Crack on it and seals are coming off lettings roos grow inside, recommend to replace box with a new fralo monster box. Line closer to tree not taking water, left it out of service. Added root-x to dbox to help with root problem. Added root destroyer to ecoflow pod to help keep root out. Will send proposal for work needed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
11/01/2023 | Alternative | RoutineScheduled | 001-STS-93090 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn |  |  | FUJI CLEAN CEN 5 |  | Pump | Gravity | Mound | UV | 450.000000 | [] | [] | YES | [17 empty] | SLUDGE JUDGE TEST REVEALED 4-6" FROM BOTTOM AND 1" FROM TOP IN FUJI CLEAN REPLACED UV LIGHT BULB REPLACED SEWAGE PUMP ALARM FLOAT EVERYTHING WORKING AS IT SHOULD | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/05/2023 | 09:20 AM
07/20/2023 | Alternative | RoutineScheduled Component Maintenance | 175-08-0259 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
03/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
03/17/2023 | Alternative | RoutineScheduled | SD-11-30 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches |  | 750.000000 | ["Attached Growth Medium","Effluent Screens","Control Operation","SludgeScum Accumulation"] | ["Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/17/2023 | 03:00 PM
07/18/2023 | Alternative | RoutineScheduled | 175-03-0803 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-6"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Media turned in all 5 modules and in fair condition/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-009642 ETM-0050487 On-20s Off-3h/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
01/12/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Air pre-filter cleaned as a measure of preventative maintenance. Alarm switch was in the silence position from an earlier alarm, reset it. Whine and slight bearing noise heard coming from the blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
08/17/2023 | Alternative | Routine/Scheduled | 22017-143-0189 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 16.400000 | [7 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The inlet tee was stopped up. Replaced one valve box on the drainfield. The timer is set to 8 minutes every 1.5 hours. Took 5 year BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/17/2023 | 08:15 AM
01/24/2023 |  | RoutineScheduled | 101-15-0243 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/28/2023 | 12:00 AM
10/27/2023 | Alternative | Routine/Scheduled | 157-10-0015 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the alarm light bulb. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/27/2023 | 11:00 AM
02/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | NA | [17 empty] | Septic-6"sludge 6"scum/ .625 Microfast ATU-6"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working properly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-3420 ETM-603h 50m/ Peak-20/ High-27/ Watermeter-0,175,936.3 On-11m 15s Off-2h 15m Peak Off-1h 46m/ Filters in the hydraulic unit cleaned/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/04/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation"] | ["Control Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Bad panel replaced Still need to evaluate pump and repair or replace | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/18/2023 | 04:10 AM
05/18/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.360000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/31/2023 | 11:45 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/04/2023 |  | Routine/Scheduled | {FIPSCode}-STS-1832 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/04/2023 | Jan 1 1900 9:15AM
01/30/2023 |  | RoutineScheduled | 14-100-0486 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | AQUASAFE |  | Pump | Gravity | Mound | UV | 600.000000 | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | [17 empty] | Pumped Out | Everything working. Pumped sludge. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/10/2023 | 01:55 PM
09/28/2023 | Alternative | Routine/Scheduled | 228-13-0486 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Changed the filter in the aerator and changed the mesh screen in the spinfilter. The pressure switch on the aerator is not hooked up. Replaced the UV ballast. The septic tank needs to be pumped out and pump out the the Clearstream tank. The timer is set to 4.5 minutes every 1 hour. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/28/2023 | Dec 30 1899 1:00PM
09/21/2023 | Alternative | Routine/Scheduled | 151-11-0142 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Puraflo |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 0.000000 | [11 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/21/2023 | 04:06 PM
11/24/2023 | Alternative | Routine/Scheduled | R-09-111-0110 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable |  | None | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/24/2023 | Dec 30 1899 2:00PM
02/08/2023 |  | RoutineScheduled | 165-STS-336632 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 2.000000 | 2000 | Septic Tank Only | AdvantexAX20RT | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | NO | [7 empty] | 02/08/2023 | Pump Chamber | 5.000000 |  |  | 4.000000 |  |  | Attached to this report |  | The sample draw was the 180 day sample draw and both the BOD and TSS were within the permitted limits. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/25/2023 | 01:15 PM
09/26/2023 | Alternative | Follow-Up | 128.13.0086 | Essex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | replaced df control panel, replaced blower control panel | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
04/19/2023 |  |  | 07-163-0256 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 1.000000 |  | Norweco Singulair |  | Gravity | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/19/2023 | 12:00 AM
08/16/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NO | [17 empty] | Septic Tank-3"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Controls, pump, floats and alarms functioning properly/ Filters cleaned in the hydraulic unit/ Watermeter counts: 0,322,434.89/ No breakout or spongy areas on the drip field and dosing all 3 zones properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/22/2023 |  | RoutineScheduled | 2016-143-0144 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 2.000000 |  | Puraflo |  | Pump | Gravity | Mound |  |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Auxiliary Filter","Level Sensor Operation"] |  | Musty | Cloudy | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/22/2023 | 12:00 AM
10/16/2023 | Alternative | RoutineScheduled | 181-04-0249 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","SludgeScum Accumulation"] | ["Effluent Screens","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | The 1500 Gallon MicroFast tank was pumped. The blower and spin filters were both pulled and cleaned. The effluent screen was cleaned on the discharge pump. The controls were operating as designed. There was effluent returning to the pump tank from the drip field. The drip field was operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | 11:00 AM
03/30/2023 |  | Follow-Up | SWP-03-784 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Owner had both tanks pumped out about a week ago. Effluent is still cloudy, but should improve over the next month (owner will discontinue use of scent beads). Replaced timer float switch that was sticking on at times. Bleach-flushed drip tubing and manifolds. Return ARV was about 10" below grade. When digging around it, discovered a check valve on the return line. Single zone drips do not need a check valve. This one had failed (flapper stuck open) and was removed. ARV raised to a more serviceable grade. Drip rate and flush rate were better after this work. Drip rate may improve a little more over the next month or two. Supply pressure, measured at the finger screen tubing, was a bit high at 72 psi. Return line pressure, measured at a new ARV with schrader valve, was 62 psi. Owner is planning on replacing the atu panel in the near future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
07/19/2023 | Alternative | Initial Visit | -STS-43184 | Botetourt | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation","SludgeScum Accumulation","Effluent Screens"] | ["Dispersal System Operation","SludgeScum Accumulation","Effluent Screens"] | YES | [16 empty] | Pumped Out | The 1500 Gal MicroFast tank was pumped and cleaned. The blower and spin clean filter were both pulled and cleaned. The discharge pump was getting hot and cutting off, however pumping the pump tank and cleaning the spin filter and the effluent screen fixed the problem. The controls were operating as designed. There was return effluent returning to the pump tank. There were no visible leaks in the drip field. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/08/2023 | Jan 1 1900 3:25PM
05/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/13/2023 | Alternative | Routine/Scheduled | 157-02-169 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annua Maintenance: -Septic Tank: Found at normal level, 3in of sludge and less than 1in of solids. Pulled and cleaned filter. Filter is up under the tank a little bit, difficult to pull filter -Discharge/Pump Tank: Found at normal level, 5in of sludge and less than 1in of solids. Tesyd floats and pump all working as they should. Riser section was installed with spray foam -Aeration: Found at normal level. 2in of sludge and less than 1in of solids. Pulled weir. Non serviceable air line. High level float working as it should -Air Pump/Blower: Pulled and cleaned air filter. No wires for air pressure sensor. -Control Panel: 120 volts audio and visual alarms working as they should. Pumpmpulled 7.3 amps -Distribution Box: Found at normal, 4 lines taking water some roots. Seals are deteriorating -Drain Field: No surfacing in drainfield area Repair (10/18): -Installation of 6" - 12" Riser on Pump Tank -Removal of outdated non-serviceable Air Hose Installation of a new serviceable Air Hose inside Tank -Installation of a Diffuser -Conduit & Wiring up to 10' -Replacement of the plastic Seals in the Distribution Box includes manual excavation up to 12" | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/30/2023 | 08:00 AM
09/22/2023 | Alternative | Routine/Scheduled | 14-177-1058 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | EcoPure |  | Pump | Gravity | Trenches | UV |  | None | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/22/2023 | 04:15 PM
02/15/2023 |  | RoutineScheduled | 179-16-0020-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for routine inspection. Sludge levels have risen dramatically since last year due to the use of scent beads and fabric softner. The drip rate and flush rate have decreased from last year. After system is pumped out and restarted we will follow up to see if the have increased. If they do not increase we will send a proposal to bleach flush the drip tubing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
07/20/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Bushes and shrubs around tank need trimming for access. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | Dec 30 1899 1:44PM
08/22/2023 | Alternative | Routine/Scheduled | 18-137-0074 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [17 empty] | Changed air filter. Checked system operation. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/23/2023 | Dec 30 1899 4:04PM
10/12/2023 | Alternative | Routine/Scheduled | 095-STS-5018 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Pressure | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/12/2023 | Dec 30 1899 11:07AM
12/04/2023 | Alternative | Reportable Incident | 157-00-0101 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/04/2023 | 04:30 PM
05/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | A sale inspection was done on an alternative septic system. All alternative septic systems in Virgina are required to be inspected every year and filed with the state and county. The septic control panel is an exterior time dose. There is a clean out near the house that we ran the camera snaked thru the sewer line to the Anua tank. The tank was pumped out and appears to be in good condition. The pump tank, pump, floats, force main and electric box were inspected. The 8 port concrete surge box is cracked and is not holding any effluent. It will need to be replaced. The 10 port d-box was in good condition. All 5 header lines were camera snaked and were clear. The drain field was probed and dry. At time of inspection the septic system is not in working condition. The surge box will need replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
01/20/2023 |  | RoutineScheduled | 07-113-327 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/20/2023 | 12:00 AM
09/11/2023 | Alternative | Follow-Up Component Maintenance | SP-04-958 | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced lower portion of headers 2, 3 & 4. Found line 1 EZ Flow crushed. Need permit by M&M to replace line with pipe and gravel. Jet cleaned lines 2, 3 &4. Replaced old RSV with new style RSV. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/02/2023 | 05:18 AM
10/11/2023 | Alternative | RoutineScheduled | 199-19-0007 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Clearstream |  | Pump | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | 12:00 AM
03/15/2023 | Alternative | RoutineScheduled | 159-11-161 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | [] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
08/09/2023 | Alternative | Reportable Incident Component Maintenance | 153-STS-20297 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired fittings in hydraulic unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Level Sensor Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
11/30/2023 | Alternative | Routine/Scheduled | 159-13-0068 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level Has 1" of solids with 4" of sludge Pulled and cleaned filter -Discharge/Pump Tank: At normal level Pump and floats working properly -Peat Moss: Tipping bucket and trays intact and working Peat in decent shape, Raked out peat -Control Panel: Panel working properly Discharge pump pulling 8.53amps -Distribution Box: At grade At normal level -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 04:03 PM
09/28/2023 | Alternative | Routine/Scheduled | 147-08-0051 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Found at normal level, 6in of sludge and less than 1in of solids. -Aeration: Found at normal level, 4in of suspended sludge. Could hear treatment tank working as it should. -Air Pump/Blower: Pulled and cleaned air filter. Air pressure sensor working as it should. -Control Panel: 120 volts audio and visual alarms working as they should. Air pump pulled 1.5 amps -Distribution Box: Found at normal level, 6 lines balanced and taking water. Removed small roots while on site. Dbox lid has a hairline crack -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | Dec 30 1899 9:09AM
03/14/2023 |  | RoutineScheduled | 107-06-0771 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Gravity | Drip |  |  | ["Auxiliary Filter","Dispersal System Operation"] | ["Auxiliary Filter","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 12:00 AM
10/03/2023 | Alternative | RoutineScheduled | 061-STS-24247 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | system check okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/21/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-88908 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Alarm float was not working due to bad connection, cleaned wires and put new wire nuts and started working. HL-190, LL-90, OVERRIDE-134. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
08/08/2023 | Alternative | Routine/Scheduled | 228-12-0542 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | Dec 30 1899 11:30AM
02/21/2023 |  | Reportable Incident | 107-14-0304 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | YES | Musty | Clear | [15 empty] | Replaced blower | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/08/2023 | 12:00 AM
05/04/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Whitewater ATU |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [16 empty] | Inspected | Sludge level-minimal scum-4=5" sludge trace in Septic tank - Tank level low, No Occupancy- Treatment tank 24" sludge, No scum- Clear on top,Good aeration heard But water at low level - No Use- no Flow. Cleaned Blower Airfilter, Tested blower alarm which sounded and is operational. Drainfield is overgrown with pine trees and needs cutting. System appears as unused and fully functional at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/05/2023 | 09:30 AM
08/16/2023 | Alternative | RoutineScheduled | 139-17-0106 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | AquaSafe |  | Pump | Pressure | Drip | Not Applicable | 150.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Control Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [17 empty] | Compressor was replaced on 09/01/2023 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | 12:05 PM
04/06/2023 |  | RoutineScheduled | 153-STS-20345 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"Disinfection" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Disinfection" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
11/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/20/2023 | 02:30 PM
07/07/2023 | Alternative | Reportable Incident | 154-17-0377 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 0-3 | 0-3 0-0 | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear |  |  | 6.000000 | [11 empty] | Inspected | replaced linear air compressor | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/02/2023 | Alternative | Routine/Scheduled | 05-160-0397 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/02/2023 | 01:30 PM
09/05/2023 | Alternative | Routine/Scheduled | MS39 Lot 17A | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [13 empty] | Replaced aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | Dec 30 1899 11:20AM
11/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1500 |  |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 | ["Other","Dispersal System Operation"] | ["Other","Dispersal System Operation"] | YES | [16 empty] | Pumped Out | dug up 2nd distribution box and adjusted flow diverter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/15/2023 | Dec 30 1899 2:40PM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
03/18/2023 | Alternative | RoutineScheduled | SD-10-196 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2000 | Septic | Microfast | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | YES | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/11/2023 | 07:30 AM
05/26/2023 |  |  | 033-STS-87113 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
05/26/2023 |  | RoutineScheduled | 132-06-0053 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Discharge | Chlorination | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/28/2023 | 12:00 AM
04/06/2023 |  | Routine/Scheduled | 550-STS-6827 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/06/2023 | Jan 1 1900 2:00PM
11/08/2023 | Alternative | RoutineScheduled Component Maintenance | 015-STS-339032 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 11/08/2023 |  | 12.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
09/21/2023 | Alternative | RoutineScheduled | 182-18-0181 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 RT |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles","Recirculation Pump"] | ["Septic Tank Baffles","Recirculation Pump"] | [18 empty] | baffle and pump intake were clogged | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/21/2023 | 12:00 AM
08/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1200 |  |  | Pump | Gravity | Pad | Not Applicable | 750.000000 | ["None"] | ["None"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/21/2023 | Dec 30 1899 3:10AM
05/25/2023 | Alternative | RoutineScheduled Component Maintenance | 033-06-0500-SP | Caroline | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["Recirculation Pump" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | The manual headworks box appears to be under the walkway between the tanks and the dispersal area. This will need to be located so we can service the spin filters. Fence posts have been driven through drip tubing in several locations. This will need to be excavated by hand and repaired. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/03/2023 | 05:43 AM
10/30/2023 | Alternative |  | 033-09-0059- | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/24/2023 |  | Reportable Incident | 234-09 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [17 empty] | Replaced float and pump | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/24/2023 | Jan 1 1900 8:00AM
10/03/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Septic Tank-4"sludge 4"scum/ Microfast-4"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-2493 ETM-2147h/ Peak-21 bETM-390h / High-11/ Watermeter-0,434,204.44 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/28/2023 | Alternative | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [6 empty] | Distribution Pump Operation | Distribution Pump Operation | N/A | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/27/2023 | 12:38 PM
04/08/2023 |  |  |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 1.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/22/2023 | 12:00 AM
10/24/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Gravity |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/24/2023 | Dec 30 1899 10:15AM
11/17/2023 | Alternative | Routine/Scheduled | 08-120-0469A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Microfast |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/17/2023 | Dec 30 1899 8:53AM
10/31/2023 | Alternative | Reportable Incident | 136-07-0481 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Customer stated alarm was going Opened system and noted The Pump was bad Also noted the Panel and Floats are Aged And the concrete Pump chamber riser is below grade Gave solutions to rosey and she approved Pump only. Replaced pump on site. System functioning properly upon departure | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | 09:18 AM
11/06/2023 | Alternative | Routine/Scheduled | 151-18-0051 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | 01:32 PM
12/20/2023 | Alternative |  | 101-08-0093 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Mike | Sipe | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/22/2023 |  | Routine/Scheduled | 19-120-0152AR | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | The treatment tank needs to be pumped | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/22/2023 | Jan 1 1900 10:37AM
01/19/2023 |  | RoutineScheduled | SWP-05-189 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["SludgeScum Accumulation" ,"Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Treatment looks good in treatment zone of atu, but lots of suspended "chunks". Due to poor access for pumping, recommend a pump out before it gets much worse. Homeowner will run water in house 4 to 5 hours afterwards to refill the tank with clean water. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
09/14/2023 | Alternative | RoutineScheduled | 145-17-0017 | Highland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | AdvantexAX20RT | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The textile sheets were sprayed off. The recirculating and discharge pumps were both pulled and sprayed off. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | 10:30 PM
01/17/2023 |  | RoutineScheduled | 177-STS-89709 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
04/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
07/18/2023 | Alternative | Initial Visit | 550-STS-6786 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 18.000000 |  | 2.000000 | [5 empty] | Owner called due to the yellow light being on. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The grade on the pipe in the Clearstream is not okay - adjusted it - needs to be addressed and/or fixed. Could not locate the drainfield. The timer is set to 5 minutes every 2 hours. Took initial BOD and Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/18/2023 | Dec 30 1899 1:30PM
10/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Drainfield leak repaired | This AOSS should now return to normal function after having provided the above state routine maintenance | 11/22/2023 | 09:18 AM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance | SD-07-138 | Orange | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | There is broken plumbing next to the Zone 1 air release valve that should be repaired. There appears to be a wet area near where the Zone 2 air release valve is located. We recommend excavating & repairing this area. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/03/2023 | 05:43 AM
01/09/2023 |  |  | 132-08-0214 | Fluvanna | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2500 | Delta Whitewater |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation","Other"] | YES | Musty | Cloudy | [14 empty] | Pumped Out | Septic and Treatment Tank Pumped Aerator Rebuilt Check Valve Seal Replaced | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/09/2023 | 10:00 AM
01/16/2023 | Alternative | RoutineScheduled | 151-13-0029 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1200 | Microfast |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/17/2023 | 12:00 AM
12/07/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-23623 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/07/2023 | 12:00 AM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/05/2023 | Alternative | Routine/Scheduled | 166-11-186 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 5.000000 | 10000 | Norweco Singulair ATU |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 07:09 PM
03/27/2023 |  | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [6 empty] | Distribution Pump Operation | Distribution Pump Operation | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/18/2023 | 03:28 PM
06/27/2023 | Alternative | Routine/Scheduled | 145-STS-259186 | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/27/2023 | Dec 30 1899 4:23PM
05/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/03/2023 |  | RoutineScheduled | 179-13-0174-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Control Operation" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Top line is not taking water took it out of service to let it dry, will put it back in service next year to see if is dry. Mother board had lost settings for discharge , put original seed back to 1.3 on and 120.0 off. Recirc tank most likely will need pump out next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 09:31 AM
01/31/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.700000 |  | 10.000000 |  |  | 01/31/2023 |  | 2.000000 |  |  | 5.600000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2023 | 08:00 AM
05/19/2023 |  | RoutineScheduled | 175-13-0325 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/18/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 01/18/2023 |  | 42.000000 | [5 empty] | Will be sent separately | Inspected | snake outside riser filter clog | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
06/19/2023 | Alternative | Follow-Up Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced peat in Puraflo modules. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/17/2023 | Dec 30 1899 12:46PM
04/06/2023 |  | RoutineScheduled | 04-100-0821 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 3.000000 | 6600 | ECOFLO |  | Pump | Gravity | Pad | Not Applicable | 2100.000000 | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | PUMPS AND ALARMS WORKING-PEAT LOOKS GOOD IN ALL 4 PODS-REPLACED 4 ECLOFLO VENTS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/24/2023 | 12:00 PM
04/05/2023 |  | RoutineScheduled | 132-02-0389 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Drip | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/08/2023 | 12:00 AM
03/31/2023 | Alternative | Reportable Incident | S-05-111-0156 | Botetourt | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1200 | Biomicrobics Fast |  | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation","BlowerCompressorAerator Operation","Level Sensor Operation"] | ["Control Operation","Level Sensor Operation"] | NA | [16 empty] | Inspected | Initial Visit- Owner was reffered to us by Affordable who had pumped out the treatment and discharge tanks. Upon arrivial the level sensor was dismantled and pump not operating, Blower was locked up, filter very dirty and had not been serviced for many years. Both tanks are buried about 8 inches below grade and possiblly may have water infiltration during rain. Reccomeded to owner to trench and /or lower grade. add berm or ditch to direct run off away from the septic system. A new Blower motor has been ordered and will be installed shortly. We filled the pump tank and reassembled the rk series lvel sensor, upon adding water it appears to run as it should and the pump ran when called on time dosing. The drip system appears to reach 20psi and both zoners and air relief valves are operational. Upon replcement of the blower it should be fully operational minus any infiltration or over recirculation which will need to be addressed if so. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/03/2023 | Jan 1 1900 9:30AM
11/13/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | Dec 30 1899 8:40AM
10/10/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 8.330000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 03:45 PM
09/28/2023 | Alternative | Initial Visit | 095-STS-6793 | James City | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Peninsula | Hutchens Septic Services LLC | 1942001509 | Robert | Hutchens, Jr. | 1.000000 | 1250 | EZ Treat |  | Pump | Pressure | Drip |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear | [15 empty] | System was pumped in order to replace bad recirculating pump. Effluent is surfacing in the drip field. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/27/2023 | 12:00 AM
05/23/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | ["BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed new Aquarobic blower. Repaired broken force main in pump tank. Reprogrammed computer in control panel. Installed lock out tag on control panel. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Lower line might be receiving slightly more effluent than the other lines. Recommend uncovering Distribution Box and re-leveling if necessary | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/26/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Quanics |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation","Control Operation"] | ["Level Sensor Operation","Control Operation"] | NA | [16 empty] | Inspected | Had Steven Myers dig and try to locate the Dbox, located electrical conduit and a 2 in pipe. D box maybe under the driveway. More to be determinded | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
08/24/2023 | Alternative | RoutineScheduled | 195-STS-26571 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  |  |  | Pump | Pressure | Discharge | UV | 200.000000 | ["Attached Growth Medium","Disinfection","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Disinfection","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/24/2023 | 12:00 AM
12/28/2023 | Alternative | RoutineScheduled | 182-14-0227 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Pressure | Trenches | Not Applicable |  | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | There is no power getting to the Norweco control panel. Aerator/alarm are not functioning due to this. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Trees have been recently planted on/near the end of the drainfield lines. The homeowner is contacting the landscaper to remove the trees and an installer to assess and repair the lines in the appropriate manner. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
03/20/2023 |  | RoutineScheduled | 175-16-0197 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
10/10/2023 | Alternative | Pump-Out Only | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim septic and pumping | 1942001330 | Michelle | McKim | 2.000000 | 1250 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/10/2023 | Dec 30 1899 9:00AM
11/22/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out. -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and found middle float has failed. Flushed and cleaned effluent screen. Recirculation pump has exceeded life expectancy. Recirculation pump plumbing has exceeded life expectancy. Recirculation floats have exceeded life expectancy. -RSV (Recirculating Splitter Valve): Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. Discharge pump has exceeded life expectancy. Discharge floats are not properly secured. Discharge floats have exceeded life expectancy. Discharge pump and floats power leads pass between tank and riser. -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Checked and confirmed spray height is good -Control Panel: Upon arrival, I found that programming had defaulted. Programmed control panel for proper operation. Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact. -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | Dec 30 1899 9:16AM
10/09/2023 | Alternative | Routine/Scheduled | 157-10-0105 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 8 minutes every 1 hour. No valve boxes - could not locate vacuum breakers. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | 03:15 PM
04/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/09/2023 | Alternative | Routine/Scheduled |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - normal level - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 09:45 AM
09/19/2023 | Alternative | RoutineScheduled | 08-197-A4 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Multiflo |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/19/2023 | 12:00 AM
10/19/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/22/2023 | 12:00 AM
05/20/2023 | Alternative | Routine/Scheduled | 127-STS-34598 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/20/2023 | Dec 30 1899 11:00AM
03/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
11/08/2023 | Alternative | RoutineScheduled Component Maintenance | {FIPSCode}-STS-6368 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["SludgeScum Accumulation" ,"Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS should now return to normal function after having provided the above state routine maintenance | 12/01/2023 | 10:33 AM
10/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Septic | Clear | [13 empty] | Will be sent separately | Inspected | Air line is broken. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/13/2024 | 05:34 PM
01/06/2023 |  | RoutineScheduled | 132-14-0067 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | AquaSafe |  | Gravity | Pressure | Drip | Not Applicable | 500.000000 | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | 12:00 AM
09/13/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
12/08/2023 | Alternative | Pump-Out Only | 121-STS-12411 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner |  |  | AQUASAFE / DIRECT DISCHARGE | [6 empty] | [] | [] | [17 empty] | Pumped Out | Pumping & Cleaning Alternative Pretreatment Tank (1000 gallons) JOB SCOPE: Pumped/cleaned septic tank; septic system is functioning at this time but not as designed as there are components that are recommended to be repaired/replaced. - system is Aquasafe / Direct Discharge - another company completing repairs on system | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/11/2023 | 12:00 AM
09/22/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  | Ecoflo |  | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Distribution Pump Operation","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 12:00 AM
05/04/2023 | Alternative | Routine/Scheduled | SHUN-AV5Q6V | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash Tank - normal level Aeration Tank - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. UV - bulb and housing serviced. Drip - headworks serviced. Mound - no surfacing noted. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | Dec 30 1899 7:30AM
09/21/2023 | Alternative | RoutineScheduled Component Maintenance | SD-02-302 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Level Sensor Operation"] | ["Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Puraflo modules holding water. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | 12:58 PM
11/30/2023 | Alternative | Routine/Scheduled | 03-160-0520 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/30/2023 | 10:30 AM
05/05/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Multiflo ATU |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Septic tank trace scum layer and 12 in sludge layer. <ultiflo has a trace and looks good. Pump tank has 14" sluidge and pump good. Multiflo Aerator pump running good. Alarm and silence button both function. RK pump panel has proper depth gauge and 40 psi on drainfield when running and pressuriser. 15.5 in on depth gauge, Cleaned spin filter. clear effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 12:30 PM
04/10/2023 |  |  | 2004-143-0306 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Ecoflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
10/30/2023 | Alternative | RoutineScheduled Component Maintenance | 179-10-0093-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Drip rate has slowed down and system had a lot of growth in microfast tank due to products being used in the laundry. Home owner made arrangements to get tank pumped out. Spoke with home owner about dos and donts. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
05/11/2023 |  | RoutineScheduled | 177-06-0016-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. No more filamentus bacteria. Treatment is crystal clear. Blower 3.26 amps | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
03/27/2023 | Alternative | RoutineScheduled | 109-STS-31736 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1000 | EZ Treat |  | Pump | Pressure | Trenches |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 12:00 AM
04/13/2023 |  | RoutineScheduled | 10-192-200 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Discharge | UV | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Level Sensor Operation","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation","Disinfection"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/13/2023 | 12:00 AM
01/18/2023 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/07/2023 | 11:47 AM
09/14/2023 | Alternative | RoutineScheduled Component Maintenance | 061-16-250 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation"] | ["Control Operation"] | NA | Septic | Cloudy | [13 empty] | Will be sent separately | Inspected | Biweekly inspection. Noticed that blower #1 sounded funny and no bubbling was taking place. Used camera to verify that the airline coupling at the splash plate was broken in half. Shut down atu #1, switched valves to deliver influent to atu #2, and powered up blower #2. Will send repair estimate to the airport manager. Drip panel high level count at 52, low level alarm count at 496. In the past 24 days, system has pumped an average of 1603.3 gals/day at 432.3 gals/dose (avg.) for a total of 38,481 gallons. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
04/03/2023 | Alternative | Routine/Scheduled | S 093-19-0082 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | Dec 30 1899 8:00AM
12/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired air supply line | This AOSS should now return to normal function after having provided the above state routine maintenance | 01/15/2024 | 10:39 AM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/10/2023 |  | RoutineScheduled | {FIPSCode}-STS-83761 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | ["Distribution Pump Operation" ,"Dispersal System Operation" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | There are four air release valve lids that need to be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
01/25/2023 |  | Routine/Scheduled | 228-18-0017 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/25/2023 | Jan 1 1900 10:45AM
10/26/2023 | Alternative |  |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/03/2023 | 12:00 AM
01/18/2023 |  |  | 17-142-0112 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Replaced clearstream blower | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/03/2023 | 12:00 AM
02/15/2023 | Alternative |  | 101-17-0214 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Frank | Bergland | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/01/2023 | Alternative | RoutineScheduled | 133 10 0206 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 2000 | EZ Treat |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Second quarter 2023 inspection. Cleaned recirculation tank filter. Tested floats, pumps and alarm. Spray heads spraying very good. Restaurant is on a regular grease trap pump out schedule. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | 07:03 PM
04/17/2023 |  | RoutineScheduled | 177-10-0105-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Distribution Pump Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend pumping the septic tank, aerobic treatment unit and pump tank due to scum & sludge accumulation in the tanks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
10/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
03/13/2023 |  | RoutineScheduled | 101-16-0472 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/19/2023 | 12:00 AM
01/31/2023 |  | Pump-Out Only | 550-STS-5876 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | Jan 1 1900 9:00AM
08/25/2023 | Alternative | Initial Visit | 093-STS-14037 | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 5.000000 |  | 1900.000000 | [5 empty] | Owner called due to an alarm. Serviced system. Checked the panel and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Replaced the relay and wired the pump through the pump float - pump was running 24/7. Flushed out the weir filter. Need to pump and clean the pump tank and pump trash out of the Clearstream tank when doing so. The timer is set to 8 minutes every 2 hour. Took initial BOD and Fecal samples. NOTE - Fecal sample was high - system should function properly after service. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/25/2023 | Dec 30 1899 10:30AM
05/01/2023 | Alternative | Initial Visit | 157-13-0052 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | AOSS - Initial visit - Alarm event - overflowing from tanks. Found discharge pump failed - pumped discharge tank empty and removed 500 gallon from septic tank for storage. Septic Tank - "T' intact. Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - Replaced discharge pump - float sensors & controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | 06:45 AM
10/06/2023 | Alternative | RoutineScheduled Component Maintenance | 175-08-0072 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Noticed at time of inspection drainfield trench lines are all browned over. I can not see any record of repair or adding of any dirt. Due to this it is recommended to dig up d boxes to further investigate drainfield. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/15/2023 | 02:02 PM
02/23/2023 |  | Routine/Scheduled | {FIPSCode}-STS-4829 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  |  |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/23/2023 | Jan 1 1900 3:05PM
03/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
05/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/06/2023 |  | RoutineScheduled | 179-08-0262-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | As noted on last year's inspection, we recommend replacing the top riser section & riser lid on the septic tank. We also noted that the peat is settling, but it remains in good condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
04/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/21/2023 |  | Initial Visit | 1182-94-0516 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Trenches |  |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Blower replaced and FAST unit dug off and blockage cleared. Septic pumped | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/11/2023 | 12:00 AM
12/02/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Fairfax | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation","Distribution Pump Operation"] | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | NA | Musty | Clear | 6.900000 |  |  | 2.100000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/11/2023 | 12:00 AM
09/26/2023 | Alternative | RoutineScheduled | 02-113-265 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 8 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/26/2023 | 12:00 AM
09/27/2023 | Alternative | Routine/Scheduled | 810-STS-3963 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/27/2023 | Dec 30 1899 11:15AM
08/03/2023 | Alternative |  | 17-100-0507 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/11/2023 | Alternative | RoutineScheduled | 2012-143-0034 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/03/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | BioWheel |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | September 2023 monthly report. Total flow for month of September 2023 - 69,066 gallons. Average daily flow- 2,302 gallons per day. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | 07:03 PM
05/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/23/2023 | 09:32 AM
11/02/2023 | Alternative | RoutineScheduled | 115-13-0326 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Norweco Singulair ATU |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | [17 empty] | Inspected | First inspection since new ownership about 2 years. Septic zone had 6" scum layer and 18" sludge and recommend to pump out asap. Cleanen effluent filter it was very dirty and had backed up a few inches in the unit. Arranged Foutz to Pump out of treatment unit for the next day. cleaned effluent filter. aerator good and alarm good. System appears as fully operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 05:30 PM
10/24/2023 | Alternative | Reportable Incident | 097-STS-96191 | King & Queen | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | System was at normal level. System has a very strong sewer smell. The bacteria in the system has died and is what is causing the smell. Sent estimates over. Ran camera in sewer line to make sure there were no bellies in the line and found none | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 04:21 PM
05/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 2.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/30/2023 | 10:30 AM
07/03/2023 | Alternative | Follow-Up Component Maintenance | 179-07-0058-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Resealed pump tank wedge lid. Water softener on septic, referred plumber. Advised homeowner to stop using fabric softeners. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 04:50 AM
11/10/2023 | Alternative | RoutineScheduled | 08-135-3128 | Giles | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | King's Alternative Septic | 1942001112 | William | King, II | 1.000000 | 1000 | BioMicrobics Retrofast 0.5 |  | Gravity | Gravity | Discharge | UV | 200.000000 | ["None"] | ["None"] | YES |  |  | 6.910000 | 7.780000 |  |  |  | 10/05/2023 |  |  |  |  | 3.700000 |  |  | Attached to this report |  | System is working correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2024 | 12:00 AM
10/11/2023 | Alternative | Initial Visit | 093-STS-14632 | Isle Of Wight | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the panel (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed a new P-20 pump (new serial # 2203-134275). Installed a 3/4" brass check valve. Replaced the relay in the panel wired pump through the pump float. There is visible wetness on the drainfield - the pump had been running 24/7 due to the relay. Once it dries up need to keep an eye on it. The timer is set to 1.5 minutes every 2.5 hours. Did not take samples. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/11/2023 | Dec 30 1899 10:00AM
03/16/2023 | Alternative | RoutineScheduled | 159-STS-95859 | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/19/2023 |  | Routine/Scheduled | 2017-143-0030 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Meet with the pumping company and pumped and cleaned the Clearstream tank and pump tank. Disconnected the pressure switch on the aerator and cut the UV off due to the pumping of the tanks. The timer is set to 6 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/19/2023 | 01:45 PM
12/06/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Ecoflo |  |  | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles"] | ["Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 12:00 AM
12/27/2023 | Alternative | RoutineScheduled | 001-STS-92742 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | JEFulbright Septic, LLC | 1942001131 | Jason | Fulbright | 1.000000 | 1000 | Fuji Clean | Chlorine Disinfection | Pump | Gravity | Trenches | Chlorination | 500.000000 | [] | [] | NA | Musty | Clear | 7.250000 | 3.280000 |  |  |  | 12/27/2023 | Pump Chamber | 2.000000 |  | 0.000000 | 4.000000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/04/2024 | 12:00 PM
04/19/2023 |  | Reportable Incident | 234-14-295 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/19/2023 | Jan 1 1900 1:00PM
08/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 08/07/2023 |  | 49.000000 | [5 empty] | Will be sent separately | Inspected | Replaced 2 pressure gauges | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
05/30/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/30/2023 | 09:36 AM
10/12/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Pump | Pressure | Drip |  | 600.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 11:43 AM
10/18/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Ecoflo |  | Pump | Gravity | Trenches |  | 650.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/19/2023 | 10:56 AM
01/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
11/06/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-88980 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"Attached Growth Medium"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"Attached Growth Medium"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
06/09/2023 | Alternative | Pump-Out Only | 03-160-0379 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [17 empty] | Pumped Out | - system appears to be functioning however it is recommend for repair/replacement of the inlet and outlet lines | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 12:00 AM
07/27/2023 | Alternative | Routine/Scheduled | 136-18-0290 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | Routine Service Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - plastic - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | 07:30 AM
03/19/2023 |  | Reportable Incident | 177-15-0220-SR | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to discharge pump not pumping. Neutral wire for pump burnt and came disconnected. All wire connections in discharge junction box were redone. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
01/10/2023 |  | Routine/Scheduled | 10-142-0276 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | EcoPod |  | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [17 empty] | Air filter cleaned. System inspected. System appears to be operating normally. Septic tank is due for pumpout in March. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | Jan 1 1900 12:50PM
06/20/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was replaced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/06/2023 | Alternative | Initial Visit | VAG401959 | Augusta | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Gravity | Discharge | Chlorination |  | ["Attached Growth Medium","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | elevated level in FAST. Blower running hot (232F). No discharge at this time | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/06/2023 | 12:00 AM
12/07/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/27/2023 | 01:45 PM
08/03/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-90067 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Disinfection" ,"Attached Growth Medium"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Disinfection" ,"Attached Growth Medium"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Replaced uv bulb. Grease accumulating in septic tank. Gave customer copy of Do's and don'ts. Headworks always full of water need to clear drain line. RECIRC: HL-3, LL-19, OVERRIDE-591. DISCHARGE:HL-2, LL-16, OVERRIDE-4. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
03/30/2023 |  | RoutineScheduled | 107-11-0200 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [9 empty] | [] | [] | YES | None | Clear | 7.710000 |  |  |  |  | 03/30/2023 |  | 5.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 02:30 PM
10/31/2023 | Alternative | RoutineScheduled | 182-05-0081 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
02/15/2023 |  | RoutineScheduled | 175-15-0089 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | [17 empty] | Septic-10"sludge 6"scum/ Microfast ATU-12"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time but the Septic-Microfast Tank may need pump out next year due to sludge levels/ Controls, pump, floats and alarms functioning properly/ Blower air filter cleaned and blower working properly/ Counts: Pump Run Time-1471 cc-22532 On-5m 58s Off-1h 54m/ High-13/ Swith to hand-55/ Watermeter-0,358,120/ Drip rate 4.4gpm/ Replaced UV-Light Bulb and cleaned the sleeve/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
04/20/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | Jan 1 1900 12:48PM
04/14/2023 |  | RoutineScheduled | 09-120-0056A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 2200 | 1000 | 1000 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","SludgeScum Accumulation","Effluent Screens","Distribution Pump Operation","Level Sensor Operation"] | YES | Pungent | Discolored | 6.000000 |  | 5.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | Jan 1 1900 11:00AM
02/21/2023 |  | Initial Visit | 107-05-0748 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Gravity | Trenches |  |  | ["Septic Tank Baffles","Dispersal System Operation"] | ["Septic Tank Baffles","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/21/2023 | 12:00 AM
01/20/2023 |  | RoutineScheduled | 196-04-414 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Assure Plumbing & Septic LLC | 1942001502 | Assure | LLC | 2.000000 | 1000 | Puraflo |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | ["None"] | ["Control Operation","Distribution Pump Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/20/2023 | 05:15 PM
06/16/2023 | Alternative | RoutineScheduled Component Maintenance | 061-18-175 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Clearstream | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"Effluent Screens" ,"BlowerCompressorAerator Operation"] | YES | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Effluent appeared clear, but not necessarily crystal clear. Cleaned air filter with compressed air. House is now rented out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
10/30/2023 | Alternative | RoutineScheduled | 08-197-A13 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  | ["Disinfection"] |  |  | None | Clear | 6.500000 | 7.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
11/20/2023 | Alternative | RoutineScheduled | 175-13-0323 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ Microfast ATU | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-12"sludge 2"scum/ Microfast-16"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ Pump out required on the Septic-Microfast Tank/ Blower air filter cleaned and blower functioning properly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-17869 ETM-1776h/ High-19/ On-6m 9s Off-1h 5m/ Watermeter-066060/ Zone1-5.6/ Zone2-5.5/ Zone3-5.7/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/23/2023 | Alternative | RoutineScheduled | 107-07-0558 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  |  | Trenches |  |  | ["Septic Tank Baffles"] | ["Septic Tank Baffles"] | [18 empty] | Bio Tube filter was clogged causing alarm | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/23/2023 | 12:00 AM
08/03/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Gravity | Pressure | Drip | UV |  | [] | ["Auxiliary Filter","Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Dispersal System Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/06/2023 | Dec 30 1899 4:30PM
04/07/2023 | Alternative | RoutineScheduled | 061-STS-24826 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Distribution Pump Operation"] | ["Control Operation" ,"Level Sensor Operation" ,"Distribution Pump Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Infiltration occurs (during heavy rain) at the makeshift support bars for the recirc pump vault. A repair proposal has been provided to the owner. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
02/03/2023 | Alternative | RoutineScheduled | 166-07-163 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | ["None"] | [18 empty] | Needs access riser for annual inspection of septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/07/2023 | 12:00 AM
10/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
07/11/2023 | Alternative | RoutineScheduled | SP-05-253 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Elite Onsite | 1942001726 | Drew | Saunders | 3.000000 | 1750 | 1000 | 750 | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/13/2023 | 05:30 PM
01/18/2023 |  | RoutineScheduled | 177-10-0047-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"SludgeScum Accumulation" ,"Control Operation" ,"Distribution Pump Operation"] | ["Level Sensor Operation" ,"Control Operation" ,"Distribution Pump Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Scheduled semi-annual inspection/maintenance. Discharge tank in low level alarm due to timer float being stuck on. Replaced the blue Connery float with an Orenco float switch. Grease trap needs pumping, owner to make arrangements. Sludge return pump initially would not pump. Had to clear a clog in the pump line to restore flow. Pumped all but about 3" of scum and sludge back to the grease trap. Reset all "R" counts in the discharge panel back to zero (total to date is maintained). A couple of the sphere cages in the first Nibbler tank (closer to the surge dosing tank) had floated up so that treatment was reduced. Effluent was not as clear as the other Nibbler. Re-positioned the cages and replaced the missing 1" pvc bracing pipes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
07/06/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | Dec 30 1899 12:46PM
10/05/2023 | Alternative | RoutineScheduled | 107-13-0146 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
11/17/2023 | Alternative | RoutineScheduled | SD-03-189 | Madison | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | Micro fast |  | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | YES | Musty | Clear | 7.000000 |  |  | 1.000000 |  | 11/17/2023 | Sample Chamber | 2.000000 | 0.000000 |  | 5.580000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/01/2023 | 08:55 AM
04/21/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Trenches | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
02/13/2023 |  | RoutineScheduled | 11-125-041 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 12 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/13/2023 | 12:00 AM
10/12/2023 | Alternative |  | 195-STS-26562 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.500000 | 7.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/13/2023 | Alternative |  | 033-07-0494-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/07/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 2000 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 11/07/2023 | Sample Chamber | 18.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/12/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Septic zone 12" Scum layer on top & 16-18" Sludge layer on bottom, This chambers is full and reccomend to get it pumped, do it first when pumping out the entire tank, the pumper may need a smaller hose to fit into the tank. Fast side port has 16-18" sludge. Clear Effluent, Good aeration. Alarm opperational. Pump operational, pump puts out 20psi to drip drainfield, cleaned drip filter. Drip Dainfield appears dry and unremarkable. The pressure relief valves were fine and appear to opperate.System pump panel was struck by lightning and owner replaced the circuit board, It appears function but display not showing pump cycle and pump time any more, may need to relace screen to get dispay to work. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
10/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Distribution Pump Operation"] | ["Attached Growth Medium","Distribution Pump Operation"] | YES | [17 empty] | Septic Tank-4"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Puraflo Peat ponding in all 5 modules, turned the peat and peat all drained properly/ Recommend Puraflo Peat be replaced next year/ Found broken male adapter on pump #1 and was replaced during inspection/ Counts: Pump1-020657 ETM-005581/ Pump2-02062 ETM-0056848 On-1m 4s Off-6h / No breakout or spongy areas on the drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/01/2023 | Alternative | RoutineScheduled |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 |  | EZ Treat |  | Pump | Pressure | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 12:00 AM
01/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/18/2023 |  | RoutineScheduled | 043140080 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | None | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 08:45 AM
03/15/2023 |  | Reportable Incident |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Ecoflo |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None |  | 6.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | Jan 1 1900 8:00AM
02/15/2023 |  | Routine/Scheduled | 15-142-0057 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 150.000000 | ["Control Operation","Dispersal System Operation","Effluent Screens","Recirculation Pump"] | ["Disinfection","Dispersal System Operation","Effluent Screens","Recirculation Pump"] | YES | [17 empty] | There were no overrides in the past 30 days The Advantex manifold was flushed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/15/2023 | Jan 1 1900 1:35PM
04/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NO | [7 empty] | 04/20/2023 |  | 4.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | Dec 30 1899 12:48PM
05/08/2023 |  | RoutineScheduled | 181-02-0215 (LEGACY ALT. SYSTEM) | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | Sand Filter | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The spin filter was cleaned. The sand filter was operating as designed. There were no visible leaks in the drip field. There was effluent returning to the pump tank so the drip field was operating as designed. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/03/2023 | 12:05 PM
02/20/2023 | Alternative | RoutineScheduled | 137-STS-21209 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
07/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic/ Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-6"sludge 0"scum/ Microfast-10"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Blower controls and alarm is functioning properly/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/15/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"Recirculation Pump"] | ["Auxiliary Filter"] | NA | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | Dec 30 1899 12:58PM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance | 165-STS-334525 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 10/03/2023 |  | 8.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
07/18/2023 | Alternative | RoutineScheduled | 117-STS-13263 | Mecklenburg | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Southside | Matthews Sanitation Services LLC | 1942001226 | BRIAN | MATTHEWS | 2.000000 | 1000 |  |  | Pump |  | Trenches |  | 450.000000 | ["Other"] | [] | NA | None | [15 empty] | Inspected | SEPTIC TANK WILL NEED PUMPING | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/18/2023 | 12:00 AM
12/04/2023 | Alternative | RoutineScheduled Component Maintenance | 177-07-0050-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["SludgeScum Accumulation" ,"Effluent Screens" ,"Attached Growth Medium"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | The peat in the first three Puraflo modules is starting to hold water. When the peat is replaced, we also recommend excavating and replacing clogged drainage plumbing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
11/15/2023 | Alternative | Routine/Scheduled | 07-160-0103 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable | 141.000000 | None | ["Control Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/15/2023 | 02:00 PM
08/15/2023 | Alternative | Reportable Incident |  | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Dispersal System Operation","Distribution Pump Operation"] | ["Dispersal System Operation","Distribution Pump Operation"] | NO | [17 empty] | Discharge pump failure - System high level - discharge pump failed - replaced with Liberty 250 - system pumped self downon own accord. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/21/2023 | 06:30 AM
07/21/2023 | Alternative | RoutineScheduled | 109-06-0493 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | Trouble Shooting Installed new tank lids and some conduit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/30/2023 | 09:30 AM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/27/2023 |  | Reportable Incident |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Lord Fairfax | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"SludgeScum Accumulation" ,"Auxiliary Filter" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation" ,"SludgeScum Accumulation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Heavy scum accumulation observed in treatment tank and sludge in discharge tank. Both tanks were pumped out by Powell's Plumbing. Washed down manway and piping in tanks. Cleaned air filter and spin filter. Replaced failed Goulds drip pump. New pump running at 12.66 amps. System restored to normal operation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
12/14/2023 | Alternative | Routine/Scheduled | 05-142-0365 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Trash Tank Condition of above Component Notes for above Component Found at normal level, 3in of sludge and 2in of solids. Pulled cleaned rsv and check ball. Recirculation Tank Condition of above Component Notes for above Component Found at normal level, 10in of sludge and less than 1in of solids. Pulled and cleaned pump floats and biotube filter. Tested floats and pump all working as they should. Pump and floats have met life expectancy Discharge/Pump Tank Condition of above Component Notes for above Component Found at normal level, found less than 1in of sludge and solids.. tested floats and pump all working as they should. Pump and floats have met life expectancy Media Sheets Condition of above Component Notes for above Component Sprayed media sheets, brushed laterals. Flushed unit. Locking strut kit and hinges have failed. Control Panel Condition of above Component Notes for above Component 120 volts, tested alarm. Alarm buzzer is unplugged, recirc pump pulled 11 amps Discharge pump pulled 8.11 amps Drain Field Condition of above Component Notes for above Component No signs if surfacing in drainfield area | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | Dec 30 1899 10:06AM
11/29/2023 | Alternative | RoutineScheduled | 14-163-0025 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Clearstream |  | Pump | Pressure | Drip |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/29/2023 | 12:00 AM
03/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
10/03/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.180000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | 12:35 PM
10/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | YES | [17 empty] | Septic Tank-2"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Controls, pumps, floats and alarm function properly/ No counts or etm readings, system is a demand dose LPD Trench System/ No breakout or spongy areas on the LPD Trench area, valves cleaned and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/01/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | UV |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | 8.100000 | 12.900000 |  | 0.000000 |  | 03/01/2023 |  | 22.000000 |  | 1.800000 | 6.000000 |  |  | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/31/2023 | Jan 1 1900 12:26PM
04/18/2023 |  | RoutineScheduled |  | Frederick | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | UV |  | ["Attached Growth Medium","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [17 empty] | septic and microfast tank needs pumped | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/20/2023 | 06:20 PM
09/27/2023 | Alternative | Reportable Incident Component Maintenance | 175-10-0082 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Several alarms last week from the Puraflo dosing tank being in high level. Replaced the timer enabler float switch. Cleaned debris from under both solenoid valve diaphragms. The septic return line tees into the sewer line, so extra water was being recirculated back to the septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
01/11/2023 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | 01:59 PM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance | 179-12-0269-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
05/18/2023 |  | Follow-Up | 234-16-29 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | Disinfection | Disinfection | N/A | [17 empty] | Replaced UV ballast & UV bulb. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/18/2023 | Jan 1 1900 2:00PM
07/28/2023 | Alternative | RoutineScheduled |  | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Garland Easter Septic Service | 1942001206 | Garland | Easter | [9 empty] | ["Effluent Screens","Auxiliary Filter"] | ["Effluent Screens","Auxiliary Filter"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | 12:00 AM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Module closest to the house is ponding. Module second from the house has severe roots. The tank structure appears to be good from the surface view through the risers. The distribution box appeared lower than dialflow openings. Drainfield lines are saturated but not surfacing. Recommend homeowner contact AOSE regarding options for replacement of peat and field. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/12/2023 | 03:17 AM
06/27/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced control floats. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
09/20/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation"] |  | NA | [15 empty] | Will be sent separately | Inspected | Check valve in discharge tank is not functioning allowing effluent to drain back in tank after cycle. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | Dec 30 1899 12:58PM
03/07/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | UV |  | ["Disinfection"] | ["Disinfection"] | NA | Septic | Clear | 7.800000 | 17.300000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/31/2023 | Jan 1 1900 12:26PM
08/17/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 |  |  | Pump | Pressure | Trenches |  | 450.000000 | None | None | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/18/2023 | 11:29 AM
08/16/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
07/19/2023 | Alternative | Routine/Scheduled | 550-STS-6781 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | Dec 30 1899 9:30AM
01/10/2023 |  | Routine/Scheduled | 234-08 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | Jan 1 1900 2:10PM
09/18/2023 | Alternative | RoutineScheduled Component Maintenance | 182-12-0260 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 | 2500 | none | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 09/18/2023 |  | 24.000000 | [5 empty] | Will be sent separately | Inspected | Added riser and pumped primary tank Replaced 6" caps Lab sample normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
07/12/2023 | Alternative | Reportable Incident | 550-STS-6542 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Changed the filter in the aerator and changed the mesh screen in the spinfilter. Cleaned the UV light bulb. Need to pump and clean the pump tank as well as the Clearstream tank and flush tubing with fresh H20. The timer was set to 3 minutes every 2 hours changed it to 10 minutes every 2 hours. Looks like a damp spot on the mound - could be leaking - homeowner needs to keep an eye on it and let us know. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | Dec 30 1899 1:30PM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/10/2023 |  | RoutineScheduled | 175-16-0260 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic/ Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 01/10/2023 | Sample Chamber | 8.000000 | [5 empty] | Attached to this report |  | Septic-4"sludge 2"scum/ Microfast-4"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned/ Microfast blower controls and alarm functioning properly/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/12/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Puraflo | [6 empty] | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/12/2023 | 12:00 AM
10/19/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | LPD | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/18/2023 | Alternative | RoutineScheduled | SD-02-195 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2000 | septic | LPD | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | YES | Musty | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/21/2023 |  | Routine/Scheduled | 2007-143-0074 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes and spray grid serviced. Pump tank - float sensors, pumpa nd controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/22/2023 | 09:00 AM
08/23/2023 | Alternative | RoutineScheduled Component Maintenance | VAG408471 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Added mulch to ET bed and cleared Added riser and pumped primary | This AOSS should now return to normal function after having provided the above state routine maintenance | 09/20/2023 | 01:07 PM
06/05/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1000 | Septic tank | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [7 empty] | 06/06/2023 | Sample Chamber | 325.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/05/2023 | Alternative | Follow-Up |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Control Operation","Disinfection"] | ["Control Operation","Disinfection"] | N/A | [17 empty] | Replaced UV control panel and bulb | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/05/2023 | Dec 30 1899 9:00AM
04/20/2023 |  | RoutineScheduled | 07-113-071 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Disinfection","BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","SludgeScum Accumulation","Dispersal System Operation","Control Operation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/20/2023 | 12:00 AM
09/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | pumping recommended of Fuji System Media was clogged but cleared | This AOSS should now return to normal function after having provided the above state routine maintenance | 10/13/2023 | 01:07 PM
07/18/2023 | Alternative | RoutineScheduled | 04-100-0736 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 2.000000 | 5600 | Septic Tank | PuraFlo | Gravity | Pressure | Pad | Not Applicable | 900.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 04:15 PM
05/17/2023 |  | Routine/Scheduled | 234-15-010 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [14 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/17/2023 | Jan 1 1900 12:12PM
04/21/2023 | Alternative | RoutineScheduled | SD-09-10 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
07/24/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | 12:00 AM
01/30/2023 |  | RoutineScheduled | 18-183-088 | Russell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | ATL |  | Gravity | Gravity | Mound | Not Applicable | 200.000000 | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | 12:00 AM
07/27/2023 | Alternative |  | 09-197-A2 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/27/2023 |  | 2.670000 |  |  | 6.130000 |  |  | Will be sent separately |  | BOD: 2.67 TSS: 6.13 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | 12:00 AM
12/05/2023 | Alternative | Routine/Scheduled | 166-11-186 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 07:05 PM
03/21/2023 |  | RoutineScheduled |  | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 03/21/2023 |  | 6.000000 | [5 empty] | Will be sent separately | Inspected | replaced buzzer | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/28/2023 | 02:17 PM
05/31/2023 | Alternative | RoutineScheduled | 182-15-0169 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Aqua Safe |  |  | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/31/2023 | 12:00 AM
03/29/2023 |  | Reportable Incident | 175-15-0274 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic / Ecopod ATU Treatment Tank | Pump Tank | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Service call only: Replaced faulty E-60 Ecopod Blower. Wired and tested system, now functioning properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
04/21/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | On site to complete follow-up repairs. Soil excavated between mechanical manway and blower housing. Installed bulkhead adapters for the airline and mechanical seals for the blower's power cord to provide water-tight connections. Lowered the pump so that the bottom was 10" above tank floor, per design. Cleaned the air pre-filter as preventative maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 06:43 AM
01/09/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | K-Rain was replaced. All zones receiving design dosing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
11/30/2023 | Alternative | Follow-Up | 00-197-A10 | Wise | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 0.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.000000 | 4.000000 |  | 0.000000 | [12 empty] | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | 12:00 AM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/12/2023 | Alternative | RoutineScheduled Component Maintenance | 175-04-0584 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
05/16/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Advantex | Pump | Pressure | Drip | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | 8" of sludge 2" of scum in the inlet side of septic tank. 8" of loose sludge in outlet side. pump tank has 2" of sludge. Cleaned recirculation pump and pipes. All alarms, pump, and floats are operational. Field is dry. Recirc run time is 4689 h, 46843 events discharge run time 858h, 13532 events | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 PM
04/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/14/2023 | Alternative |  | 177-15-0217-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
01/07/2023 | Alternative | RoutineScheduled | SD-09-214 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2000 | septic | EZ-Treat 1200 | Gravity | Pressure | Drip | Not Applicable |  | [] | [] | YES | Musty | Cloudy | [14 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | 09:45 AM
01/18/2023 |  | Routine/Scheduled | 550-STS-5866 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | Jan 1 1900 12:25PM
02/08/2023 | Alternative | RoutineScheduled | 061-16-250 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Control Operation"] | ["Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Biweekly inspection. Low pressure observed while running a test cycle on zone 2 suggested that there was a heavy loss of water somewhere. Walked over the zone with the pump running and found a small amount of effluent surfacing (would not have found it in tall grass!). Will repair after gaining approval to do so. In the past 19 days, the system pumped an average of 1,511.5 gals/day at 350.2 gals/cycle (avg.) for a total of 28,720 gallons. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
09/07/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 12:00 AM
03/13/2023 | Alternative | Reportable Incident | 11-163-0014 | New Kent | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chickahominy | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | ["Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Last known documented service conducted 08/10/2020 - no service agreement in place - ALARM event about wet spot and smell of sewage in yard. Controls and tanks NOT in alarm condition on arrival. DBox intact and all laterals accepting effluent. Wet area and surfacing present at end of laterals. Recommend undergound consult and evaluation for absorption field failure. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/14/2023 | Dec 30 1899 7:00AM
06/23/2023 | Alternative | RoutineScheduled Component Maintenance | 179-18-0444-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/10/2023 | 10:02 AM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance | SD-02-805 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. This system actually has 5 zones. Zone 5 (next to Krain zoner valve) tested at 5.3 (7.9). Zone 3 (farthest from zoner valve) tested at 7.5 gpm which suggest a leak somewhere or some bad emitters. Confirmed solenoid valves were shut, and no wet/soft spots found. Will continue to monitor. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
06/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/12/2023 | 02:06 PM
06/16/2023 |  |  | 033-16-0090-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
02/06/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 2000 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/28/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 09/28/2023 | Sample Chamber | 4.000000 | [5 empty] | Attached to this report |  | Septic Tank-6"sludge 4"scum/ Microfast-12"sludge/ Pump Tank-1"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-700 ETM-28h 35m/ Pump2-681 ETM-27h 47m On-2m 28s Off-6h/ Peak-11 Peak Off-4h 48m/ High-11/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/03/2023 | Alternative | RoutineScheduled Component Maintenance | 175-08-0286 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
12/19/2023 | Alternative | RoutineScheduled | 08-137-0213 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 2.000000 | 2500 | EZ Treat |  | Pump | Pressure | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/29/2023 | 12:00 AM
06/07/2023 |  |  | 033-07-0305-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
05/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/24/2023 | Alternative | Reportable Incident |  | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 300.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | AOSS - VDH Permit 159-23-0073 Pumped septic tank empty - serviced effluent screen Removed spent peatmoss biofilter - replaced with new BioCoir biofilter media. Modified treatment modules with new spray / distribution grid. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/28/2023 | 11:30 AM
05/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
02/14/2023 |  | RoutineScheduled | 08-113-227 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/14/2023 | 12:00 AM
03/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/12/2023 | Alternative | RoutineScheduled Component Maintenance | 099-STS-91700 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Blower 2.80 amps. Treatment crystal clear. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
01/26/2023 |  | RoutineScheduled | 179-16-0092-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
03/25/2023 |  | RoutineScheduled | 133 17 0309 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 4150 | BioMIcrobics MicroFast |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | 1st Qtr. 2023 inspection. Grease trap accumulation - Chamber #1 - 2" crust, 6" bottom. Chamber #2 - 2" crust, 0" bottom. Chamber #3 - skim crust, 30" bottom. Chamber #4 - 4" crust, 8" bottom. Solids in septic tank -3" crust, 24" bottom. MicroFast clarifier- 0" crust, 30"solids. Cleaned blower filter. 14" solids in discharge pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/07/2023 | 07:03 PM
08/09/2023 | Alternative | RoutineScheduled | SD-11-265 / SD-12-340 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Septic Tank | Puraflo | Pump | Gravity | Trenches | Not Applicable | 62.500000 | ["SludgeScum Accumulation","Effluent Screens"] | ["SludgeScum Accumulation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 02:50 PM
08/09/2023 | Alternative | RoutineScheduled | 175-96-0565 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | NO | [17 empty] | Septic Tank-3"sludge 0"scum/ Pump Tank-2"sludge/ No pump out needed at this time/ Noted: System has new control panel and hydraulic unit/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-3060 ETM-382h 55m/ Peak-20 ETM-1011h 58m/ High-21/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/28/2023 | Alternative | Pump-Out Only |  | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | AOSS - pumpout of trash tank as recommended during previous service visit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/31/2023 | Dec 30 1899 6:15AM
09/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation" ,"SludgeScum Accumulation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | 9/14 - Treatment tank pumped by Powell's Plumbing, all sludge and debris removed. Tank had an excessive amount of sludge and a viscous substance. Three diffusers were found to be damaged. Owner elected to replace all as a set. Added a check valve to the manifold to prevent a backup into the blower during high level events. This same viscous substance was found inside the piping when the old diffusers were removed - flushed out before installing new diffusers. Dosing tank was also pumped out. Replaced the clogged spin filter with a clean one. Replaced the spinplate with one that had larger holes for better filter cleaning. Cleaned the air pre-filter. Reset timers. The number 2 timer has had issues twice. Recommended upgrading the controls to today's standards. Began refilling both tanks with fresh water, but flow rate for incoming water was very slow. 9/15 - Finished adding fresh water to the tanks. Added 2 gallons of Septic Scrub to the tanks to try to eliminate the remaining sludge and viscous substance. Checked flow rate on both pumps. Verified excellent aeration from all diffusers. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 06:43 AM
02/09/2023 |  | RoutineScheduled | 099-12-0100-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Return valve had trash inside so it was letting water back to septic, cleaned valve and started working correctly. Gallons per minute Higher than design but no water on surface. Will check next year. Peak counts 999999, etm 3552. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
08/09/2023 | Alternative | Routine/Scheduled |  | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - normal level - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - plastic - root intrusion through seals - should replace seals. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | Dec 30 1899 9:30AM
04/05/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Rejected | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | Discharge sign installed. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/05/2023 | 12:00 AM
03/06/2023 |  | Reportable Incident | 228-14-0349 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm, red light, and smell - they do have a toilet that runs sometimes. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter (old one was split open). The grade on the pipe in the Clearstream is not okay - needs to be addressed. The septic tank needs pumping and when doing so pump and clean the pump tank and pump the trash from the Clearstream tank. There is visible wetness on the drainfield - most likely from rain - once it dries need to keep an eye on it. The timer was set at 8 minutes every 2 hours changed it to 8 minutes every 1 hour. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/06/2023 | Jan 1 1900 12:50PM
04/14/2023 |  | RoutineScheduled | -STS-20144 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
10/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Madison | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Blower is bad and needs further diagnosis with manufacturer. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/15/2023 | 02:02 PM
08/01/2023 | Alternative | Routine/Scheduled | 12-120-0164A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/01/2023 | Dec 30 1899 12:16PM
11/15/2023 | Alternative | Routine/Scheduled | 14-142-0192 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 150.000000 | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | Dec 30 1899 3:15PM
08/18/2023 | Alternative | Routine/Scheduled | 19-120-0237 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Aqua Klear |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/18/2023 | Dec 30 1899 3:25PM
12/20/2023 | Alternative |  | 101-16-0320 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Rebecca | Klaff | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-03-372 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | The peat in your system is aging. Peat replacement may be recommended at next year?s inspection. Also, we recommend replacing the riser lid on the pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
05/01/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | RSV clog tank low level Keep Drainfield and tank area mowed move kennel off field please | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/21/2023 | 03:35 PM
07/17/2023 | Alternative | Routine/Scheduled | 151-14-0099 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3250 | EcoPod |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 10.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 06:00 PM
07/25/2023 | Alternative |  | 195-Discharge-14227 Peaceful Valley Rd. | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/25/2023 |  | 8.030000 |  |  | 3.000000 |  |  | Will be sent separately |  | BOD: 8.03 TSS: 3.00 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/25/2023 | 12:00 AM
11/21/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Rejected | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | 2 air release valves have settled The valve box covers need to be uncovered and raised to protect the valve | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/06/2023 | 09:34 AM
01/12/2023 |  | RoutineScheduled | 195-Discharge-30134 Aistrop Road | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["Control Operation","Disinfection","BlowerCompressorAerator Operation","Auxiliary Filter","Attached Growth Medium","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/12/2023 | 12:00 AM
07/06/2023 | Alternative | Reportable Incident | 550-STS-6650 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Owner called due to an alarm - replaced the UV light bulb. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/06/2023 | Dec 30 1899 12:00PM
07/28/2023 | Alternative |  | -STS-93452 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
05/08/2023 |  | RoutineScheduled | SWP-04-507 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The Advantex recirculation pump has lost strength. The system is not processing at the level necessary for good treatment. Pump replacement is recommended. Also, there appear to be trees growing along the end of the drainfield. We recommend these be removed to prevent roots from growing into the drainfield lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
08/15/2023 | Alternative | Reportable Incident | 019-STS-25797 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | AquaKlear |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | We replaced the old Aquaklear fiberglass treatment tank with a new cement treatment tank, Installed a new blower motor and connected the exhisting pump and float switches and alarms. System is now fully operational | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/24/2023 | 09:30 AM
06/20/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-241 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment is clear. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
10/13/2023 | Alternative | Routine/Scheduled | 093-06-0155 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | Dec 30 1899 8:40AM
02/22/2023 | Alternative | Reportable Incident | 136-09-0106 | Gloucester | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - No Service Agreement - ALARM event. No audible/visual alarm - owner contacted office regarding effluent coming out of riser - no service conducted since 2020. Septic tank - effluent screen clogged - serviced. Owner declined full service on treatment system. Owner declined pumpout. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 02/23/2023 | 07:45 AM
12/13/2023 | Alternative | RoutineScheduled | 107-12-0089 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 09:30 AM
01/27/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Led not working on blower panel neither does silence. Replacement is needed for passing inspection | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/18/2023 | 04:10 AM
03/06/2023 | Alternative | RoutineScheduled | 154-14-0094 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
03/17/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | Jan 1 1900 7:20PM
03/09/2023 |  | RoutineScheduled | SP-03-2003 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | Annual inspection. Owner removed roots from around septic outlet pipe. No recent alarms. Will continue to monitor. Peat is showing its age (close to 20 years old) and is recommended to be replaced before it stops providing any treatment. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
06/27/2023 | Alternative | RoutineScheduled | 109-18-0253 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | AdvantexAX20RT | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent screen was pulled and cleaned. The textile sheets were sprayed off. The recirculating and discharge pumps were both pulled and cleaned. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | 09:35 PM
03/16/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | Dec 30 1899 12:26PM
12/04/2023 | Alternative | RoutineScheduled | 09-142-0136 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/20/2023 | Alternative | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [6 empty] | Distribution Pump Operation | Distribution Pump Operation | [17 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/12/2023 | 02:18 PM
06/02/2023 | Alternative | Initial Visit | 136-01-0303 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Visit Primary septic tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. Dbox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/07/2023 | 12:15 PM
08/30/2023 | Alternative | RoutineScheduled | 177-06-0558-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-2"sludge 2"scum/ Pump Tank-2"sludge/ No pump out needed at this time/ Turned the peat in all 5 modules and a lot of roots in 2 modules/ peat is in good condition at this time/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-18,259 ETM-31179/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/06/2023 |  | Routine/Scheduled | 234-16-272 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | Jan 1 1900 9:00AM
03/07/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | Jan 1 1900 12:26PM
05/09/2023 |  | Reportable Incident | 179-09-0157-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for blower alarm due to failed blower. Replaced blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
10/09/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 04:00 PM
10/20/2023 | Alternative | Reportable Incident Component Maintenance | 099-STS-88900 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Complaint inspection. UV fail alarm. UV bulb was burned out, replaced bulb and reset time counter for bulb. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
08/07/2023 | Alternative | Routine/Scheduled | S 800-18-0112 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | Dec 30 1899 9:42AM
04/07/2023 | Alternative |  | -STS-13559 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2500 | LPD |  | Pump | Pressure | Trenches | Not Applicable |  | ["Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | [] | YES | Septic | Dark Brown | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/08/2023 |  | RoutineScheduled | 175-11-0306 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ Advantex Recirc. Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | [18 empty] | Septic Tank-6"sludge 2"scum/ Recirc-6"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Recirc. Pump intake cleaned and media in good condition/ Controls, pumps, floats and alarms functioning properly/ Counts: Recirc-76648 ETM- 1413.6/ Discharge pump-6647 ETM-304.7/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/21/2023 | Alternative | RoutineScheduled | 115-07-0498 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Effluent Screens"] | YES | Musty | [15 empty] | Inspected | Sludge levels-Scum layer minimal and 12" in. sludge in Septic tank zone -Discharge zone minimal scum and 8" Sludge and Pump basin 5" trace of Sludge in Discharge zone of tank. Cleaned biofilter, Media looks clean, Tested floats and all respond alarm works and ran system in test mode. Recirc pump run tim 972.2 hours and 33439 Cycles, Discharge pump 168.5 Hours and 3516 cycles in history. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
02/10/2023 |  | RoutineScheduled | SWP-03-417 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Metal float bar in Puraflo dosing pump tank is corroded and should be replaced before it falls into the tank. Peat has not been raked since 2019 and was pretty compacted, but no ponding water. Some small roots were growing in the peat below the surface, presumably growing in from the bottom (it's a pad side). Owner says no recent alarms. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
08/23/2023 | Alternative | Routine/Scheduled | 151-16-0027 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 75.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/23/2023 | 05:32 PM
02/04/2023 |  | RoutineScheduled | 133 07 0159 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 3.000000 | 3000 | Orenco Advantex |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. Grease trap - 12" of accumulated grease. Septic tank - 8" of solids crust, 6" of accumulated solids on bottom. 20" of solids in recirculation tank. Most likely the recirculation tank will need to be pumped out next year. Cleaned recirculation pump basket filter. Flushed treatment unit spray manifold. There is some sign of grease making it's way to the treatment unit. Tested floats, pump and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/09/2023 | 07:03 PM
07/26/2023 | Alternative | RoutineScheduled | 05-125-003 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 2 - Blue Crystal tablets installed 14 - Bio Max tablets installed 1 - Discharge sign placed 1 - 210P Control Panel installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/26/2023 | 12:00 AM
01/17/2023 |  | Follow-Up | 234-14-267 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | UV | 450.000000 | ["Disinfection","Septic Tank Baffles","SludgeScum Accumulation"] | ["Disinfection","Dispersal System Operation","Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Supervised pumpout by Goodmans Septic Service as recommended during previous service visit - serviced discharge pump and drip headworks - restored operation to UV disinfection system. System refilled with fresh water for re-start. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/18/2023 | Jan 1 1900 8:45AM
11/01/2023 | Alternative | Routine/Scheduled | 04-120-0418A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level Less than 1" of solids with 12" of sludge Pulled and cleaned rsv Needs pumping -Recirculation Tank: At normal level Has 10" of sludge Pulled and cleaned pump, floats and filter Pump and floats aged -Discharge/Pump Tank: At normal level Pump and floats working properly -Media Sheets: Lid is splitting and has no struts Sheets are stuck together and ponding water Sprayed off sheets and flushed laterals -Control Panel: Panel is working properly but aged Visual and audible alarms working Recirc pulling 11.23amps Discharge pulling 6.92amsp -Distribution Box X2: Both dbox are concrete and at grade Both at normal level No cracks or deterioration -Drain Field: No signs of surfacing or blowouts | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | Dec 30 1899 10:38AM
02/23/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/30/2024 | Dec 30 1899 1:28PM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/16/2023 | Alternative | RoutineScheduled | 09-192-191 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | 12:00 AM
07/07/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0461-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Level Sensor Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Tipping trade was not turning to both sides due to pebble under it stopping it, took care of problem and tested. Everything working good after. Peat was higher on 1 side so I fluffed peat and moved a little bit of peat to lower side to make it even. Peat showing its age but still OK, maybe 2 more years left. Will check next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
04/27/2023 |  | Initial Visit |  | Powhatan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Payment | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Orenco Advantex |  | Gravity | Gravity | Discharge | UV | 450.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Discharge - Initial Visit. Primary septic tank - normal level Processing Tank - normal level - recirc pump RSV, and Effluent screen serviced. Treatment Module - media drapes & spray grid serviced. U.V. - bulb and housing serviced. discharge point clear of debris and free flowing. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/01/2023 | Jan 1 1900 7:00AM
03/23/2023 |  | Routine/Scheduled | 041-STS-261255 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/23/2023 | Jan 1 1900 10:39AM
03/16/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | Dec 30 1899 12:26PM
02/02/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.150000 |  | 40.000000 |  |  |  |  | 40.000000 |  |  | 1.200000 |  |  |  |  | Advised client to have system pumped. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2023 | 08:00 AM
09/07/2023 | Alternative | Reportable Incident | 166-14-003 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | changed out faulty float | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/02/2023 | Alternative | RoutineScheduled | 02-197-091 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Cloudy | 6.500000 | 6.000000 |  | 0.000000 | [11 empty] | Aerator is working, no chlorine or de-clorinator tablets were stocked. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/06/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-87469 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
10/12/2023 | Alternative | RoutineScheduled | 103-STS-96410 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Ecoflo is in poor condition. There is severe root infiltration and a large amount of ponding. The homeowners are going to take the path of replacing the Ecoflo with a modern treatment unit. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
12/13/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | Dec 30 1899 1:58PM
07/06/2023 | Alternative | RoutineScheduled | 107-16-0084 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 1.000000 |  | 0.5 FAST |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | NA | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | 05:15 PM
01/13/2023 |  | Reportable Incident | 175-06-0288 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed N98 effluent pump & 3 control floats. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 11:08 AM
10/10/2023 | Alternative | RoutineScheduled | 166-03-542 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Elite Onsite | 1942001726 | Drew | Saunders | 2.000000 | 2000 | 1000 | 1000 | Pump | Gravity | Pad | Not Applicable | 450.000000 | ["Attached Growth Medium","Effluent Screens"] | ["Effluent Screens","Attached Growth Medium"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | 04:30 PM
02/22/2023 |  | RoutineScheduled | 175-05-0785 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Replaced foam block style air filter. Very minor roots seen at top seam, middle of tank, side closer to driveway. No signs of infiltration and owner says no alarms since last year. Will monitor for now. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
01/31/2023 |  |  | 05-192-030 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/31/2023 |  | 2.440000 |  |  | 1.500000 |  |  | Will be sent separately |  | BOD: 2.44 TSS: 1.50 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/31/2023 | 12:00 AM
01/17/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20464 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [7 empty] | 01/17/2023 |  | 4.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
08/11/2023 | Alternative | RoutineScheduled Component Maintenance | SD-03-13 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Peat is in amazing shape for being 19 years old. Note: owner located, dug up and checked his d-box a few days later. Said it was in good shape. Attached picture is from him. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
08/07/2023 | Alternative | Routine/Scheduled | 800-08-0190 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | Dec 30 1899 11:05AM
12/14/2023 | Alternative | Routine/Scheduled | 16-172-0411A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Septic Tank Condition of above Component Notes for above Component Water level normal. Inlet tee appears to be intact. Flushed and cleaned effluent screen. Not due for pump out. Recirculation Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Discharge/Pump Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats Media Sheets Condition of above Component Notes for above Component Cleaned media sheets. Checked and confirmed spray pattern is good Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Drain Field Condition of above Component Notes for above Component Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | Dec 30 1899 10:07AM
03/14/2023 |  | Routine/Scheduled | 18-142-0215 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Treatment Module - recirc - recirc pump, media drapes & spray grid serviced. Treatment Module - discharge - float sensors, pump and controls operating. Pumps to community absorption field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | Jan 1 1900 9:30AM
09/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and pumping | 1942001330 | Michelle | McKim | 3.000000 | 1250 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 4:00PM
09/26/2023 | Alternative |  | 03-197-A12 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity |  |  | Chlorination |  |  |  |  | None | Clear | 6.000000 | 7.000000 |  | -1.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
03/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The system appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/02/2023 |  | RoutineScheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Dispersal System Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Dispersal System Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 02/02/2023 |  | 51.000000 | [5 empty] | Will be sent separately | Inspected | Repaired puraflo alarm float Replaced cracked valve box lid Upgraded timer Repaired visual alarm | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
02/28/2023 |  | Routine/Scheduled | 228-14-0447 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/28/2023 | Jan 1 1900 11:00AM
05/18/2023 | Alternative | RoutineScheduled | SD-88-411 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1500 | septic | Jet | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | YES | Musty | Clear | 7.000000 | 3.100000 | [13 empty] | Informal | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/08/2023 | 08:45 AM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/07/2023 |  | RoutineScheduled | 179-15-0418-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"SludgeScum Accumulation" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend pumping the Advantex tank due to scum & sludge accumulation in the tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/20/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | DeHaven's Backhoe Service Inc. | 1942001541 | Wayne | Edmonson | 2.000000 | 2500 | Septic tank |  | Pump | Pressure | Trenches | Not Applicable | 225.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/22/2023 | 10:00 PM
05/30/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Fairfax | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump","Level Sensor Operation"] | ["Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump","Level Sensor Operation"] | YES | Musty | Clear | 7.400000 |  |  | 1.600000 |  | 05/31/2023 | Sample Chamber | 2.000000 |  |  | 2.200000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/11/2023 | 12:00 AM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/24/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [7 empty] | 10/24/2023 | Sample Chamber | 6.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/17/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/15/2023 | Alternative | RoutineScheduled | 159-17-0108 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Aquasafe |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | [] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
11/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
05/23/2023 |  | Routine/Scheduled | 2007-143-0135 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Trenches | Not Applicable | 750.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level Processing Tank - RES, recirc pump and effluent screen serviced. Treatment Modules (2) - media drapes & spray grids serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 09:30 AM
02/07/2023 |  | Routine/Scheduled | {FIPSCode}-STS-2015 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/07/2023 | Jan 1 1900 2:06PM
10/31/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-4"sludge 0"scum/ Pump Tank-2"sludge/ No pump out needed at this time/ Controls, pumps, floats and alarms are functioning properly/ Peat turned in all 5 modules and is in good condition/ Puraflo support bars are deteriorated and need replacement/ Counts: Pump1-048,903 ETM-0,089,526/ Pump2-005,691 ETM-0,059,478 On 44s Off-2h/ Dose-30 Gallons/ Pump Rate-41.1 GPM/ No breakout or spongy areas on the Puraflo Pad Area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/28/2023 | Alternative | RoutineScheduled | 015-STS-333692 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.180000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 02:30 PM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance | SWT-01-242 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/07/2023 | 07:22 AM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Gravity | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
08/21/2023 | Alternative | RoutineScheduled Component Maintenance | 179-12-0319-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 2.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles" ,"Level Sensor Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles" ,"Level Sensor Operation"] | NA | Musty | Clear | [5 empty] | 08/21/2023 |  | 13.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Cleaned air blower filter. Replaced pressure switch with new style. Replaced diffuser. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
11/25/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | BioMicrobics MicroFast |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 20" of accumulated solids in septic tank. 30" of solids in treatment unit. 6" of solids in discharge pump tank. It may be necessary to pump all three tanks out next year. Cleaned blower air filter. Cleaned drip manifold spin filter. Good aeration and treatment quality. Tested floats, pump and alarms. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/29/2023 | 07:03 PM
04/07/2023 |  |  | 01-120-0523A | Chesterfield | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 3000 | 1000 | 1000 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | Pungent | Discolored | 9.000000 |  | 5.000000 | [13 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/07/2023 | Jan 1 1900 1:00PM
10/31/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 10/31/2023 | Sample Chamber | 26.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/09/2023 |  | RoutineScheduled | 101-16-0057 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Advantex |  | Gravity | Gravity | Trenches | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
11/06/2023 | Alternative | RoutineScheduled | 132-11-0061 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Norweco 960 |  | Pump | Pressure | Drip | Not Applicable | 150.000000 | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/15/2023 | 11:00 AM
12/13/2023 | Alternative | Routine/Scheduled | 127-STS-35037 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfields LLC | 1942001219 | Gene | Shanks | 2.000000 | 1250 |  |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 2:00PM
07/06/2023 | Alternative | Reportable Incident Component Maintenance | 099-06-0361-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to failed on/off float. Replaced float. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
12/11/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Hoot |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/11/2023 | Dec 30 1899 10:40AM
07/25/2023 | Alternative |  | 14-113-135 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/25/2023 |  | 2.320000 |  |  | 2.800000 |  |  | Will be sent separately |  | BOD: 2.32 TSS: 2.80 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/25/2023 | 12:00 AM
04/04/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | 12:00 AM
09/25/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | Dec 30 1899 1:45PM
08/22/2023 | Alternative | RoutineScheduled | 2004-143-0117 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/20/2023 | Alternative | RoutineScheduled | Discharging | Halifax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Southside | Acres of Virginia, Inc. |  | Melvin | Collins | 1.000000 | 1500 | Aquaklear |  | Gravity | Gravity | Discharge | UV | 450.000000 | ["Auxiliary Filter"] | ["Auxiliary Filter"] |  | None | Cloudy | 7.000000 |  |  |  |  | 12/20/2023 | Sample Tap | 34.200000 |  | 12000.000000 | 24.800000 | 50.900000 | 5.100000 |  |  | Water sample was out specs. Home is a summer home and has been been closed down. Possibly take another water sample in summer months to verify equipment is working properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/12/2024 | 01:00 PM
05/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/15/2023 | Alternative | RoutineScheduled | 14-125-091 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | ELJEN |  | Gravity | Gravity | Mound | Not Applicable | 200.000000 | ["Dispersal System Operation","SludgeScum Accumulation"] | ["Dispersal System Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/15/2023 | 12:00 AM
06/14/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was replaced and the system appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 | 2500 | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Media cleaner added Pumped Primary tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/13/2023 | Alternative | RoutineScheduled | 07-184-5003 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 12 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/13/2023 | 12:00 AM
07/02/2023 | Alternative | Reportable Incident | SD-10-312 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation"] | [18 empty] | Alarm service call only: Found the turbine pump and blower were faulty. Returned on 8/2/2023 and replaced faulty T25 pump with a STEP 30 turbine pump 230 volts and replaced the DF-50 air blower with a HP 80 blower/ Counts: Pump Run-3334 Pump Counts-37379/ High level-13/ Override-13/ Drip rate-4.8 On-4m 4s Off-1h 55m/ Watermeter-1,145,042 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
01/03/2023 |  | RoutineScheduled | 177-STS-89571 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Pump | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | 12:00 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/08/2023 |  | RoutineScheduled | 124-STS-2379 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Virginia Beach | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1875 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/07/2023 | Alternative | RoutineScheduled | 159-STS-95150 | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/23/2023 |  | RoutineScheduled | 099-16-0067 SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [5 empty] | 02/23/2023 |  | 3.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Customer had tank pumped last year and treatment side already has 11" of sludge that looks more like regrowth. Gave customer copy of Do's and don'ts. Will check next year. Blower 2.96 amps. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
03/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
04/25/2023 |  | RoutineScheduled | 03-100-0003 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 2.000000 | 2000 | Septic Tank | Micro-Fast | Pump | Pressure | Trenches | Not Applicable | 1000.000000 | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/27/2023 | 02:35 PM
03/02/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None |  | 7.090000 |  |  |  |  | 03/02/2023 |  | 2.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 03:00 PM
02/22/2023 | Alternative | RoutineScheduled | 115-15-0130 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Advanced Enviro-Septic -Presby |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge level-16" Sludge in Septic tank (2 inch increase from last year), approx 1" scum layer on top. Drainfield Observation port is clear and looks fine about 1 in water observed in observation port. Drainfield looks good, no bad smells noticed from air breather port. May get system pumped next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/01/2023 | 09:30 AM
06/23/2023 | Alternative | RoutineScheduled | 107-07-0103 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/06/2023 | 12:00 AM
02/08/2023 |  | Follow-Up | 179-11-0025-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to disassemble components in recirc tank and assist pumper with proper pump out. Reassembled components in recirc tank and all tanks were refilled back to proper levels by a water truck. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
10/10/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:00 AM
04/04/2023 |  | Routine/Scheduled | 157-09-0145 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The pressure switch on the aerator is not hooked up - needs to be addressed. The septic tank needs additional risers on it to be properly inspected in the future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | 11:00 AM
07/27/2023 | Alternative | RoutineScheduled | 07-160-0147 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 |  | Ecoflo (peat moss) | [6 empty] | [] | ["SludgeScum Accumulation"] | [18 empty] | - pump is not working, needs more work | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/14/2023 | 12:00 AM
11/20/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Replaced pump and float | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/20/2023 | Dec 30 1899 10:00AM
06/11/2023 |  | RoutineScheduled | SD-12-060 | Madison | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1500 | septic | Advantex | Gravity | Gravity | Discharge | UV |  | [] | [] | YES | Musty | Clear | [15 empty] | No Discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/12/2023 | 08:25 AM
06/09/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Level Sensor Operation"] | NA | Septic | Clear | [13 empty] | Will be sent separately | Inspected | On arrival, effluent level was excessively low (below diffusers). Septic odor present. Replaced the timer enabler float switch (had stuck on). Refilled tank with enough fresh water to cover the diffusers. Cleaned the air pre-filter and replaced the filter element for the blower canister filter. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/08/2023 | Dec 30 1899 6:43AM
09/28/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-417 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
04/12/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Primary tank pumped | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/22/2023 | 11:15 AM
12/20/2023 | Alternative | Pump-Out Only | 228-01-0360 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | Dec 30 1899 10:00AM
09/07/2023 | Alternative | Initial Visit | 015-STS-337623 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | EZ Treat |  |  | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | [7 empty] | Start Up | [10 empty] | Start up system | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/02/2023 | 12:00 AM
01/30/2023 |  |  | 02-113-116 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/30/2023 |  | 2.110000 | [5 empty] | Will be sent separately |  | BOD: 2.11 TSS: BDL SV | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | 12:00 AM
01/05/2023 |  | Follow-Up | 179-09-0106-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Level Sensor Operation" ,"Distribution Pump Operation" ,"Dispersal System Operation" ,"SludgeScum Accumulation" ,"Septic Tank Baffles"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite to follow up for a peat change. Pods 1 and 4 had ponding water. Pods 2,3 and 5 looked great for its age. All 5 pods were augered and sample box was vacuumed to remove clogs in pods 1 and 4. Peat change not required at this time treatment still looks good. Inlet wedge lids leak on both tank. Distribution box was dug up and drainfield was video inspected. All header lines had new growth roots. Added root-x. There was a blockage possibly crushed header at the ez flow joint not allowing waste water to get to trench 4. Proposal to be sent to correct infiltration on tanks, repair header line 4 and install proper float tree. Home owner to make arrangements to get all tanks pumped due to sludge levels. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
06/17/2023 | Alternative | RoutineScheduled | 2022-06-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | Chlorination | 500.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.700000 |  |  | 1.600000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/02/2023 | 12:00 AM
11/10/2023 | Alternative | RoutineScheduled |  | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1000 | 250 | 750 | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles"] | YES | Pungent | Cloudy | [14 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | 12:00 AM
03/03/2023 |  | RoutineScheduled | 179-14-0046-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Auxiliary Filter"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Due to the rainy conditions on the day of the inspection, it was not possible to determine if the system is allowing effluent to surface at the end of the drip dispersal area. We did not see any evidence of this last year in dry weather conditions. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
07/14/2023 | Alternative | Reportable Incident Component Maintenance | 179-12-0057-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for blower alarm. Replaced failed blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/18/2023 | 11:45 AM
05/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Peat fiber is very broken down and will need replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
08/14/2023 | Alternative | Routine/Scheduled | 041-STS-258035 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/14/2023 | Dec 30 1899 3:02PM
05/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/15/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 09:45 AM
01/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/21/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Type of System Alternative Type of AOSS System Auqasafe to drip Septic Tank Condition of above Component Notes for above Component Normal Level 6" of sludge Heavy amount of solids Pulled and cleaned filter Discharge/Pump Tank Condition of above Component Notes for above Component Above normal Level 10" of suspended solids All floats and pump are functioning properly however floats are Aged Pump screen was clogged Pulled and cleaned floats, pump screen and disc filter. Riser has signs of leaks Aeration Condition of above Component Notes for above Component Normal Level Heavy suspended solids Aerating properly Air Pump/Blower Condition of above Component Notes for above Component Pulling 1.7amps of 1.6 max amps Cleaned filter. Screw for filter housing was broken off prior to me cleaning filter All audible and visual alarms are functioning properly Control Panel Condition of above Component Notes for above Component 120v to each breaker All audible and visual alarms are functioning properly Pump is pulling 11.5amps Drip Field Condition of above Component Notes for above Component No signs of surfacing. Field is pressuring properly Flushed field until water ran clear | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | 08:44 AM
03/13/2023 |  | RoutineScheduled | 101-05-0595 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/19/2023 | 12:00 AM
01/09/2023 |  | Routine/Scheduled | 234-14-432 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | Jan 1 1900 9:51AM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank filter was clogged and level was very high. Filter was cleaned and the level returned to normal levels. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/28/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Dispersal System Operation","Attached Growth Medium","Septic Tank Baffles"] | ["Auxiliary Filter","Dispersal System Operation","Attached Growth Medium","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 12:00 AM
03/16/2023 | Alternative | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced Microfast blower. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/15/2023 | Dec 30 1899 12:05PM
11/17/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-90175 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
11/10/2023 | Alternative | RoutineScheduled | 179-11-0093-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 0-3 0-4 | 0-0 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | None | Clear |  |  | 7.000000 | [11 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | 10:00 AM
03/30/2023 | Alternative | Routine/Scheduled | 128-08-126 | Essex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | ["Attached Growth Medium","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Biofilter changeout. Septic tank pumped empty for storage and for drying. Biofilter changed out with new. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/03/2023 | 07:00 AM
07/10/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank | Discharge pump tank | Pump | Gravity | Discharge | UV |  | ["Recirculation Pump"] | ["Recirculation Pump"] | YES | [17 empty] | Septic Tank-4"sludge 0"scum/ EZ-Treat Recirculation Tank-3"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ Recirc. pump intake cleaned and media in good condition/ UV-Light sleeve cleaned and functioning properly/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-9725 ETM-101h 19m/ Pump2-9715 ETM-101h 23m/ Peak-193/ High-122 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
08/18/2023 | Alternative | Reportable Incident | 234-13-245 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/18/2023 | Dec 30 1899 9:00AM
08/11/2023 | Alternative | RoutineScheduled Component Maintenance | 175-07-0579 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | UV unit has sustained electric damage to all components and needs to be replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/15/2023 | Dec 30 1899 2:02PM
02/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/01/2023 | Dec 30 1899 2:21PM
12/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | roots in media filter not working alarm light on pump panel not operating blower alarm doesnt operate Call to schedule these repairs | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 01/15/2024 | 10:39 AM
12/27/2023 | Alternative | RoutineScheduled | 182-03-0341 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [18 empty] | (2) valve box lids needed. CP functioning but recommend replacing. Tank volume low and unable to test for leak(s) and operation of media | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/26/2023 | Alternative | Routine/Scheduled | 234-16-334 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/26/2023 | Dec 30 1899 2:25PM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Delta Environmental Products, UC Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/11/2023 | Alternative | RoutineScheduled | 06-100-1001 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | PURAFLO |  | Pump | Gravity | Pad | Not Applicable | 300.000000 | [] | [] | NA | [17 empty] | SLUDGE JUDGE 5" FROM BOTTOM EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 12:00 AM
02/20/2023 |  | Routine/Scheduled | 800-03-0144 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | [15 empty] | Replaced on/off float | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | Jan 1 1900 8:20AM
06/21/2023 | Alternative | RoutineScheduled | 085-STS-31853 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | NA | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
08/31/2023 | Alternative |  | 001-STS-92314 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
05/24/2023 | Alternative | Routine/Scheduled | 103-STS-94607 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Biofilter - peatmoss saturated - raked / turned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 11:15 AM
09/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and pumping | 1942001330 | Michelle | McKim | 3.000000 | 1500 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 4:00PM
08/28/2023 | Alternative |  | 033-06-0617-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
01/24/2023 |  | Routine/Scheduled | {FIPSCode}-STS-3540 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [12 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/27/2023 | Jan 1 1900 2:00PM
07/27/2023 | Alternative | RoutineScheduled | 107-09-0001 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | 12:00 AM
09/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 2.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 09/25/2023 |  | 12.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
10/04/2023 | Alternative | RoutineScheduled | 04-125-104 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 15 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/04/2023 | 12:00 AM
02/28/2023 | Alternative | Routine/Scheduled | 053-STS-10251 | Dinwiddie | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/28/2023 | Dec 30 1899 12:19PM
08/29/2023 | Alternative | RoutineScheduled | 147-11-0108 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Hutchens Septic Services LLC | 1942001509 | Robert | Hutchens, Jr. | 1.000000 | 1250 | Delta Ecopod |  | Pump | Pressure | Drip |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/14/2023 |  | Routine/Scheduled | 13-120-0451A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Multiflo ATU |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/14/2023 | Jan 1 1900 3:33PM
05/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
05/16/2023 |  | Reportable Incident | 2015-143-0169 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [20 empty] | 17.300000 |  | 2419.600000 | [5 empty] | Owner called due to an alarm - no alarm on arrival - H20 levels all good - everything working properly. Took 5 year BOD and Fecal samples. NOTE : Fecal sample was high - system should function properly after service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 PM
06/27/2023 | Alternative | RoutineScheduled | SD-96-491 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [17 empty] | Septic Tank is buried without access to the surface, owner stated they get the septic tank pumped out every 5 years/ Pump Tank-2"sludge/ No pump out needed at this time/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-7227 ETM-84509/ High cnts-12 ETM-331/ Watermeter-120,082.6/ Hydraulic unit return & filter solenoids require replacement/ No breakout or spongy areas on the drip field. 7/11/2023 Returned to replace 3 solenoids, tested hydraulic unit now functioning and dosing properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
01/26/2023 |  |  | AWES-9B9PWQ | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [18 empty] | Told homeowner the tank needs to be pumped soon. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | 12:00 AM
02/22/2023 | Alternative | Reportable Incident | 151-06-0114 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Distribution Pump Operation | Distribution Pump Operation | N/A | [17 empty] | AOSS - ALARM EVENT - System high level in all tanks due to failed discharge pump - owner only wanted discharge pump replaced - no pumpout - Discharge pump replaced like for like, system pumped to normal level on own accord. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/23/2023 | 08:00 AM
06/02/2023 | Alternative | RoutineScheduled | 001-STS-92313 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1500 | PURASYS |  | Pump | Pressure | Trenches | Not Applicable |  | [] | [] | [18 empty] | EVERYTHING WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/06/2023 | 12:00 AM
10/12/2023 | Alternative | RoutineScheduled Component Maintenance | SD-13-181 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity |  | UV |  | ["Disinfection" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Disinfection" ,"Attached Growth Medium" ,"Recirculation Pump"] | NO | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
07/03/2023 | Alternative | Routine/Scheduled | 228-05-0109 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/03/2023 | Dec 30 1899 9:55AM
10/09/2023 | Alternative | RoutineScheduled Component Maintenance | SD-047-16-109 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"Effluent Screens" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["Attached Growth Medium" ,"Effluent Screens" ,"BlowerCompressorAerator Operation"] | YES | Pungent | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend that the septic/ATU tanks be pumped due to the sludge accumulation in the tanks. We also recommend replacing the damaged riser lid. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
06/22/2023 | Alternative |  | 132-18-0035 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Alexandra | Williams | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/01/2023 | Alternative | Routine/Scheduled | 157-06-0041 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/01/2023 | 09:30 AM
11/29/2023 | Alternative | RoutineScheduled | 06-184-5002 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.500000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
03/06/2023 |  | RoutineScheduled | 165-STS-335355 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Gravity | Discharge | UV |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/02/2023 | 12:00 AM
12/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
02/15/2023 |  | RoutineScheduled | SWP-04-533 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
02/27/2023 |  | RoutineScheduled | 179-07-0162-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/06/2023 |  | Routine/Scheduled | -STS-6482 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Pressure | Pad |  |  | ["Attached Growth Medium","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/06/2023 | 12:39 PM
08/17/2023 | Alternative | Reportable Incident | 800-09-0261 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Environmental Services of Virginia | 1942001182 | Steve | Haley | 3.000000 | 450 | Clearstream 600NC3T |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | YES | Musty | Clear | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/17/2023 | 12:00 AM
05/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/17/2023 | Alternative |  | 01-120-0539A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Advantex |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Recirculation Pump"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 12:00 AM
01/12/2023 |  | RoutineScheduled | 153-STS-19018 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | ATU Needs pumped out. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/02/2023 | 02:20 PM
03/04/2023 |  | RoutineScheduled | 2111-06-153m | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination | 500.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty |  | 7.800000 |  |  | 1.300000 |  | 03/06/2023 | Sample Chamber | 25.000000 |  |  | 14.500000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/17/2023 | 12:00 AM
05/02/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/15/2023 | Alternative | RoutineScheduled | 150-06-358 | King William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 3.000000 | 2900 gallons | septic tank | Clearstream | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Level Sensor Operation","Control Operation","Distribution Pump Operation","BlowerCompressorAerator Operation"] | NA | Musty | Clear |  |  | 60.000000 | [12 empty] | Septic tank 6" fog, 8" sludge. Clearstream 60% SS. Cleaned air pump. Aerator not functioning, rebuilt, functioning properly now. Pump, alarm, floats, controls operating properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/23/2023 | 08:20 PM
02/01/2023 |  | Initial Visit | 800-STS-14673 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 11.000000 | [7 empty] | Owner called due to an alarm going off a few nights ago and the toilet running for 5 hours. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 1.5 minutes every 2 hours. Took initial BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/01/2023 | Jan 1 1900 1:00PM
03/20/2023 |  |  | 087-STS-6153 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 1.000000 | 1200 | 1200 |  | Pump | Gravity |  | Not Applicable |  | [] | ["Control Operation","SludgeScum Accumulation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Septic Tank Baffles"] | YES | Musty | Clear | 7.000000 |  | 7.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/20/2023 | 12:00 AM
03/10/2023 |  | RoutineScheduled | 10-142-0174 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Semi-Annual Inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | Jan 1 1900 8:19AM
02/13/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced (2) floats to modules. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
10/31/2023 | Alternative |  |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [18 empty] | See attached analytics | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 12:00 AM
03/17/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1125 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/28/2023 | Alternative | RoutineScheduled Component Maintenance | 165-STS-334031 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Pad | UV |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced UV Bulb Filter clog cleared Recommend keep overgrowth away from ET BED | This AOSS should now return to normal function after having provided the above state routine maintenance | 10/13/2023 | 01:07 PM
02/23/2023 |  | RoutineScheduled | 099-STS-92267 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | NA | None | Clear | [5 empty] | 02/23/2023 |  | 4.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Blower 3.07 amps. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
02/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/07/2023 | Alternative |  | 061-STS-21874 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/07/2023 | 12:00 AM
06/02/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
02/07/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [7 empty] | 02/07/2023 |  | 11.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
09/19/2023 | Alternative | Reportable Incident | 196-10-183 | Westmoreland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | rebuilt compressor, cleaned filters, flushed drip lines | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping ATU. Recommend mowing drainfield area to keep larger vegetation down. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/13/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-90510 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
01/31/2023 |  | RoutineScheduled | 177-14-0243-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | None | Clear | [5 empty] | 01/31/2023 |  | 2.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Treatment looks very clean and water level normal. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
06/07/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1875 | Septic | Micro fast | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/10/2023 |  | RoutineScheduled | 099-14-0100-SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"Dispersal System Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["Effluent Screens" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend removing the trees growing next to the distribution box. We also recommend pumping the septic tank and aerobic treatment unit. This was completed on May 23, 2023 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
10/12/2023 | Alternative | Routine/Scheduled | 157-08-0195 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual maintenance: -Septic Tank 1 Primary: At normal level Has 1" of sludge with 10" of solids Riser is leaking -Septic Tank 2 Secondary: At normal level Has 1" of solids with 6" of sludge Filter was laying on top of tee due to system floods from water intrusion. -Discharge/Pump Tank 1 Ecoflow: At normal level Pump and floats working Splice box is not water tight Top of chamber is at grade -Discharge/Pump Tank 2 Clearstream: At normal level Pump and floats aged Riser is leaking Plumbing is inside of the tank Riser lid is broken -Discharge/Pump Tank 3 Garage pump chamber: At normal level Pump and floats working but aged -Aeration: At normal level Has 4" of sludge Aerator is bad so nothing was mixed up Riser is leaking Pulled and cleaned defuser and wier -Peat Moss: Chamber is at grade Riser sections are leaking Tipping bucket and trays were laying at the bottom of the chamber due to flooding from water intrusion Peat is compacted -Air Pump/Blower: Air pumps diaphragms are busted and no longer working -Control Panel 1 Ecoflow: Pump pulling 6.25amps -Control Panel 2 Clearstream: Pump pulling 8.25amps -Distribution Box 1 Ecoflow: At grade Box is pushing in from ground weight Box is at normal level Lid is cracked and has holes in it -Distribution Box 2 Clearstream: Box is at grade Lid does nit fit due to box being pushed in from ground weight At normal level Lots of debris inside -Distribution Box 3 Splitter box for septic tank: Right outside of the secondary septic tank Box is plastic and is being pushed in Has some cracks Two lines going out, one for ecoflow, one for clearstream -Drain Field: Not seeing any surfacing in the drainfields, the area is naturally damp | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/24/2023 | 04:12 PM
02/23/2023 | Alternative | Routine/Scheduled | 15-174-0047S | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/23/2023 | Dec 30 1899 12:57PM
04/08/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/09/2023 | 12:00 AM
05/09/2023 | Alternative | RoutineScheduled | 05-160-0353 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | [] | NA | Septic | Dark Brown | [15 empty] | - check valve is leaking, not functioning properly, needs to be replumbed - Microfast tank needs to be pumped-cleaned | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/19/2023 | 12:00 AM
07/07/2023 | Alternative | RoutineScheduled Component Maintenance | 175-12-0069 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
09/26/2023 | Alternative | RoutineScheduled | 01-197-137 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 |  | ATU |  |  |  |  | Chlorination | [22 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
06/12/2023 | Alternative | Routine/Scheduled | 151-19-0040 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Advanced Septic |  | Gravity | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 0.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 06:17 PM
04/05/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/15/2023 | Jan 1 1900 7:20PM
11/24/2023 | Alternative | Routine/Scheduled | 13-120-0417 VU | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Annual Maintenance: -Septic Tank: High level upon arrival due to clogged effluent screen. Flushed and cleaned effluent screen and water level returned to normal. Inlet tee appears to be intact. Outlet tee appears to be intact. Not due for pump out -Recirculation Tank:Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly -Media Sheets: Cleaned media sheets. Checked and confirmed spray pattern is good -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | Dec 30 1899 9:51AM
08/08/2023 | Alternative | RoutineScheduled Component Maintenance | 179-11-0148-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
11/10/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | [17 empty] | Septic Tank-2"sludge 0"scum/ Microfast ATU Tank-6"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Off float and the control contactor is faulty and requires replacement/ Done on 11/15/2023/ Controls, pump, floats and alarms are now functioning properly/ Counts: Pump-7509 ETM-1672h 35m/ Watermeter-0541921.66/ Peak counts-79 ETM-823h 6m/ No breakout or spongy areas on the drip field/ UV-Light sleeve was cleaned and the light is functioning properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
09/21/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:00 AM
06/27/2023 | Alternative | RoutineScheduled | S-15-111-0015 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 500 | Septic Tank Only | Delta Whitewater | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The blower filter was cleaned. The treatment unit was operating as designed. The controls were operating as designed. There were no samples taken because there was no discharge to the D-Box. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | Jan 1 1900 9:45PM
06/19/2023 | Alternative | Routine/Scheduled | 800-STS-15024 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | Dec 30 1899 12:45PM
03/09/2023 |  | RoutineScheduled | 179-12-0188-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"BlowerCompressorAerator Operation"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | The K Rain Valve is leaking and should be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
05/12/2023 |  |  |  | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
09/27/2023 | Alternative | Initial Visit |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Meet with the pumping company and pumped and and cleaned the pump tank. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The septic tank has no riser on the outlet end. The timer is set to 9 minutes every 2 hours. Did not take samples. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/27/2023 | Dec 30 1899 10:00AM
02/28/2023 | Alternative | Follow-Up | 151-07-0064 | Lancaster | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 2000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | None | NO | [17 empty] | Site visited for evaluation. Filed FOIA with local HD - Received FIVE (5) pages of a known TWENTY-SEVEN (27) page permit !!! - Repeat FOIA filed! Technicians attempted to conduct biofilter changeout - removed peatmoss to gravel layer - ground water return was overcoming the ability of the pump truck to keep up. Ground water finally stabilized in the module at 30" below Grade. Soil boring outside of gravel pad install area indicates a heavy shrink/swell clay, streaked with gray. At a depth of 42", encountered the water table - free water filled the soil boring to a depth of 30" below grade, equal to that at the treatment Module. Additional soil borings need to be conducted to develop a repair option. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/01/2023 | 10:00 AM
05/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
05/04/2023 |  | RoutineScheduled | 145-05-0003 | Highland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 2.000000 | 2500 | Septic Tank Only | MicroFast | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NO | [17 empty] | The system did not need to be pumped. The blower and spin clean filters were both cleaned. The controls were operating as designed. There were no visible leaks in the drip field. There were some over growth of some pine trees on the drip field and advised the land owner that the field needed to be maintained and cleared. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/03/2023 | 11:50 AM
11/30/2023 | Alternative | RoutineScheduled | 182-10-0290 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation"] | [18 empty] | Pump replaced. Wiring replaced and drip field leak fixed | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/30/2023 | 12:00 AM
03/23/2023 |  | RoutineScheduled | 153-STS-19296 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | [7 empty] | 04/26/2023 | Sample Chamber | 4.000000 |  | 11.000000 |  |  |  | Attached to this report |  | Septic Tank-4"sludge 3"scum/ Microfast-6"sludge/ Pump Tank-2"sludge/ No pump out needed at this time/ UV-Light is faulty and requires replacement/ Returned and repaired the UV-Light/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-1795 ETM-224h/ Watermeter-0104996.6/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/16/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 |  |  |  | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Install Blower Motor | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/16/2023 | Dec 30 1899 10:35AM
01/14/2023 | Alternative | RoutineScheduled | 061-STS-23024 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001682 | Frank | Hogan |  | 11650 | Whitewater ATU | Whitewater ATU | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Dispersal System Operation" ,"Level Sensor Operation" ,"SludgeScum Accumulation"] | NA | Musty | Clear | 7.200000 | 2.300000 |  |  |  | 10/31/2022 | Pump Chamber | 14.000000 |  |  | 5.000000 | 22.300000 |  | Will be sent separately | Inspected | 4th Quarter 2022 Inspection Report Weekly Checks completed and routine service 10-31-22 Repaired damaged valve box in drip field 10-31-22 Sampling 4th qrtr 11-28-22 Pump Station Section B Alarm- Found floats would not turn pump on due to grease accumulation, floats cleaned station operable. 11-30-22 Reinstalled new updated telemetry at WWTP 12-2 Alarms continue amperage on pump variable, not pumping. pulled pump found clogged with wipes reinstalled working reset to alternate 12-20- Replace float on omni panel Average Daily Flow 15,692 gpd Influent trash tank pumped Monthly Dec 3,250 November 4,200 October 4,200 total 11,650 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/14/2023 | 03:49 PM
04/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/03/2023 | Alternative | Reportable Incident | 061-18-115 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | replaced failed pump | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Effluent Screens" ,"Auxiliary Filter" ,"Disinfection"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. UV Unit needs repairing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | 12:05 PM
04/26/2023 |  |  | {FIPSCode}-STS-22991 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 04/26/2023 |  | 4.130000 | [5 empty] | Will be sent separately |  | BOD: 4.13 TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | 12:00 AM
04/05/2023 |  | RoutineScheduled | 133 06 0436 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Western Virginia Water Authority | 1942001144 | Michael | Doss | [9 empty] | ["None"] | ["None"] | NA | None | Clear | [5 empty] | 04/05/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/11/2023 | 01:05 PM
09/05/2023 | Alternative | RoutineScheduled | 04-192-236 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 3 - Blue Crystal tablets installed 14 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/05/2023 | 12:00 AM
10/30/2023 | Alternative | Routine/Scheduled | 136-07-0222 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal level 6 in of sludge less than 1 in of solids Pulled and cleaned filter No signs of infiltration -Discharge/Pump Tank Pump chamber: Normal level Tested floats and pump all working as should All plumbing intact and pump moving water properly No signs of infiltration -Peat Moss: Peat moss is spent and broken down Recommend peat change Module is intact no cracks or breaks Dispersal trays and tipping bucket intact -Control Panel: 120 volts coming in All visual and audible alarms functioning Pump pulled 8.5 amps All components working however panel is aged -Distribution Box: Normal level 2 lines intact and properly taking water -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | 08:45 AM
01/16/2023 |  | Reportable Incident | 228-09-0208A | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/16/2023 | Jan 1 1900 9:00AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
10/04/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["Dispersal System Operation","Distribution Pump Operation"] | ["Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Cleaned filters | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/04/2023 | Dec 30 1899 11:30AM
03/01/2023 | Alternative | Pump-Out Only | 128-13-0037 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | NO | [16 empty] | Pumped Out | AOSS - Initial Visit - PUMPOUT ONLY Contacted by property owner for routine pumpout - It was unknown at the time that this is an AOSS. Trash Tank pumped empty and service. Aspirator functioning. System requires service agreement and full service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/02/2023 | 08:45 AM
02/22/2023 |  | Routine/Scheduled | 234-09 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | Jan 1 1900 12:10PM
10/06/2023 | Alternative | RoutineScheduled |  | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | BIOCOIR |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Distribution Pump Operation","Attached Growth Medium"] | ["Distribution Pump Operation","Attached Growth Medium"] | [17 empty] | Pumped Out | REPLACED SEWAGE PUMP AND FLOAT. REPLACED TD1 PANEL. PUMPED SEPTIC. REPLACED FIBER. EVERYTHING WORKING AS IT SHOULD. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/03/2024 | 02:20 PM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Effluent pump appears to be near the end of its life but is functioning at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/05/2023 | Alternative | Routine/Scheduled |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Gravity | Trenches |  | 450.000000 | ["BlowerCompressorAerator Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/22/2023 | 11:58 AM
12/14/2023 | Alternative | RoutineScheduled | 07-184-5011 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
06/29/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | Sussex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Purasys |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/29/2023 | Dec 30 1899 9:12AM
04/24/2023 |  | RoutineScheduled | 133 07 0058 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | Septic zone- minimal scum- 6" sludge- Recirc zone -8" sludge, Discharge Tank trace sludge - Cleaned Biofilter, Flushed and Brushed spray manifold- Cleaned RSV, Flushed System, Ran in test mode. Alarm light good vocal sound disconnected. Tested all 6 Floats all ok. memory is corrupted on computer and does not hold history or alarm register, replaced battery but still not holding memory, reset time date, Ram seems corrupt but setting ok and it is operational. System pumped out last summer by Foutz. Added one Rootx 2lb treatment to discharge tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
08/02/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Microfast |  | Pump | Gravity | Trenches |  | 600.000000 | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/16/2023 | 11:16 AM
08/09/2023 | Alternative | Routine/Scheduled |  | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - normal level - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. NOTE - control panel is having intermittent power issues - recommend replacing with MVP DM controls. PUmp tank - float sensors, pump and controls are operating DBox intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | Dec 30 1899 9:45AM
02/01/2023 |  | Routine/Scheduled | 199-16-0003 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Routine Service Pumped processing tank empty - pressure washed Serviced aspirator & effluent screen. Refilled with fresh water for restart - mixing present on departure. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | Jan 1 1900 9:30AM
07/05/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-89580 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium"] | ["Attached Growth Medium"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | The conduit has settled below the control panel leaving wiring exposed. Also, the RSV in the Advantex unit is not glued to the split flow tee. We are copying the builder, Pruitt, Contracting Group so they can have the installer make these repairs for you under warranty. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | 11:26 AM
09/19/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/19/2023 | 12:00 AM
11/13/2023 | Alternative | RoutineScheduled | 165-STS-336584 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 RT |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 12:00 AM
11/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium"] | ["Auxiliary Filter" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
11/02/2023 | Alternative | Routine/Scheduled | 166-07-573 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 40.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | 05:58 PM
06/29/2023 | Alternative | RoutineScheduled | 2018-143-0171 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | YES | [17 empty] | Replaced Step 20 pump with a new one. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
04/20/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [5 empty] | 04/20/2023 |  | 81.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | Jan 1 1900 12:48PM
03/01/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired inlet pipe | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
01/19/2023 |  |  | 07-120-0070A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 2300 | 1300 | 1000 | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","SludgeScum Accumulation","Dispersal System Operation","Effluent Screens","Recirculation Pump"] | YES | None | Clear | 7.000000 |  | 7.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/19/2023 | Jan 1 1900 11:00AM
07/06/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/17/2023 | Dec 30 1899 12:46PM
03/06/2023 | Alternative | RoutineScheduled | 109-STS-33065 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | The Norweco lid for the effluent filter is still not secure. We have reminded the installer of this, and he plans to address it. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
05/17/2023 | Alternative | RoutineScheduled | 115-07-0522 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 12000 | Dual Biomicrobics Fast 2.5 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Level Sensor Operation","Control Operation","Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Effluent Screens","Level Sensor Operation","Control Operation","Auxiliary Filter","BlowerCompressorAerator Operation"] | YES |  |  | 7.300000 | 7.200000 |  |  | 20 | 05/17/2023 | Pump Chamber | 4.500000 |  |  | 5.000000 | 31.000000 |  | Will be sent separately | Inspected | Septic Tank #1 Sludge levels- 2-3" scum and 12-14" sludge trace ( tanks were pumped in last august), septic tank #2 minimal scum and 12-24" sludge trace- Fast treatment unit has good Aeration Fast #1 5" sludge trace and Fast #2 Trace-6" sludge. The system tanks were pumped 9 months ago. Cleaned blower airfilters, Good Aeration observed from both Blowers, cleaned all the probes. One probe TSS in for replacment. Took Ph and Do Readings. Collected lab samples, results included. Cleaned both Effluent screens. Enormous amount of heavy duty wipes for in the front tank, Please ask folks to not dispose of them. Treatment unit #1 6.6 DO and 7.8 pH. Treatment unit #2 8.2 DO, pH 6.2. pH . In pump tank Ph was 7.3 -TSS#1 700 #2 600 - Effluent meter reading 6814689 vs 6672663 85 days 142,026galloin or about 1,670 gallons per days. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
03/14/2023 |  | Routine/Scheduled | 18-142-0322 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Treatment Module - recirc - recirc pump, media drapes & spray grid serviced. Treatment Module - discharge - float sensors, pump and controls operating. Pumps to community absorption field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | Jan 1 1900 9:30AM
11/27/2023 | Alternative | Reportable Incident | 228-04-1027 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/27/2023 | Dec 30 1899 10:30AM
05/15/2023 | Alternative | RoutineScheduled | 154-05-1077 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Puraflo |  | Gravity | Pressure | Pad | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
01/31/2023 |  |  | 12-192-126 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/31/2023 | [7 empty] | Will be sent separately |  | BOD: BDL TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | 12:00 AM
08/23/2023 | Alternative | Routine/Scheduled | 09-137-0155 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | NO | [17 empty] | Changed spin filter. Flushed manifold. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/23/2023 | Dec 30 1899 3:31PM
08/10/2023 | Alternative | Routine/Scheduled |  | James City | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 750 | Multiflo FTB |  | Pump | Gravity | Discharge | Chlorination | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Grinder lift station - float sensors, pump and controls operating. Primary septic tank - normal level MultiFlo ATU - mizing present - compressor serviced - socks clear. Chlorination - tablets present Discharge point - no signage - discharge point under water. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/15/2023 | Dec 30 1899 1:00PM
06/14/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was replaced and the system appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/11/2023 | Alternative | RoutineScheduled | 19-163-0051 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/20/2023 | Alternative | RoutineScheduled | 115-12-0133 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Septic | Eljen | Pump | Gravity | Drip | Not Applicable | 350.000000 | ["Effluent Screens"] | ["Distribution Pump Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/20/2023 | 09:30 AM
12/18/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | Dec 30 1899 10:15AM
08/01/2023 | Alternative | Routine/Scheduled | 800-STS-13946 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream, cleaned the UV light bulb, and cleaned the filter in the septic tank. Changed the diffuser in the Clearstream and changed the filter in the aerator. Fixed the grade on the pipe in the Clearstream. The timer is set to 2 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/01/2023 | Dec 30 1899 11:00AM
12/20/2023 | Alternative | Routine/Scheduled | 085-STS-34711 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 750 |  |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | Dec 30 1899 9:00AM
01/16/2023 |  | Routine/Scheduled | 228-04-1252 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | Jan 1 1900 1:45PM
12/20/2023 | Alternative |  | 001-STS-92314 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
11/28/2023 | Alternative |  | 2013-143-0157 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | INSTALLED NEW NORWECO AGITATOR | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/01/2023 | 12:00 AM
12/20/2023 | Alternative | RoutineScheduled | 181-04-0381 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | RetroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NO | [17 empty] | The system did not need to be pumped. The blower and spin filters were both pulled and cleaned. The controls were operating as designed. There was return effluent returning to the pump chamber so the drip field was operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/17/2024 | 03:40 PM
09/28/2023 | Alternative | Routine/Scheduled | 06-160-0110 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/28/2023 | 02:30 PM
03/28/2023 |  | Follow-Up | SWP-04-661 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to disassemble components in recirc tank and assist pumper with proper pump out. Reassembled components and tank was refilled with water truck. Junction box was cracked upon arrival. Pumpers hose hit box and broke it all the way off. Replaced junction box and redid all wiring in recirc tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
03/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
10/24/2023 | Alternative | Reportable Incident | 154-04-0557 | Louisa | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2500 | MICRFAST |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Effluent Screens"] | YES | Musty | Clear | [14 empty] | Inspected | PUMP AMPERAGE 13A SLUDGE/SCUM ACCUMULATION - SEPTIC 3", ATU <2", PUMP STATION <2" DRIP SYSTEM FLUSHED FOR 15MINS AERATOR REPLACED | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/24/2023 | 04:00 PM
03/27/2023 |  | RoutineScheduled | 033-17-0230-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance | 177-09-0103-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | Pungent | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the septic tank due to scum & sludge accumulation in the tank. As noted previously, roots have grown into the Puraflo modules. This makes if difficult to fully service the peat. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
12/29/2023 | Alternative |  | 16-163-0049 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Norweco Singulair |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/29/2023 | 12:00 AM
05/30/2023 | Alternative | RoutineScheduled | 181-09-0163 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | Septic Tank Only | AdvantexAX20 | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The recirculating pump was pulled and sprayed off. The textile sheets were sprayed off. The laterals in the treatment unit was cleaned. The pressure was adjusted in the treatment unit. The controls were operating as designed. There were no visible leaks in the leech field. The RSV splitter valve was pulled and cleaned. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/06/2023 | 11:10 PM
12/12/2023 | Alternative | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Aquarobic Mini Plant | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/29/2024 | 01:15 PM
06/06/2023 |  | RoutineScheduled | 2018-143-0122 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Aqua Klear |  | Pump | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/06/2023 | 12:00 AM
11/27/2023 | Alternative | RoutineScheduled | 101-10-0012 | Albemarle | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Blue Ridge | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Level Sensor Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","Dispersal System Operation","Level Sensor Operation"] | [18 empty] | Filter blown out and replaced. Bottom float replaced (bad). Blower not moving effluent as it should. All tanks need to be pumped and repairs are needed to leaks in drip field | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/03/2024 | 12:00 AM
10/18/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20179 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
02/23/2023 | Alternative | Reportable Incident | 115-STS-101945 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | COSS - Repair - VDH HDID 157-23-0004 - GMP2018-02 Existing pump tank - pumped empty, components removed and tank collapsed and removed. Installed new 1000 gallon concrete mid-seam septic tank as pump tank. Installed new Orenco control panel. Installed effluent screen in outlet of septic tank - installed access riser to grade. Installed 5' section of 4" PVC as surge arrestor - rebalanced DBox. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/27/2023 | 06:45 AM
10/30/2023 | Alternative | Routine/Scheduled | 041-STS-260406 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/30/2023 | Dec 30 1899 1:27PM
06/05/2023 | Alternative | Reportable Incident | 147-11-0036 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Pressure | Drip | UV | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Last documented service conducted 09/22/2021 Owner refused service agreement. Property located in Cypress Point! System in high level due to electrical connection failure for discharge pump. New connections made - headworks serviced - No other service conducted. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/08/2023 | Dec 30 1899 7:30AM
06/26/2023 | Alternative | RoutineScheduled | 061-STS-21303 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Cloverleaf Environmental Consulting, Inc | 1942001135 | Robert | Charnley |  |  | EZ-Treat |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NO | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/12/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0150-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
01/23/2023 |  | RoutineScheduled | 175-03-0436 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation"] | ["Distribution Pump Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Owners aware that control panel (outside) high level alarm is not working - uf cable needs replaced. Tested inside alarm panel, functioning, owners content. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
10/09/2023 | Alternative | Routine/Scheduled | 041-STS-259215 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Flushed and cleaned effluent screen. Not due for pump out. -Discharge/Pump Tank: Water level. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. -Peat Moss: Raked and tilled peat moss. Peat moss is in good condition. Structural integrity of tipping bucket appears to be intact. Checked and confirmed tipping bucket is functioning properly. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact. Removed root infiltration. -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | Dec 30 1899 1:33PM
09/25/2023 | Alternative |  | -STS-92248 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
09/22/2023 | Alternative | RoutineScheduled | 05-197-A4 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/22/2023 | 12:00 AM
08/15/2023 | Alternative | RoutineScheduled | 150-05-191 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1250 | Clearstream |  | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 12:00 AM
01/31/2023 |  | Initial Visit | 124-STS-2379 | Chesapeake | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Rejected | EHD - Chesapeake | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 2500 | Clearstream |  | Pump | Gravity | Discharge | UV | 600.000000 | Disinfection | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | AOSS Discharging System - Initial Visit Primary septic tank - normal level - root intrusion present - recommend pumpout. Secondary septic tank - normal level Clearstream trash tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. UV Disinfection - Salcor unit has failed - requres replacing with "Other" UV equipment. Pump Tank - float sensors, pump and controls operating. Discharge point - free of debris - free flowing - no rodent guard, no signage. | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/01/2023 | Jan 1 1900 12:00PM
09/27/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
05/08/2023 |  | RoutineScheduled | 2006-143-0126 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 9.000000 |  | Puraflo |  | Pump | Gravity | Pad |  |  | [] | ["Attached Growth Medium","Level Sensor Operation","Control Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | 12:00 AM
06/06/2023 | Alternative | Routine/Scheduled | 136-18-0297 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1000.000000 |  | Biomicrobics Retrofast |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Primary septic tank - normal level RetroFAST - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. Drip - serviced headworks | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 08:15 AM
03/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | Dec 30 1899 12:26PM
03/07/2023 |  | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Control Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired recirc middle float and zone valve | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
02/21/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced EZ Treat pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | Dec 30 1899 12:26PM
04/19/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/21/2023 | 03:35 PM
02/08/2023 | Alternative | Routine/Scheduled | 157-01-281 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Aeration Tank - mixing present - compressor serviced - Control panel seal leaking - recommend replacing. Pump Tank - float sensors, pump and controls operating. DBox Intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/09/2023 | 10:00 AM
08/22/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
03/14/2023 |  | RoutineScheduled | 15-113-096 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Effluent Screens","Control Operation","Auxiliary Filter"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 9 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/14/2023 | 12:00 AM
07/25/2023 | Alternative | Pump-Out Only | 550-STS-6405 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/25/2023 | Dec 30 1899 3:30PM
03/09/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.230000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 08:40 AM
04/08/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 1.000000 | 1000 |  |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | YES | Septic | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/22/2023 | 12:00 AM
08/16/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | Dec 30 1899 3:58AM
02/13/2023 |  | RoutineScheduled |  | Cumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Piedmont | Bobby's septic inspections LLC | 1942001548 | Robert | Burnett | 2.000000 | 1000 | ecopod |  | Gravity | Gravity | Discharge | UV | 350.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Septic Tank Baffles","SludgeScum Accumulation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Septic Tank Baffles","SludgeScum Accumulation","Effluent Screens"] | YES | None | Clear | 6.800000 |  | 2.000000 | [12 empty] | Replaced blower with a new one | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/13/2023 | Jan 1 1900 10:00AM
07/26/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
08/28/2023 | Alternative | RoutineScheduled | 182-96-0434 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Sand |  |  | Pressure | Trenches | Not Applicable |  | ["Attached Growth Medium","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | Sand replaced | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/01/2023 | 12:00 AM
12/12/2023 | Alternative | Follow-Up | 101-STS-92805 | King William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
04/07/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Pump chamber is full of mud from when tank lid collapsed in. Repair was completed by others and not SES. Pump chamber needs pumped to remove all mud from tank. Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 12:48 PM
10/24/2023 | Alternative | RoutineScheduled Component Maintenance | SD-14-459 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
01/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Air pre-filter cleaned as preventative maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
02/16/2023 |  | Initial Visit | 228-17-0303 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to a red light and one aerator not running - installed an aerator rebuild kit on it. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in both of the Clearstreams and cleaned the filter in the septic tank. Changed the diffuser in both Clearstreams and changed the filter in both aerators. Replaced one of the buzzers in the control panel. Replaced the UV light bulb and replaced the cord. No inlet tee in the septic tank - will need to dig up to install - needs to be addressed. The timer is set to 1.5 minutes every 1.5 hours. Did not take the BOD and Fecal samples due to the aerator and UV not working on arrival. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/16/2023 | Jan 1 1900 2:30PM
01/18/2023 |  | Routine/Scheduled | 234-13-320 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | Jan 1 1900 9:20AM
08/08/2023 | Alternative | Reportable Incident | 166-10-001 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | high water, repaired corroded float wire. fixed blower air line | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
09/20/2023 | Alternative | RoutineScheduled | 115-11-0016 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Norweco Singulair |  | Gravity | Gravity | Trenches | UV | 350.000000 | ["Effluent Screens","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","SludgeScum Accumulation","Disinfection"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/20/2023 | 08:00 AM
09/12/2023 | Alternative | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 |  |  | Pump | Pressure | Trenches |  | 600.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 10:38 AM
02/15/2023 |  | Reportable Incident | 234-14-282 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation"] | N/A | [16 empty] | Pumped Out | Replaced aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/17/2023 | Jan 1 1900 8:00AM
11/27/2023 | Alternative |  | 18-100-0018 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 12:00 AM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump chamber lid should be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend keeping equipment off lower area of the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/12/2023 | Alternative | RoutineScheduled | 2011-143-0143 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Carrington Pump & Irrigation | 1942001121 | John | Carrington | 2.000000 |  | Norweco |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Level Sensor Operation","Distribution Pump Operation","Effluent Screens","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation","Auxiliary Filter"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
08/01/2023 | Alternative | RoutineScheduled | 09-173-051 | Prince Edward | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1500 | Eco Flo |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | ["Effluent Screens"] | ["Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation","Control Operation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/01/2023 | Dec 30 1899 1:00PM
05/12/2023 | Alternative | RoutineScheduled | -STS-43174 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 2500 | EcoPod N |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [16 empty] | Inspected | Sludge levels-- No Scum- 8-10" sludge in Septic tank. Initial Aeration Tank/septic 6" sludge, Ecopod Treatment 6-8" sludge, Tank #4 7-12", Pump Tank - Owner may replace some lids stainless screws. Pump runs when called by float.Alarm on blower sounds as does the pump alarm. Pump hrs 17055.19hrs vs 16,854.45 hours last yr vs 10,083.70 hrs 2 years, for total of 201 Hours, pump count 62,966 cycles vs 58,510 cycles vs 34,766, 2 years for total of 4,456 dose cycles to the drainfield- 3 Hp Pump , Alarm good. Good aeration in both tanks. Drainfield looks great covered in huge blackberries, may need to be cut back after berry season, zoner valve and spin filter all look ok. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | Jan 1 1900 9:30AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The inlet riser on the septic tank is damaged and requires replacement. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/14/2023 | Alternative |  | 09-125-142 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 08/14/2023 |  | 5.620000 | [5 empty] | Will be sent separately |  | BOD: 5.62 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/14/2023 | 12:00 AM
08/22/2023 | Alternative | RoutineScheduled Component Maintenance | 175-04-0023 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
06/23/2023 | Alternative | RoutineScheduled | 109-06-0001 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank Pumped | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 11500 | Microfast |  | Pump | Pressure | Trenches | Not Applicable |  | ["Control Operation","Level Sensor Operation"] | ["Control Operation","Level Sensor Operation"] | NA | [16 empty] | Inspected | System has continued to go into a high alert after and occasionaly. - Pump & Alarm and floats test opperational. operational - Possible float switch issue but they test good and the control box is new. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | 09:30 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend mowing the drainfield area to aid in evapotranspiration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/10/2023 | Alternative |  | SD-14-36 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Randy's Complete Water & Wastewater Services | 1942001335 | Randy | Gray | 1.000000 | 1000 | Easy Treat |  | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | 11:00 AM
03/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Advantex needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
03/17/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["Other"] | [] | YES | [17 empty] | Needs alarm & bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/18/2023 | Alternative | RoutineScheduled | 015-STS-333605 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
09/05/2023 | Alternative | RoutineScheduled | 182-05-0352 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Puraflo |  |  | Pressure | Pad | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | ["Attached Growth Medium","Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | [18 empty] | drip tube fixed near driveway. Peat to be addressed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | 12:00 AM
10/02/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-505 | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. All air release valves were open. In past visits, usually 1 or both return ARV's were stuck shut. Effluent level was elevated in the Microfast atu such that the recirc trough was completely underwater, and the effluent was cloudy. This indicates poor treatment. Dug up 2 different soggy spots in zone 1 (mound closer to the house). Emitters appeared to drip properly, but there was a layer of black sand (biomat) surrounding the tubing. This is further evidence that the treatment is not good and could be the reason for the soggy spots. Recommend a pump-out and chemical cleaning of the Microfast tank. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/01/2023 | 06:08 AM
03/28/2023 |  | RoutineScheduled | 185-STS-17513 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/28/2023 | 12:00 AM
10/23/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["Auxiliary Filter","Control Operation","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
08/04/2023 | Alternative | Reportable Incident | 550-STS-5879 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/04/2023 | Dec 30 1899 10:00AM
07/11/2023 | Alternative | RoutineScheduled | 165-STS-334090 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Best1 |  |  | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | adjusted timers | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | 12:00 AM
11/14/2023 | Alternative | RoutineScheduled | 108-05-0016 | Bath | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | RetroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["SludgeScum Accumulation","Effluent Screens","Auxiliary Filter"] | ["SludgeScum Accumulation","Effluent Screens","Auxiliary Filter"] | YES | [16 empty] | Pumped Out | The 1500 gallon microfast tank and 1000 gallon pump tank were both pumped and cleaned. The blower and spin filters were both pulled and cleaned. The controls were operating as designed. There were return effluent returning to the pump tank. The drip field was operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | 11:10 AM
09/27/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Hoot |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/27/2023 | Dec 30 1899 1:30PM
12/14/2023 | Alternative | RoutineScheduled | 121-STS-12055 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | 1.000000 | 1000 | MICROFAST |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | 12:00 AM
10/13/2023 | Alternative | Reportable Incident | 03-120-0390A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm call: -Upon arrival, I found the control panel in alarm condition indicating that the recirculation is in high level. Checked timers and confirmed that discharge has cycled since issues with leaking toilets. Checked recirculation and confirmed it was high level. Found that the RSV inlet/ outlet assembly was separating from mounting bracket resulting in excessive return into the recirculation tank. Spoke with Cindy and she is interested in the work but hesitant with the pricing. She was inquiring if any additional discounts could be applied. (edited) -Sent customer estimates -nothing approved as of yet | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | Dec 30 1899 8:51AM
03/09/2023 | Alternative | Routine/Scheduled | 151-00-297 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. Pumps to Community absorption field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | 08:00 AM
05/09/2023 |  | RoutineScheduled | 108-04-0009 | Bath | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 2.000000 | 2000 | Septic Tank Only | Peat Moss | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The two effluent filters were both cleaned. The peat moss was raked. The trays were sprayed off. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/03/2023 | 12:35 PM
12/01/2023 | Alternative | RoutineScheduled Component Maintenance | 177-18-0079-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
11/21/2023 | Alternative |  | 033-STS-90156 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend replacing one of the lids as it was slightly damaged by mower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/05/2023 | Alternative | Routine/Scheduled | 151-05-402 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating Biofilter - 5 modules - Peatmoss in fair condition - raked / turned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 08:00 AM
03/07/2023 | Alternative | Reportable Incident | {FIPSCode}-STS-17791 | Hanover | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Discharge | UV | 525.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | A new air compressor and control panel were installed. Re-routed air line from septic tank to pump tank. Cleaned effluent filter, RSV, and Recirculation pump vault filter. Brushed and flushed Advantex manifold. Replaced air vent screen. Cleaned UV crystal. Leaks were observed around the grommet of the splitter tee for the recirculation tank and in both pump tank access risers. These leaks could be the primary cause of the 231 overrides or the recirculation pump and the 60 overrides of the pump tank in the past 30 days. These leaks should be sealed. Installing a water meter on the water supply line would be helpful for detecting leaks. Another visit is planned on or around 4/12/2023 for replacing the UV bulb and taking samples for compliance testing. | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/13/2023 | Dec 30 1899 8:56AM
04/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/17/2023 |  | RoutineScheduled | 12-192-126 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Discharge | UV | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/17/2023 | 12:00 AM
09/11/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/11/2023 | 12:00 AM
12/08/2023 | Alternative | Routine/Scheduled | 810-STS-4028 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Fixed the grade on the pipe in the Clearstream. The timer was set at 3minutes every 1 hour changed it to 4 minutes every 1 hour. Set pressures - 40 on the pump and 20 on the return. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/08/2023 | Dec 30 1899 12:00PM
03/07/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | Jan 1 1900 12:26PM
03/11/2023 |  | Routine/Scheduled | 036-STS-34560 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 1250 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/11/2023 | Jan 1 1900 9:30AM
04/03/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | replaced part of conveyance line, d-box and small section of header lines. Septic system is in working condition at this time | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
08/25/2023 | Alternative | Reportable Incident | 234-16-385 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [16 empty] | Pumped Out | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/25/2023 | Dec 30 1899 9:00AM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
09/13/2023 | Alternative | RoutineScheduled | SD-03-307 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Routine Annual, nothing to report | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
01/27/2023 |  | RoutineScheduled | 027-STS-15561 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Clearstream |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 12 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/27/2023 | 12:00 AM
03/24/2023 |  | Routine/Scheduled | MS 62A Lot 11B | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/24/2023 | Jan 1 1900 1:40PM
05/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/05/2023 |  | Follow-Up | 041-STS-261452 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 2.000000 | 1500 | [7 empty] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Septic | [16 empty] | Old Dominion never called for startup. Needs pumpout ASAP, tanks full. Panel was never turn on, needed to be started up. Aquakear, 804-691-4221 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/05/2023 | Jan 1 1900 10:00AM
12/18/2023 | Alternative | RoutineScheduled | 182-12-0166 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 12:00 AM
06/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Peat modules are saturated. They need to replace peat fiber. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/26/2023 | 12:49 PM
11/20/2023 | Alternative | RoutineScheduled | 99-197-054 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 5.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/30/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - West Piedmont | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | BioMicrobics Fast 3.0 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | Bio-MicrobicsFast# 3741 0.75 Fast- Initial Visit- Septic Tank - Minimal scum on top and 10" slduge layer on floor- Treatment tank no scum and 26" light sludge- Pump tank 3" light sludge layer- Blower Motor pulls 3.4 Amps - Control box wont stop alarming unrelated to switch. Determined bad circuit board. Due to age of control box we will replace it with the newer style control box which elminate use of old mechanical air switch and wiring on our return visit. Good aeration in treatment tank. System is opperational but alarm control needs replacement | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/31/2023 | 09:30 AM
01/19/2023 |  | RoutineScheduled | 179-15-0193-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
05/04/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/03/2023 | Alternative | Routine/Scheduled | 133-STS-106418 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 4.000000 | 4800 | Microfast |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 35.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/03/2023 | 05:37 PM
08/08/2023 | Alternative | Follow-Up Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired UV unit. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/15/2023 | Dec 30 1899 1:44PM
07/17/2023 | Alternative | Routine/Scheduled | 228-19-0001 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | Dec 30 1899 11:25AM
06/08/2023 | Alternative | Routine/Scheduled | 036-STS-32843 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 2.5 minutes every 3 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | Dec 30 1899 11:30AM
07/20/2023 | Alternative | Routine/Scheduled | 06-190-103 | Surry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | Dec 30 1899 11:20AM
02/28/2023 | Alternative | Routine/Scheduled | 053-STS-10327 | Dinwiddie | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/28/2023 | Dec 30 1899 9:47AM
05/21/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | 12:00 AM
05/24/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 2.000000 | 2500 | Multiflo ATU |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Septic tank 1-2" scum and 6-8" sludge, Multiflo 1-2" scum and trace sludge on bottom. Pump tank has a trace of sludge. Alarm good, Owner Replaces chlorine anf dechlor as needed. some present on eaach. System alarm now opperational. Deck does not need pumping, | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
09/22/2023 | Alternative | RoutineScheduled Component Maintenance | 182-10-0170 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Recommend pump primary tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
01/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic/ Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 07/12/2023 | Sample Chamber | 13.000000 | [5 empty] | Attached to this report |  | Septic Tank-4"sludge 0"scum/ Microfast-4"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Blower controls and alarm functioning properly/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping Pump chamber. There is a fair amount of scum visible. Small roots were seen around the riser but does not appear to be an issue. Recommend monitoring and resealing if necessary. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/01/2023 | Alternative | Routine/Scheduled |  | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Biomicrobics MicroFAST |  | Pump | Pressure | Mound | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - normal level Aeration tank - normal level - recommend pumpout next service event - mixing present - compressor serviced. U.V. Disinfection - bulb and housing serviced. Pump tank - float sensors, pump and controls operating. LPP Mound - no indications of surfacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | 07:00 AM
10/02/2023 | Alternative | Reportable Incident | 157-10-0043 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Repair: -installation of a time-dose control panel -installation of 18" riser on the pump tank | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/12/2023 | 01:05 PM
12/08/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Customer Cheryl McRae & Kevin Tucker Property Address 11420 Edenberry Drive, Richmond, VA 23236 USA Technician Logan White Date Serviced 2023-12-08 Was customer present for service? Yes Type of System Alternative Type of AOSS System Norweco Septic Tank Condition of above Component Notes for above Component Normal level 6 in of sludge less than 1 in of solids No signs of infiltration Discharge/Pump Tank Condition of above Component Notes for above Component High level upon arrival due to pump failing 2 in of suspended solids Tested floats all working properly All plumbing intact Replaced pump and floats on site Returned back to Normal level No signs of infiltration Aeration Condition of above Component Notes for above Component High level upon arrival due to pump failing Pulled and cleaned aspirator it is functioning properly No signs if infiltration Returned to normal level Control Panel Condition of above Component Notes for above Component 120 volts coming in All visual and audible alarms functional Discharge pump pulled 10.08 amps Aspirator pulled 3.03 amps All components working as should Drip Field Condition of above Component Notes for above Component Pulled and cleaned disc filter No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 12:37 PM
06/02/2023 | Alternative | Routine/Scheduled | 166-03-094 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. BioFilter - 3 modules - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/02/2023 | 12:00 PM
07/07/2023 | Alternative | Reportable Incident | 166-10-075 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Broken diffuser. repaired diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
10/31/2023 | Alternative | RoutineScheduled | 015-STS-333395 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
08/30/2023 | Alternative | RoutineScheduled | 2007-143-0109 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out | Replaced Step 20 pump | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
08/07/2023 | Alternative | Reportable Incident | NYII-ATHMSE | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [16 empty] | Pumped Out | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/07/2023 | Dec 30 1899 2:00PM
06/13/2023 | Alternative | Routine/Scheduled | 17-120-0472AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 |  |  |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/13/2023 | Dec 30 1899 9:00AM
08/07/2023 | Alternative | Initial Visit | 810-STS-3759 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. The septic tank needs additional risers on it to properly inspected in the future. The timer is set to 1.5 minutes every 2 hours. Did not take samples. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/07/2023 | Dec 30 1899 12:30PM
12/06/2023 | Alternative | RoutineScheduled Component Maintenance | 179-07-0336-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Adjusted alarm to level as it had to much storage. Pump rate has slowed down. If pump slows down more during next years inspection we recommend replacing pump during next years inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
09/08/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-1992 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | Dec 30 1899 11:15AM
07/20/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-86718 | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump and effluent screen serviced. Treatment Module - media drapes and spray grid serviced. Community Drainfield - NOT Contracted. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | 07:00 AM
10/09/2023 | Alternative | RoutineScheduled | 061-STS-23409 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2000 | septic | Advantex | Gravity | Pressure | Drip | UV |  | [] | [] | YES | Musty | Clear | [15 empty] | Per 10/2023 Repair Letter from AOSS. 1. Plant check- Septic tank is a little high. Pulled filter and cleaned. 2. Sludge: 1' Scum: 3.5" Thick Scum 3. Adjust return flow rate back to septic tank 4. Pulled and cleaned floats and pumps 5. Checked alarms and UV Bulb, Cleaned vortex filter 6. Cleaned spray manifold, nozzles and Textiles 7. System passed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 09:10 AM
11/15/2023 | Alternative | Routine/Scheduled | 04-160-0051 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 141.000000 | None | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/15/2023 | 04:00 PM
03/14/2023 |  | Routine/Scheduled | 15-120-0050A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Aqua Klear |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/14/2023 | Jan 1 1900 7:48AM
05/15/2023 | Alternative | RoutineScheduled | 115-06-0044 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 300 | Best 1 |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | [15 empty] | Inspected | Sludge level-1-2" Scum layer on top- 24-28" Sludge layer on bottom in septic zone- Odd light gray color, may watch chemaical, cleaners and antibiotics and soaps. Treatment has good aeration and a trace of sludge - Clear effluent- Discharge Clear effluent, trace of sludge- Cleaned effluent screen -Grey slime on effluent brush, no odd smells, alarm test operational. Cleaned blower airfilter. on off Cycle works, | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
06/16/2023 | Alternative | Routine/Scheduled | 157-02-039 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - plastic - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | 09:00 AM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | EZ treat unit might need servicing in the near future | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
04/27/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The trees were removed from the ends of the lines. DSS verified that the lines were not impacted. The system appears to be functioning as designed at this time. Recommend homeowner monitor that area and notify if there are any changes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/07/2023 |  | RoutineScheduled | 179-18-0235-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend replacing the psi gauge in the drip dispersal system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/04/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump tank needs pumped out. Also the Hydrotek 4000n is not switching zones and is leaking. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
08/28/2023 | Alternative |  | 97-125-153 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | SANDFILTER |  | Gravity | Gravity | Mound | Chlorination | 200.000000 | ["Dispersal System Operation","SludgeScum Accumulation"] | ["Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 - Blue Crystal tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/28/2023 | 12:00 AM
04/05/2023 |  | Routine/Scheduled | 033-16-0028-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The septic tank needs to be pumped out and the Clearstream tank should be pumped as well. The timer is set to 9.5 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/05/2023 | 09:30 AM
01/31/2023 |  | Reportable Incident | 153-STS-20268 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced Step 20 EZ Treat pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 11:08 AM
08/04/2023 | Alternative | Pump-Out Only |  | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Processing tank pumped empty and serviced as recommend at last service visit. Processing tank refilled with fresh water for re-start. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | Dec 30 1899 11:00AM
03/14/2023 | Alternative | Routine/Scheduled | 093-10-0170 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | Dec 30 1899 2:37PM
11/14/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | Dec 30 1899 9:25AM
05/31/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-353 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump" ,"SludgeScum Accumulation"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the Advantex tank due to scum & sludge accumulation in the tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
02/22/2023 | Alternative | RoutineScheduled | 150-06-116 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/23/2023 | 12:30 PM
05/01/2023 |  | Routine/Scheduled | 11-120-0037A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/01/2023 | Jan 1 1900 4:42PM
07/11/2023 | Alternative | Routine/Scheduled | 06-142-0346 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | NO | [17 empty] | Manifold flushed, rsv cleaned. Found loose connection for middle float and fixed. System should return to normal operation. Alarm still will not sound. Control panel may be malfunctioning and will need to be replaced soon. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/11/2023 | Dec 30 1899 1:31PM
03/29/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
12/18/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 12:00 AM
08/02/2023 | Alternative |  | 06-125-086 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 08/02/2023 |  | 5.120000 |  |  | 15.400000 |  |  | Will be sent separately |  | BOD: 5.12 TSS: 15.4 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/02/2023 | 12:00 AM
11/21/2023 | Alternative |  | 167-STS-15634 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/21/2023 |  | 19.200000 |  |  | 11.400000 |  |  | Will be sent separately |  | BOD: 19.2 TSS: 11.4 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/21/2023 | 12:00 AM
06/23/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/30/2023 | 09:23 AM
10/30/2023 | Alternative | RoutineScheduled Component Maintenance | 099-06-0079-ST | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Root in 1 pod removed and added root destroyer to all 5 pods. Recommend to remove bushes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
06/09/2023 | Alternative | Routine/Scheduled | 115-STS-94982 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 3 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/09/2023 | 09:30 AM
04/26/2023 |  | Routine/Scheduled | 14-142-0271 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | UV |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [17 empty] | Filter cleaned. Uv bulb changed. Manifold flushed. Pulled roots from dbox. Dbox needs to be redone to keep roots from getting in. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | Jan 1 1900 1:45PM
08/09/2023 | Alternative | RoutineScheduled | 001-STS-92418 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 |  | FUJI CLEAN CEN 5 |  | Pump | Pressure | Mound | UV | 300.000000 | [] | [] | YES | [17 empty] | SLUDGE JUDGE 4" FROM BOTTOM 3" FROM TOP EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | 11:25 AM
06/20/2023 | Alternative | RoutineScheduled | 2001-143-0308 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Advantex |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","Auxiliary Filter","Recirculation Pump","Dispersal System Operation","Distribution Pump Operation","Control Operation","Level Sensor Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 12:00 AM
10/02/2023 | Alternative | RoutineScheduled Component Maintenance | 179-07-0027-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
01/17/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | None | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/13/2023 | 07:50 AM
03/18/2023 |  | RoutineScheduled | 133 18 0214 | Franklin | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 2.000000 | 4000 | EZ Treat Filter |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | [17 empty] | First Quarter 2023 inspection. Operator onsite several times since last inspection for repairing float trees. Repaired PVC spray laterals in EZ Treat filter #3 that appear to have frozen and split. Replaced dirty and clogged spray nozzles in all four treatment units. Grease trap #1 - First section- 6" crust, 18" in bottom, Second section - 8" crust, 24" in bottom. Grease trap #2 - First section- 2" crust, 20" in bottom. second section - 4" crust, 14" in bottom. Septic Tank- First section- 4" crust, 14" in bottom. Second section- 1" crust, 10" bottom. Anoxic tank/Septic tank #2- first section -skim crust, 12" on bottom. Second section- skim crust, 10" on bottom. Recirculation Tank- First section-0" crust, 10" on bottom. Second section- 0" crust, 0" on bottom. EZ Treat Tank #1- o" crust, 24" on bottom. EZ Treat Tank #2- o" crust, 28" on bottom. Discharge pump tank- 0" crust, 0" on bottom. Cleaned septic tank filters. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/16/2023 | 07:03 PM
05/16/2023 |  | RoutineScheduled | 179-18-0317-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The return line for the recirculation pump is cracked and should be repaired. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
12/06/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Upon arrival, I found the control panel was NOT in alarm condition and system in normal level. I checked and confirmed floats are functioning properly. I checked and confirmed discharge pump is functioning properly. I flushed and cleaned discharge pump. I flushed and cleaned vortex filter. Checked and confirmed control panel is functioning properly. Checked and confirmed draw down within discharge. The vortex flush returns to the head of the system and after a period of detention through the septic tank and processing tank it will return to the discharge tank. The discharge tank could pump itself out of high level and after the return flow reaches the discharge tank it could return it to high level. Spoke with homeowner and he stated they had about 35 people during thanksgiving weekend and recently had a day where they ran 10 loads of laundry. He confirmed that the alarms have been less frequent and less prolonged. Confirmed system is functioning properly and that it requires time to recover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 10:23AM
01/18/2023 |  | Reportable Incident | 228-12-0542 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm and red light. Serviced system. Checked the pump, panel, and floats (ok). Can not remove the filter in the Clearstream - flushed it out. The grade on the pipe in the Clearstream is not okay - needs to be addressed. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the UV light bulb. The septic tank needs additional risers on it to be properly inspected in the future. The timer is set to 1 minute every 1 hour. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | Jan 1 1900 12:45PM
04/27/2023 |  | RoutineScheduled |  | Bedford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Central | Acres of Virginia, Inc. |  | Melvin | Collins | 1.000000 | 500 | Multiflo |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation"] | [] | [18 empty] | Aerator not working customer has been informed | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/10/2023 | 11:00 AM
10/24/2023 | Alternative | RoutineScheduled | 12-192-022 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Pump | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/24/2023 | 12:00 AM
04/27/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
08/17/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0083-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"Auxiliary Filter"] | ["Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Owner called about a high level alarm that he was able to clear by cleaning the effluent filter (brush type), but then got a compressor fail alarm. Today, neither alarm was on and compressor was operating normally at 1.14 amps (1.4 A max). Replaced very dirty air filter. Replaced damaged plastic lid for inlet end of septic tank. Recommended pump-out of septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
05/26/2023 |  | RoutineScheduled | 179-07-0350-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Media looks better than last year, most filamentus bacteria died so treatment looks way better. Septic tank needs pump out both compartments due to solids. HL 82, LL 54, OVERRIDE 3101. Pump did 30 gallons per minute so we set up run time at 1m40s to get rid of 50 gallons per dose. Spoke to customer about pump out and he said he will call pumper. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
08/21/2023 | Alternative | RoutineScheduled Component Maintenance | SD-13-155 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection completed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
06/10/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 500 | MultiFlo |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | Annual inspection. 6" of accumulated solids in septic tank. 0" of solids in treatment unit. 2" of solids in discharge pump tank. Excellent aeration and excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/14/2023 | 07:03 PM
04/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Ecoflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/13/2023 | Alternative | Routine/Scheduled | 093-07-0284 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | Dec 30 1899 10:00AM
08/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
03/29/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
01/27/2023 |  | Routine/Scheduled | PPIE-9GGQCX | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/27/2023 | Jan 1 1900 12:24PM
12/14/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 |  | Microfast Drip |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | ["None"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/23/2024 | 12:00 AM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
10/31/2023 | Alternative | RoutineScheduled | 133-STS-97272 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/15/2023 |  | Routine/Scheduled | 228-05-1017 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | Jan 1 1900 1:35PM
10/30/2023 | Alternative |  | SP-05-688 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/06/2023 |  | RoutineScheduled |  | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 2-2 2-2 | 0-0 | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear |  |  | 7.000000 | [11 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/06/2023 | 09:00 AM
01/24/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | BLOWER POWER LIGHT OUT, Let us know if want us to repair | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
02/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | Dec 30 1899 2:21PM
07/18/2023 | Alternative | Follow-Up | 175-17-0488 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Level Sensor Operation","Disinfection","Attached Growth Medium","SludgeScum Accumulation"] | ["Attached Growth Medium","SludgeScum Accumulation","Level Sensor Operation","Disinfection"] | [18 empty] | Service Call Follow Up Only: Chemical cleaning on the Microfast ATU and pump out/ Replaced the faulty Salcor UV-Light unit with a Jet Retro- fit UV-Light/ Replaced faulty Off (red bottom) float. Media now clean, uv-light and floats were tested and functioning properly at this time. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/30/2023 | Alternative | Routine/Scheduled | 136-06-0109 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Biofilter - 4 modules - peatmoss in fair condition - raked / turned. Inspection port holding 7" of water !!! | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | 07:00 AM
03/27/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX25RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Routine Inspection. Septic tank 0" scum, Sludge level-4-9"Trace. Recirc zone has a 10" trace of sludge in Treatment tank and Discharge zone has 9" trace. Media looks clean and has good spray pattern. Cleaned eflfuent filter - minimally dirty. All Floats switched tested good. Pumps both opperate. System has traces of sludge does not need pumping. Advantex in Xlow use mode - Recirc pump has 42,025 Cycle count, Discharge pump has 2,377 cycles. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | 09:30 AM
03/31/2023 |  | Routine/Scheduled | 085-STS-33840 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level Processing Tank - normal level - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes a& spray grid serviced. UV - bulb and housing serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | Jan 1 1900 8:00AM
07/17/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-92199 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | None | Clear | [5 empty] | 07/17/2023 |  | 6.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:19 PM
07/24/2023 | Alternative |  | 17-100-0422 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [18 empty] | See Attachement | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 12:00 AM
09/12/2023 | Alternative | RoutineScheduled | 041-STS-260808 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Carrington Pump & Irrigation | 1942001121 | John | Carrington |  |  | Norweco |  | Pump | Pressure | Drip | UV |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Level Sensor Operation","Distribution Pump Operation","Effluent Screens","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation","Auxiliary Filter"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/01/2023 | Alternative |  | 085-STS-32437 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Norweco | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [18 empty] | We are pumping the septic tank on 6/12/23 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/02/2023 | 12:00 AM
09/14/2023 | Alternative | RoutineScheduled Component Maintenance | 033-17-0119-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
04/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/26/2023 | Alternative | RoutineScheduled | 151-13-0152 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Middle Module is fully saturated and has standing water to the lip of the module | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/04/2023 | 06:02 AM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/24/2023 | Alternative | RoutineScheduled | 04-177-1389 | Pulaski | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | King's Alternative Septic | 1942001112 | William | King, II | 1.000000 | 1000 | EcoFlow |  | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","Distribution Pump Operation"] | [] | NA | [17 empty] | Pump needs to be rewired and peat needs to be added. Owner was advised and plans to schedule the work to be completed. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/29/2023 | 12:00 AM
04/25/2023 | Alternative | Routine/Scheduled | 093-18-0087 | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Meet with the pumping company and pumped and cleaned the Clearstream tank, pumped and cleaned the pump tank, and pumped out the septic tank. Re-filled the pump tank with fresh H20 to flush out the drip tubing. Replaced the gauges - 1 - 100 lb and 1 - 50 lb. Set pressures - 40 on the pump and 20 on the return. Disconnected the pressure switch on the aerator. Need to go back to do a draw down test and set timer (was set to demand). Need to set it at 8 minutes every 1 hour. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/25/2023 | Dec 30 1899 10:00AM
02/14/2023 |  | RoutineScheduled | 12-113-145 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","Auxiliary Filter","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/14/2023 | 12:00 AM
01/12/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 1.000000 | 1000 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/22/2023 |  | Follow-Up | 175-02-0079 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Uncovered distribution boxes & removed tree roots. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
12/19/2023 | Alternative | Routine/Scheduled | TELS-ATRSLQ | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | Dec 30 1899 2:20PM
07/13/2023 | Alternative | RoutineScheduled Component Maintenance | 179-10-0242-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | We saw evidence of paper heavier than toilet paper in the septic tank. Only toilet paper should be flushed into your system. There are small trees growing on the drainfield. They should be removed and the drainfield maintained in a mowed condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
10/13/2023 | Alternative | RoutineScheduled | 109-03-0916 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | [16 empty] | Inspected | Septic tank under 1" scum and 10" slduge- pump tank 5" trace of sludge, much improved over last year. Pump Count 45955 vs 43727 last year = 2,228 pump cycle counts(2x last year's) and Pump hour meter 1213.17 hr vs 1141.83 hours last year = 71.54 hour run time this year which is much improved since new pump about 7 times less hours pumping this year. Pump runs, alarm is good, CLeaned effluent filter, Turned 4 of 5 peat tanks peat Due to hornets nest in the middle tank. Peat moss was turned and looks good! | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | 09:30 AM
05/25/2023 |  | RoutineScheduled | 033-STS-90197 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/21/2023 |  |  | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
06/19/2023 | Alternative | Routine/Scheduled | C 800-17-0078 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | Dec 30 1899 1:15PM
02/21/2023 | Alternative | Reportable Incident | 151-05-003 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Attached Growth Medium","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Peatmoss biofilter changeout. 02/21/2023 - pumped septic tank empty - replaced effluent screen. 02/24/2024 - biofilter media removed and replaced. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/27/2023 | 07:00 AM
05/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/26/2023 | Alternative | Reportable Incident | {FIPSCode}-STS-4015 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/26/2023 | Dec 30 1899 8:00AM
07/26/2023 | Alternative | RoutineScheduled Component Maintenance | SD-15-42 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Found timer enabler float and redundant off float hanging down. Siemens processor input screen showed timer float blinking on and off, and redundant off float stuck on - replaced both of them with a different brand of floats (Orenco). Added water to pump tank in order to run a test cycle. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:19 PM
09/06/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 |  | Microfast Drip |  | Pump | Pressure | Drip | Not Applicable | 600.000000 | ["Other"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | YES | [16 empty] | Inspected | NEEDS PUMPED!!!!!!!!!!!!!!!!!!!!!!!!! | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/26/2023 | 12:00 AM
01/20/2023 |  |  | 03-142-0494 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
05/12/2023 | Alternative | RoutineScheduled | 17-173-049 | Prince Edward | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Septic | Anua Pursys | Pump | Gravity | Mound | Not Applicable | 350.000000 | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/12/2023 | Dec 30 1899 9:00AM
05/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
07/25/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/01/2023 | 12:00 AM
05/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping prior to 2024 inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/15/2023 |  | RoutineScheduled | -STS-20150 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | ATU | Polishing Sand Filter | Pump | Pressure | Discharge | Chlorination | 500.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Recirculation Pump","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Recirculation Pump","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.400000 |  |  | 1.100000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/16/2023 | 12:00 AM
01/26/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/10/2023 | Alternative | RoutineScheduled | 04-160-0024 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | approx 2000gal | Whitewater |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | [] | NA | Septic | Dark Brown | [15 empty] | - blower is not functional, blower needs to be replaced - septic and pretreatment tanks need to be pumped/cleaned | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/19/2023 | 12:00 AM
04/25/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [7 empty] | 04/25/2023 |  | 10.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/22/2023 | 11:15 AM
09/11/2023 | Alternative | RoutineScheduled Component Maintenance | 182-06-0505 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Added riser and pumped primary tank Repaired valve box lid | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
06/14/2023 |  |  | 179-STS-87700 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
11/08/2023 | Alternative | RoutineScheduled Component Maintenance | SD-02-220 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 10:33 AM
07/13/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | 09:39 AM
03/16/2023 |  |  | 15-142-0177 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Aquaklear | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
10/31/2023 | Alternative | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [6 empty] | ["Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Control Operation","Distribution Pump Operation","Effluent Screens"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/29/2024 | 01:55 PM
12/16/2023 | Alternative | Reportable Incident Component Maintenance | 061-STS-21231 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Clearstream | none | Pump | Gravity | Drip | UV |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | High level alarm started after heavy rain last Sunday, alarm light on all week. Checked tanks for infiltration at topseams, but not pipe penetrations (too full). Observed infiltration at conduit fitting in atu and at conduit penetration in pump tank for uv lamp. Ground needs to dry up address those leaks. Bigger problem was caused by a steady stream of water coming into the pump tank through the return-to-septic line (well after the pump cycle ended). This is a common problem for continuous flush drip systems. A spring check valve was added to the line to allow flushing when pump is running, but stay shut with spring pressure between cycles. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
10/13/2023 | Alternative | Reportable Incident Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed N98 effluent pump & (2) control floats. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
03/11/2023 |  | Routine/Scheduled | 127-STS-34293 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/11/2023 | Jan 1 1900 10:00AM
12/04/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20395 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter"] | ["Effluent Screens" ,"Auxiliary Filter"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/30/2024 | 01:28 PM
07/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast .621 | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | [7 empty] | 07/27/2023 | Sample Chamber | 53.000000 | [5 empty] | Attached to this report |  | Septic Tank-12"sludge 4"scum/ Microfast-10"sludge 0"scum (Media is clogged requiring chemical cleaning) Pump Tank-2"sludge 0"scum/ Blower air cleaned and blower working correctly/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-1549 ETM-63h 25m/ Pump2-1534 ETM-62h 55m/ Peak-10/ High-10/ No breakout or spongy areas on the drainfield. Returned on 8/25/2023 for the chemical cleaning of the .625 Microfast Unit/ Pumped out the septic tank side and the Microfast side and adjusted the PH Balance/ Media is clear now a functioning properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/14/2023 | Alternative | Routine/Scheduled | 136-92-0365 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Pump | Pressure | Trenches | Not Applicable | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS LPD Field Primary septic tank - normal level Pump Tank - normal level - float sensors, pump and controls operating. LPD Field - exercised globe valves. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 11:00 AM
10/09/2023 | Alternative | RoutineScheduled | 101-11-0158 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Aquasafe |  | Pump | Pressure | Drip | Not Applicable | 150.000000 | [] | [] | YES | [17 empty] | Compressor changed May 2023 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/10/2023 | 11:55 AM
03/17/2023 |  |  | 18-142-0440 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Puraflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
03/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | 4 EZ treat nozzles required replacement. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/05/2023 |  | Routine/Scheduled | 06-142-0586 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Biofilter - 4 modules - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | Jan 1 1900 7:15AM
02/01/2023 |  | RoutineScheduled | 177-STS-87861 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 4.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Replaced alarm bulb for control panel on back of the store (for grinder pumps). Treatment in Microfast treatment zones and in discharge pump tank looked the best it has in many years. Hopefully this will still be the case this summer when the daily flow doubles. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
01/20/2023 |  | RoutineScheduled | 175- | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 11:08 AM
04/30/2023 |  | RoutineScheduled | 2008-143-0005 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 2.000000 |  | Biomicrobics Microfast |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Level Sensor Operation","Dispersal System Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 12:00 AM
04/28/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The level of the peat is low but there are no signs of ponding failure as described by the manufacturer. Recommend leveling modules that are slightly out of level. Informed homeowner that the peat is nearly the end of its functional life and that he should plan for replacement in the future. Informed the homeowner of alternatives to peat such as aerobic treatment that would get rid of the modules. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/01/2023 | Alternative | Reportable Incident | 234-17-352 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [17 empty] | Replaced aerator, on/off float, alarm float, alarm bulb and Zoehler 152 pump | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/01/2023 | Dec 30 1899 9:00AM
03/24/2023 |  | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced off float. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/31/2023 | Jan 1 1900 12:26PM
03/15/2023 | Alternative | RoutineScheduled | 159-17-0127 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Aquasafe |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | [] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
09/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-14"sludge 6"scum/ Microfast ATU-18"sludge/ Pump Tank-2"sludge/ Pump out required on the Septic-Microfast Tank/ Blower air filter cleaned and working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-7482 ETM-1823h 0m/ Peak-18 ETM-1098h 6m/ Watermeter-439,146.99/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/01/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Issues with the distribution boxes were fixed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/18/2023 |  | RoutineScheduled | {FIPSCode}-STS-12020 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination | 500.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens"] | YES | Musty | Clear | 7.900000 |  |  | 1.800000 |  | 03/21/2023 | Sample Chamber | 23.000000 |  |  | 3.900000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/03/2023 | 12:00 AM
04/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/30/2023 | Alternative | RoutineScheduled | 18-137-0103 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1500 | PuraSYS SBR |  | Pump | Pressure | Drip |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 12:00 AM
12/14/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | Dec 30 1899 12:55PM
12/09/2023 | Alternative | RoutineScheduled | 2050-03-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 6.500000 |  |  | 1.400000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/12/2023 | 12:00 AM
02/28/2023 |  | RoutineScheduled |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 3.000000 | 1250 | 0-3 | 0-0 0-0 2 pump tanks | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] |  | None | Clear |  |  | 5.000000 | [11 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/28/2023 | 11:00 AM
02/15/2023 |  | Routine/Scheduled | 04-163-0275 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | PremierTech, EFX | PremierTech, EFX |  | Gravity | Pad | Not Applicable | 750.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level Secondary septic tank - normal level - effluent screen serviced. Pump tank - float sensors, pump and controls operating. Biofilter #1 - peatmoss in good condition - raked / turned. Biofilter #2 = peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/16/2023 | Jan 1 1900 7:30AM
03/16/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.600000 |  | 50.000000 | [12 empty] | Advised client to have system pumped. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 08:40 AM
05/05/2023 | Alternative | RoutineScheduled | 136-96-1051 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Pad | Not Applicable |  | ["Other"] | ["Other"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | 12:00 AM
05/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/16/2023 | Alternative |  | 147-01-0190 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Parsley Septic Tank , Inc. | 1942001106 | James | Parsley | 1.000000 | 1500 | Advantex |  | Gravity | Gravity | Pad |  |  | ["Effluent Screens","Attached Growth Medium"] | ["Attached Growth Medium","Effluent Screens"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/06/2023 | Alternative | Routine/Scheduled | 157-07-0065 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. BioFilter - Peatmoss in poor condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/07/2023 | 08:30 AM
05/30/2023 |  | RoutineScheduled | 067-STS-39729 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | NONE |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | Battery backup replaced and control panel is operational. Meters - A - 940, B -670, C - 910. Tested both discharge pumps in "HAND", both pumping. Still no gallons pumped to drain field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/02/2023 | 07:03 PM
09/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Primary tank pumped | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
09/29/2023 | Alternative | Reportable Incident | {FIPSCode}-STS-54060 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Came out for septic to be looked at per our plumber due to sewer line holding water. Completed Annual Maintenance report and repairs. Report: -Septic Tank: Normal level 12 in of sludge 1 in of solids Pulled and cleaned filter Filter functions however is aged Riser is leaking -Discharge/Pump Tank: Normal level Pulled and tested floats all working properly Plumbing intact Pump working and properly moving water -Peat Moss: Peat moss is spent Module is severely cracked Tipping bucket and dispersal trays are intact -Control Panel: 120 volts coming in All visual and audible alarms working properly Pump pulled 5.39amps -Distribution Box: Unable to locate -Drain Field: No signs of surfacing Repairs: -installation of new control panel -installation of liberty pump -installation for cord kit for pump -installation of plumbing kit | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/12/2023 | 10:40 AM
07/15/2023 | Alternative | RoutineScheduled | 109-11-0358 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20 |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. Septic tank solids - 2" surface crust, 6" of solids in bottom. Cleaned recirculation pump solids basket filter. Flushed treatment unit spray manifold. Excellent treatment quality. Tested floats, pump and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/22/2023 | 07:03 PM
04/07/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 06/05/2023 | [7 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-87 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend replacing the Advantex module lid and module gasket as well as the riser lid over the recirculation pump. We also recommend repairing the cover of the Advantex module and replacing the 2' x 8" band that holds the pump tank junction box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
06/02/2023 | Alternative | RoutineScheduled | 031-STS-25917 | Campbell | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Central | Taylor's Septic Service | 1942001028 | Penny | Taylor | 2.000000 | 2000 | Septic Tank | Advantex AX20 | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["Effluent Screens","Dispersal System Operation","Control Operation"] | ["Dispersal System Operation","Effluent Screens","Control Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/02/2023 | 10:30 AM
04/05/2023 |  | RoutineScheduled | 132-04-0197 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/08/2023 | 12:00 AM
11/15/2023 | Alternative | Routine/Scheduled | DISCHARGE | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Gravity | Gravity | Discharge | Chlorination |  | None | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/15/2023 | 10:00 AM
02/20/2023 |  | RoutineScheduled | SWP-05-240 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Replaced alarm float for septic tank filter (vertical Reed switch). Cracked sample box same as last year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
10/04/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
02/20/2023 |  | Routine/Scheduled | 228-11-0244 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | EZ Treat Sandfilter |  | Pump |  | Drip | UV |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | Jan 1 1900 1:20PM
05/09/2023 | Alternative | Reportable Incident | 151-11-0022 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream. Changed the filter in the aerator. Installed an aerator rebuild kit. The timer is set to 3 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/09/2023 | 02:00 PM
06/29/2023 | Alternative | RoutineScheduled Component Maintenance | SD-11-225 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Microfast needs pumping. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/17/2023 | 12:46 PM
07/25/2023 | Alternative | RoutineScheduled Component Maintenance | 182-14-0238 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 | 2500 | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Effluent Screens" ,"SludgeScum Accumulation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Pumped primary tank and added media cleaner due to no airflow, rechecked system and proper aeration Replaced spin filter Replaced 2 pressure gauges | This AOSS should now return to normal function after having provided the above state routine maintenance | 08/23/2023 | 06:57 AM
09/29/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1875 |  |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["None"] | ["None"] | NO | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | Dec 30 1899 1:45PM
05/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/18/2023 | Alternative | Reportable Incident | 234-03-11049 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  |  |  | Control Operation | Control Operation | N/A | [17 empty] | Replaced mother panel in control panel | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/18/2023 | Dec 30 1899 2:00PM
04/06/2023 |  | Routine/Scheduled |  | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Delta Environmental Products, DF Series |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Primary septic tank - normal level Aeration - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | 07:15 AM
08/21/2023 | Alternative | RoutineScheduled |  | Shenandoah | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Sand |  |  | Gravity | Discharge | Chlorination |  | ["None"] | [] | [18 empty] | no discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/21/2023 | 12:00 AM
06/08/2023 |  | RoutineScheduled | 19-163-0105 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 4.000000 |  | EZ Treat |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Recirculation Pump","Control Operation","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | 12:00 AM
10/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston |  |  | Multiflo FTB | none | Gravity | Gravity |  | Chlorination |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/11/2024 | 01:04 PM
11/18/2023 | Alternative | RoutineScheduled | SD-05-06 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2000 | septic | puraflo | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/19/2023 | 08:40 AM
04/13/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | YES | [16 empty] | Inspected | Scum minimal-sludge 10" in Septic zone- Recirculation zone 4-5" sludge-- Discharge basin 6-8" sludge- - pumped last year- RTU131465, Good spray patteren, sprayed off media and cleaned spray nozzles.Cleaned Effluent Filter, Ran in test mode. FLoat switches test good.. Recirc pump Meter reading2894.9 hrs vs 2456 Hrs on recirc pump 15112 cycles vs 82538 cycles last year (returns to o after 99999), 445 hrs vs 399 Hrs on discharge pump 5445 cycles vs 4856 cycles. <imi,al alerts, Alarms on 3-1-23,2-28-23,12-22-22,11-24-22,8-1-22,7-31-22,5-27-22,5-24-22-3-24-22 -2-24-22, 1-2-22. Maybe due to rain infiltration | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
09/25/2023 | Alternative | RoutineScheduled | 08-183-181 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Pump | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Septic Tank Baffles","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Septic Tank Baffles","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets 18 - Bio Max tablets | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/25/2023 | 12:00 AM
12/15/2023 | Alternative | RoutineScheduled | 07-113-071 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/15/2023 | 12:00 AM
06/14/2023 | Alternative | Routine/Scheduled | 121-STS-12408 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | EZ Treat Sandfilter |  | Siphon | Pressure | Pad | Not Applicable |  | None | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | 6.700000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | 01:00 PM
02/07/2023 |  |  | 2005-143-0175 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Best One | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out | Replaced contactor in control panel 2/7/23 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/26/2023 | Alternative | Reportable Incident | 033-STS-88967 | Caroline | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | replaced bad uv bulb | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
07/11/2023 | Alternative |  | 033-12-0141-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
11/07/2023 | Alternative | RoutineScheduled Component Maintenance | 175-15-0477 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Microfast needs pumping. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/01/2023 | 10:33 AM
03/27/2023 | Alternative |  | 079-STS-31038 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Jackie and Michelle | Clark | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/03/2023 | Alternative | Initial Visit | 041-STS-260846 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 23.600000 |  | 2.000000 | [5 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 1 minutes 5 seconds every 2 hours. Took initial BOD and Fecal samples. NOTE - BOD sample was a tad high - system should function properly after service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/03/2023 | Dec 30 1899 1:30PM
11/06/2023 | Alternative | Routine/Scheduled |  | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 600 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | Dec 30 1899 10:30AM
08/23/2023 | Alternative | RoutineScheduled | 07-197-A5 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | JET |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] |  | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/23/2023 | 12:00 AM
08/07/2023 | Alternative | Routine/Scheduled | 550-STS-6409 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | Dec 30 1899 10:35AM
12/22/2023 | Alternative |  | 132-07-0200 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Royal | Duffy | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/03/2023 |  | Routine/Scheduled | 234-15-282 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2023 | Jan 1 1900 10:40AM
12/07/2023 | Alternative | RoutineScheduled | 065-STS-29253 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Carrington Pump & Irrigation | 1942001121 | John | Carrington | 2.000000 |  | Norweco |  | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Level Sensor Operation","Distribution Pump Operation","Dispersal System Operation","Control Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
07/12/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Gravity | Gravity | Trenches |  | 600.000000 | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/21/2023 | 01:37 PM
01/30/2023 | Alternative | RoutineScheduled | SD-13-168 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
11/10/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Pressure | Trenches | Not Applicable | 600.000000 | ["None"] | ["Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/04/2023 | 12:00 AM
01/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Air pre-filter cleaned as preventative maintenance. There are no mechanical fittings for the connections between the blower housing and the mechanical manway. Dirt penetration observed at these connections which means that groundwater could also penetrate the connections. Repair is required. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
09/06/2023 | Alternative | Routine/Scheduled | 151-15-0053 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Multiflo FTB |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 20.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | 05:30 PM
04/27/2023 |  | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | audible alarm replaced psi x2 | This AOSS should now return to normal function after having provided the above state routine maintenance | 05/22/2023 | 11:15 AM
03/14/2023 |  | Routine/Scheduled | 085-STS-32915 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 10000 | None | None | Pump | Gravity | Trenches | Not Applicable | 10000.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | routine Service - community pump station / absorption field. Pump Tank - normal level Pumps, float sensors, and controls oeprating. Hydraulic splitter valve serviced. Dboxes intact and balanced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | Jan 1 1900 9:30AM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump chamber lid should be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/23/2023 | Alternative | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced timer enable float under warranty. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | Dec 30 1899 12:26PM
03/17/2023 |  | Routine/Scheduled | {FIPSCode}-STS-2390 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/17/2023 | Jan 1 1900 8:50AM
02/20/2023 |  | RoutineScheduled | 2099-05-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.200000 |  |  | 1.800000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/22/2023 | 12:00 AM
10/11/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 8.010000 | [14 empty] | Fast blower not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 11/07/2023 | 02:30 PM
04/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection"] | ["BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Installed new UV bulb while on site for inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | Dec 30 1899 4:23AM
10/04/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank | Advantex Recirculation Tank | Pump | Pressure | Drip | UV |  | ["None"] | ["None"] | NO | [7 empty] | 10/04/2023 | Sample Chamber | 10.000000 |  | 1600.000000 |  |  |  | Attached to this report |  | Septic Tank-3"sludge 0"scum/ Advantex Tank-0"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ Drip Pump Counts: Pump-692 ETM-109.3h On-13m 35s Off-3h/ Watermeter-005591/ UV-Light sleeve cleaned/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/22/2023 | Alternative | RoutineScheduled | 101-09-0380 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | 12:00 AM
01/24/2023 |  | RoutineScheduled | SWP-04-937 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
10/30/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-24251 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | JET |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation","Disinfection"] | YES | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 8 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/30/2023 | 12:00 AM
05/03/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
11/01/2023 | Alternative | RoutineScheduled | 151-13-0138 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Laneview Environmental, LLC | 1942001775 | James | Boone | 1.000000 | 1000 |  |  | Gravity | Pressure | Pad | Not Applicable |  | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/09/2023 | 12:00 AM
08/30/2023 | Alternative |  | 101-07-0130 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Garrett | Barfield | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/23/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Advantax | Pump | Pressure | Drip | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | 1/2' scum 12" sludge in septic tank, Filter is clean, 6" loose sludge in filter side, little sludge in advantax. No alarms in log, Pressure gauge not working for return. Straighted up the vent pipe, no leaks in field, floats and alarms working | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/23/2023 | 02:00 PM
12/07/2023 | Alternative | RoutineScheduled | VAG408187 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty |  | 7.600000 |  |  | 1.170000 |  | 12/07/2023 |  | 11.000000 |  |  | 25.000000 | [5 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/12/2024 | 04:00 PM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | 182-10-0042 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
07/31/2023 | Alternative | RoutineScheduled | 166-15-133 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/24/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Whitewater ATU |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge level-Septic tank trace scum, layer- 10-12" sludge on bottom, Treatment Tank trace scum on top, 12-16" sludge on bottom, Clear effluent, Cleaned air filter, alarm works. Treatment has Good aeration, DF-50 tank and septic tank does not need pumping. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
11/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
09/22/2023 | Alternative | RoutineScheduled | 12-197-A2 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 10 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/22/2023 | 12:00 AM
06/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/07/2023 | Alternative | RoutineScheduled Component Maintenance | 047-STS-26420 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
03/15/2023 |  | Reportable Incident | 06-118-0094 | Charles City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | Control Operation | Control Operation | NO | [17 empty] | Homeowner reported sewage coming out of riser. Found that tanks were full and the system not operating automatically. Pumps would run manually and lights on motherboard showed proper float position. Could not connect to motherboard with phone. Replaced motherboard and system appears to be operating normally. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/15/2023 | Jan 1 1900 12:18PM
11/15/2023 | Alternative | Follow-Up Component Maintenance | 099-06-0337-SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to check drip rates after repairs were done to the system. While repairs were done drip rate was 3gpm follow up visit it was 5gpm. Design tate is 7.05. If rate doesnt increase more drip tubing may need to be bleach flushed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
02/07/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Peat is ponding and needs replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/29/2023 | 12:05 PM
04/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/05/2023 | Alternative | Routine/Scheduled | 17-174-0138 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 2.000000 | 2000 |  |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/05/2023 | Dec 30 1899 2:00PM
11/20/2023 | Alternative | Routine/Scheduled | 179.06.0005 | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Puraflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | 06:52 PM
04/12/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Recommended pumping of primary tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/22/2023 | 11:15 AM
12/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1000 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/01/2023 | Alternative | Initial Visit | 127-STS-34121 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream .Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 5.5 minutes every 2 hours. Did not take sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | Dec 30 1899 8:15AM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-90520 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | As noted previously, we recommend replacing the junction box lid on the pump tank & installing a union on the EZ Treat pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
03/30/2023 |  | Routine/Scheduled | NYII-B3WRY6 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | Jan 1 1900 11:35AM
12/21/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | Dec 30 1899 11:00AM
10/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | [7 empty] | 10/18/2023 | Sample Chamber | 6.000000 |  | 240.000000 |  |  |  | Attached to this report |  | Septic Tank-10"sludge 3"scum/ Microfast ATU-18"sludge/ Pump Tank-2"sludge/ Pump out required on the Septic-Microfast Tank/ UV-Light sleeve cleaned and functioning properly/ Blower air filter cleaned and working correctly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-6186 ETM-997h 19m/ Peak-11 ETM-106h 2m/ High-15/ Watermeter-036,872.10/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/11/2023 | Alternative | RoutineScheduled Component Maintenance | 109-STS-33764 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | 90 Day Inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
02/04/2023 | Alternative | RoutineScheduled | SD-03-278 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1250 | septic/trash | Microfast | Gravity | Pressure | Drip | Not Applicable |  | [] | [] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/09/2023 | 08:50 AM
05/02/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | [9 empty] | ["None"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | 12:00 AM
12/18/2023 | Alternative | Routine/Scheduled | 05-118-0013 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Trash Tank Condition of above Component Notes for above Component Water level normal. Inlet tee appears to be intact. Not due for pump out Recirculation Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Recirculation pump has exceeded life expectancy. Recirculation pump plumbing has exceeded life expectancy. Recirculation floats have exceeded life expectancy. Riser lids have degraded and may present a safety risk in the future RSV (Recirculating Splitter Valve) Condition of above Component Notes for above Component Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly Media Sheets Condition of above Component Notes for above Component Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Checked and confirmed spray height is good. Media lid safety support struts have failed. Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Control panel has exceeded life expectancy. Chlorination / Dechlorination Condition of Component Notes for above component Checked and confirmed feeders are free of debris and free flowing. Checked and confirmed tablets are present Direct Discharge Condition of above Component Notes for above Component Direct discharge is free of debris and free flowing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | Dec 30 1899 2:27PM
11/09/2023 | Alternative | RoutineScheduled | 133-STS-95162 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | sludge checked, system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/18/2023 | Alternative | RoutineScheduled | 182-98-0297 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [18 empty] | Blower off upon arrival. no return | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/18/2023 | 12:00 AM
05/23/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
06/29/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | [17 empty] | Septic Tank-10"sludge 6"scum/ Microfast-20"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ Pump out required on the Septic-Microfast Tank/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-2281 ETM-85h 13m/ Pump2-1605 ETM-81h 45m/ Peak-57/ High-22/ No breakout or spongy areas on the LPD Trenches | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance | 179-17-0126-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
09/12/2023 | Alternative | RoutineScheduled Component Maintenance | 179-10-0192-SPWT | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens"] |  | NO | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We replaced the bottom tow gloats in the Advantex RT unit. We also replaced the broken EZ set riser lid on the septic tank. With these repairs completed, system is operating as designed and in accordance with VDH regulations. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
08/22/2023 | Alternative | RoutineScheduled | 027-STS-15415 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/22/2023 | 12:00 AM
07/12/2023 | Alternative | RoutineScheduled | 031-STS-23976 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1000 | Septic Tank | Aquaklear | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["None"] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/03/2023 | 02:30 PM
11/27/2023 | Alternative | RoutineScheduled Component Maintenance | 179-16-0331-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend pumping the Advantex RT unit with our staff present to removed sludge that has built up in the tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
10/24/2023 | Alternative | RoutineScheduled | 13-120-0370A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/31/2023 |  | RoutineScheduled | 10-163-0023 | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Bionest |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Distribution Pump Operation","Recirculation Pump","BlowerCompressorAerator Operation","Control Operation"] |  | Musty | Clear | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/31/2023 | 12:00 AM
08/15/2023 | Alternative | RoutineScheduled | 153-STS-20178 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-8"sludge 1"scum/ / Pump Tank-2"sludge/ Puraflo peat fluffed in all 5 modules and it's in good condition/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-036080 ETM-0048561/ No breakout or spongy areas on the Puraflo Pad Area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 08:45 AM
08/21/2023 | Alternative | RoutineScheduled | 154-13-0182 | Louisa | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2000 | Eco-flow |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Auxiliary Filter","Attached Growth Medium","Other"] | NA | Musty | Clear | [14 empty] | Inspected | Sludge/Scum Accumulation - Septic Tank 12", Pump Station 6" Eco-Flow Tank deformed causing distribution trays to not be seated properly at the time of inspection forcing the effluent to the left side of the pod - Left side of pod heavily saturated, right side normal. Trays readjusted and peat moss raked out. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/21/2023 | 06:30 PM
01/16/2023 |  | RoutineScheduled | 107-06-0770 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/08/2023 | 12:00 AM
01/24/2023 |  | Follow-Up | SWP-01-219 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Installed inlet and outlet risers on septic tank. Installed outlet filter. Replaced 30? concrete lid on pump tank riser. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
09/07/2023 | Alternative |  | SWT-05-689 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
03/10/2023 |  | RoutineScheduled | 08-197-176 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Multiflo |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
02/15/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | A septic system inspection of a conventional gravity. The state requires that all conventional septic tanks be pumped out every 5 years and filed with the state and county. There is a 4" pvc pipe that sticks up near the house that is called a clean out. It is attached to the sewer line. We camera snaked the sewer line and found it clear. There is a 6" pvc pipe that sticks up in the yard that is the access to the septic tank. The septic tank had 3" scum and 6" of sludge at this time the septic tank does not need to be pumped out. We would recommend to add a riser and a filter to the outlet side of the tank. The filter will stop solids from getting into the drain field. The conveyance line was camera snaked and was clear. The 9-port plastic d-box was dug up it was 16" under the ground. All 8 header lines were camera snaked and clear. The drain field was probed and dry. At time of inspection all components were in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
02/23/2023 |  | Routine/Scheduled | 06-120-0906A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Aqua Klear |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/23/2023 | Jan 1 1900 4:15PM
08/25/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/03/2023 |  | RoutineScheduled | 077-09-0183-ST | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | As noted on last year's inspection. Roots are growing into the Puraflo modules. This may make it difficult to service the peat at some point in the future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
12/13/2023 | Alternative | RoutineScheduled Component Maintenance | 099-11-0042-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
10/31/2023 | Alternative | Pump-Out Only | 05-120-0304 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [16 empty] | Pumped Out | Supervised pump out of 1000 gallon septic tank performed by CWS | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | Dec 30 1899 9:24AM
05/05/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Advantex AX20 RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Septic tank under 1-2 " Scum and 24" sludge, In Treatment- recirc zone 6" sludge and 8" sludge on discharge. Clear effluent on top. Recirc pump operational. Alarm operational. Tested floats all good. Cleaned effluent filter in spectic tank.. level in tanks is correct. drainfield is cut over by the owner. Recirc pump run time 3727.3 hours and 89,934 cycles, 1 alarm in history on 12-25-22 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
04/26/2023 | Alternative | Routine/Scheduled | 800-STS-14427 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | Dec 30 1899 11:35AM
08/16/2023 | Alternative | Routine/Scheduled | 18-160-0058 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable | 87.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/16/2023 | 02:30 PM
07/20/2023 | Alternative | Reportable Incident | 234-13-242 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [17 empty] | Replaced aerator & float | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/20/2023 | Dec 30 1899 11:00AM
01/12/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Air filter cleaned as a matter of preventative maintenance. Blower contactor making buzzing noise when engaged, sign of normal wear. New contactor ordered, per homeowner request. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
08/31/2023 | Alternative | Routine/Scheduled | 234-17-0086 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the disc filter. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the UV light bulb. The UV needs a ballast. It was raining at the time of service - could not check the drainfield or mound. The timer is set to 8 minutes every 2 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/31/2023 | Dec 30 1899 10:30AM
12/07/2023 | Alternative | RoutineScheduled Component Maintenance | 175-01-0696 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/18/2023 | 08:36 AM
05/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/29/2023 | 12:05 PM
06/13/2023 | Alternative | Routine/Scheduled | 09-160-0029 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable | 319.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/13/2023 | 05:00 PM
08/05/2023 | Alternative | RoutineScheduled | 067-STS-38685 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | Modified Extended Aeration |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | YES | [17 empty] | Total flow to drain fields July 2023 -315,350 gallons. Average 8,760 gallons per day. All aspects of the system are operational. Wasting of settled mixed liquor from the clarifier to the digester and decanting of supernatant from digester are occurring regularly. Digester pumped out twice during the month. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | 07:03 PM
09/02/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex AX20RT |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 10" of accumulated solids in septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. 0" of solids in recirculation portion of treatment unit. 4" of solids in discharge portion of treatment unit. Removed roots from treatment unit that had gotten under the lid. Cleaned drip manifold spin filter. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/15/2023 | 07:03 PM
06/01/2023 | Alternative | RoutineScheduled | -STS-25583 | Amelia | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1250 | EcoPod |  | Pump | Pressure | Trenches |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/07/2023 | 12:00 AM
03/29/2023 |  | RoutineScheduled | {FIPSCode}-STS-8890 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 4 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/29/2023 | 12:00 AM
04/24/2023 |  | Routine/Scheduled |  | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Primary septic tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. Dbox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | 07:00 AM
05/08/2023 | Alternative | Routine/Scheduled | 05-137-0102 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable | 600.000000 | Recirculation Pump | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. - Recirc pump shows indication of high amperage and intermittent failure. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | Dec 30 1899 10:45AM
09/21/2023 | Alternative | RoutineScheduled Component Maintenance | 175-02-0499 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
08/25/2023 | Alternative | RoutineScheduled | 175-06-0465 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Gravity | Pressure | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/25/2023 | 07:45 AM
03/15/2023 | Alternative | RoutineScheduled | 159-17-0213 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Aquasafe |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | [] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
07/07/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Annual Inspection, no issues found | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/07/2023 | 12:00 AM
07/05/2023 | Alternative | Routine/Scheduled | 11-120-0142A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/05/2023 | Dec 30 1899 9:21AM
10/23/2023 | Alternative | RoutineScheduled | 04-197-139 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
11/11/2023 | Alternative | RoutineScheduled | SD-05-98 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2500 | septic | puraflo | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/19/2023 | 08:50 AM
04/11/2023 |  | RoutineScheduled | 177-STS-89454 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/09/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 12:00 AM
03/08/2023 | Alternative | RoutineScheduled | SD-11-169 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Clearstream | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Dusted off air filter for the air pump. Cleaned pump intake and spin filter. Observed roots growing into inlet end of tank at the top seam. Cedar tree that is only a few feet away needs cut down, and the topseam sealed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
05/17/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1875 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/20/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | 12:00 AM
12/05/2023 | Alternative |  | 169-STS-27621 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/05/2023 |  | 13.800000 |  |  | 6.800000 |  |  | Will be sent separately |  | BOD: 13.8 TSS: 6.80 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 12:00 AM
09/14/2023 | Alternative | Routine/Scheduled | 151-08-0032 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual maintenance: -Septic Tank: Normal level Heavy amount of sludge and dirt Less than 1" of solids. Pulled and cleaned filter -Discharge/Pump Tank: Normal level 2" of suspended solids All floats and pump functioning properly No signs of infiltration -Peat Moss: Tipping bucket and dispersal trays are intact and functioning properly Peat moss in good condition. Raked Peat moss out -Control Panel: 120v to each breaker All audible and visual alarms are functioning properly Pump pulled 10.94amps | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 12:52 PM
09/25/2023 | Alternative | Routine/Scheduled | S175-11-0046 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | Dec 30 1899 9:04AM
04/21/2023 | Alternative | Reportable Incident | 157-03-041 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm - light on. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the airline assembly and replaced the pump (Liberty 280). Pumped out the pump tank due to it being flooded. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/21/2023 | 12:00 PM
04/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/16/2023 | Alternative | RoutineScheduled | 061-17-506 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 6.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/27/2023 | 11:00 AM
04/19/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 | V | Septic Tank | Pump Tank to Puraflo Modules | Pump | Gravity | Discharge | UV |  | ["Attached Growth Medium","Disinfection"] | ["Attached Growth Medium","Disinfection"] | YES | [17 empty] | Septic Tank-4"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Puraflo Peat turned and peat in good condition/ Controls, pumps, floats and alarms functioning properly/ UV-Light sleeve cleaned and working correctly/ Counts: Pump1-7101 ETM-63h 52m/ Pump2-7052 ETM-63h 15m/ Dose-37.5 / Pump Rate-68.5gpm On-32s Off-2h | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
09/05/2023 | Alternative | RoutineScheduled | 13-142-0111 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 12:00 AM
10/24/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1000 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [7 empty] | 10/24/2023 | Sample Chamber | 79.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/27/2023 |  | RoutineScheduled | 099-STS-92110 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | The water in the pump tank appeared to be murky from mud. We did not see any evidence the tanks are leaking. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
10/20/2023 | Alternative | RoutineScheduled | 003-STS-34573 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco | Norweco | Gravity | Pressure | Mound | Not Applicable | 750.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | 12:00 AM
10/10/2023 | Alternative | RoutineScheduled | 13-163-0133 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/05/2023 | Alternative | Initial Visit | 800-STS-15507 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Fuji |  | Pump | Gravity | Pad | Not Applicable | 600.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | System Commissioning / Start-up. Primary septic tank - FOG present - effluent screen serviced. Trash Tank - normal level Aeration Tank - mixing present - compressors (2) serviced. Clarifier - sludge return operating. Pump Tank - float sensors, pump and controls operating. DBox - concrete - intact - NOTE - indications of vehicle damage to sidewall of pad / bed. Inspection report with photos emailed to AOSE, PE and Local HD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | Dec 30 1899 11:00AM
03/11/2023 |  | RoutineScheduled | 133 12 0211 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 10" of accumulated solids in septic tank. 0" of solids in discharge pump tank. Cleaned recirculation pump basket filter. Flushed treatment unit spray manifold. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 07:03 PM
07/10/2023 | Alternative | Routine/Scheduled | 228-13-0515 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | Dec 30 1899 12:10PM
03/30/2023 | Alternative | Routine/Scheduled | 13-160-0012 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 06:30 PM
12/04/2023 | Alternative | Reportable Incident | 06-184-5006 | Scott | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation"] | NA | Musty | Clear | [15 empty] | Installed aerator, put plug on, put up discharge sign 5 - Blue Crystal tablets installed 15 - Bio Max tablets installed | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 12/04/2023 | 12:00 AM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | 175-02-0781 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump"] | ["Level Sensor Operation" ,"Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Septic/recirc tank will probably need pumping by next year's inspection. Owner had dug up surge box and d-box to facilitate this year's inspection (about 7" below grade). Other than a corner missing from the surge box lid, both boxes were in great shape and the clarity of effluent inside was amazing. Owner to cover boxes up again. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
02/10/2023 |  | Routine/Scheduled | C 800-13-0030 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash Tank - normal level. Aeration Tank - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. U.V. - bulb and housing serviced. Drip - headworks serviced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/13/2023 | Jan 1 1900 9:30AM
09/12/2023 | Alternative | RoutineScheduled | 001-STS-91843 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 2.000000 | 2000 | Septic Tank | PuraFlo | Gravity | Pressure | Pad | Not Applicable | 990.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/03/2023 | 10:25 AM
07/08/2023 | Alternative | RoutineScheduled | SD-14-91 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1000 |  | Clearstream | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | 08:35 AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance | SP-05-227 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Minor settling on pump tank inlet pipe. Does not appear to be causing problems at this point. Put dial-a-flow (distribution box) that was turned up last year back into level with others. If line gets saturated again, additional investigation/repairs will be needed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 07:01 AM
11/30/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/10/2023 | Alternative | Routine/Scheduled | 810-STS-4065 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | Dec 30 1899 10:08AM
04/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
12/27/2023 | Alternative | RoutineScheduled | 107-98-0273 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 1360.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/15/2024 | 10:35 AM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/27/2023 | Alternative |  | 132-14-0068 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Tasha & Clint | Birckhead | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/20/2023 | Alternative | Reportable Incident | 097-STS-99941 | King & Queen | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | COSS - Repair Install - VDH HDID 149-22-059 Pumped primary septic tank for installation of repair. Installed new 1000 gallon pump tank. Installed new conveyance line. Installed new 8 port concrete distribution box Installed three new laterals 65' x 3' in accordance with permit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/21/2023 | 09:00 AM
12/11/2023 | Alternative | Routine/Scheduled | 228-03-0176 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/11/2023 | Dec 30 1899 11:40AM
06/27/2023 | Alternative | Initial Visit | 163-STS-335141 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation","Effluent Screens"] | ["Control Operation","Effluent Screens"] | YES | Musty | Clear | [5 empty] | 06/27/2023 |  | 16.600000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/06/2023 | 12:00 AM
05/03/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Mound | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Drip loop was repaired. System is functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/16/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
04/03/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | DSS repaired break in tubing. System should return to proper function. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/20/2023 | Alternative | RoutineScheduled | 107-06-0043 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Pressure | Trenches | Not Applicable |  | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2024 | 12:00 AM
12/20/2023 | Alternative | Routine/Scheduled | 157-13-0054 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component Normal level 14 in of sludge 1 in of solids Pulled and cleaned filter No signs of infiltration Discharge/Pump Tank Condition of above Component Notes for above Component Normal level 4 in of suspended solids Tested floats and pump all working as should however floats are four years old All plumbing intact and pump working as should No signs of infiltration Control Panel Condition of above Component Notes for above Component 120 volts coming in all visual and audible alarms functional Pump pulled 6.37 amps All components working as should Distribution Box Condition of above Component Notes for above Component Normal level 4 lines all intact and taking water properly Speed balancers intact and functional Drain Field Condition of above Component Notes for above Component No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | 08:32 AM
11/15/2023 | Alternative | Reportable Incident | C102-06-0065 | Alleghany | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | Delta White Water | Pump | Pressure | Drip | Not Applicable |  | ["SludgeScum Accumulation","Effluent Screens","Auxiliary Filter"] | ["SludgeScum Accumulation","Effluent Screens","Auxiliary Filter"] | YES | [16 empty] | Pumped Out | The effluent filter and spin filter were both pulled and cleaned. The home owner had a toilet stick and was running. This caused the scum layer to wash over to the pump tank and it caused filter blockage. The pump tank and treatment units were both pumped and cleaned. The controls were operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/27/2023 | Dec 30 1899 10:20PM
03/01/2023 |  | RoutineScheduled | 179-13-0169-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
10/23/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-92506 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [5 empty] | 10/23/2023 |  | 6.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Treatment is clear but could be better, system has wipes ans alot of paper that could be messing up the treatment. Spoke to customer about it. Part of drainfield is over grown but customer is weedwacking little at a time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
12/20/2023 | Alternative |  | 17-177-1047 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | 2.000000 | 2000 | Aquasafe | [6 empty] | [] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | Septic | [16 empty] | - at last inspection, blower was not functional - customer replaced with own blower | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | 12:00 AM
11/29/2023 | Alternative | Routine/Scheduled | 166-06-191 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level Less than 1" of solids with 6" of sludge -Discharge/Pump Tank: At normal level Pump and floats functioning properly Has 2" of sludge -Aeration: At normal level Aerator is doing its job -Air Pump/Blower: Working properly Pulled and cleaned filter -Control Panel: Both panels working poorly Discharge pump pulling 9.2amps -Drip Field: Showing no signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 02:47 PM
04/13/2023 |  | Routine/Scheduled | 087-STS-6561 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | ["Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Pumped trash tank and processing tank empty and serviced as recommended during last service event. Installed new float sensors, and pressure guages. Refilled with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 09:30 AM
07/31/2023 | Alternative | RoutineScheduled | 11-100-0201 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn |  | 2232 | CLEARSTREAM |  | Pump | Pressure | Pad | UV | 600.000000 | [] | [] | NA | [16 empty] | Pumped Out | RECENTLY PUMPED. NO SLUDGE-EVERYTHING WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/03/2023 | 02:20 PM
04/11/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | EcoPod | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The blower was repaired. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance | 175-06-0218 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Level Sensor Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Drainfield has wet spot. ATU & enable floats needs replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/17/2023 | 12:46 PM
11/02/2023 | Alternative | Routine/Scheduled | S15-111-0106 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Distribution Pump Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | Dec 30 1899 12:00PM
09/27/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:00 AM
06/15/2023 | Alternative | RoutineScheduled Component Maintenance | 175-11-0491 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 2.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/07/2023 | 06:25 AM
05/22/2023 | Alternative | Routine/Scheduled | 166-09-034 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Routine Service. Processing Tank - pumped and serviced - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes and spray grid serviced. Pump Tank - float sensors, pump and controls operating. NOTE - Client is refilling system - not responsible for low level alarms or tank floating! | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 07:00 AM
05/12/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Repaired broken air relief valve. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
05/18/2023 | Alternative | RoutineScheduled | 18-100-0176 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 500 | AQUASAFE |  | Pump | Gravity | Mound | UV | 450.000000 | [] | [] | [17 empty] | Pumped Out | REPLACED AS 600 REBUILD KIT AND PUMPED SLUDGE. EVERYTHING WORKING AS IT SHOULD. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/21/2023 | 02:30 PM
05/26/2023 | Alternative | Routine/Scheduled | 166-11-182 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash Tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - air locked - repaired - float sensors, pump & controls operating. Absortption field overgrown. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 12:00 PM
10/05/2023 | Alternative | RoutineScheduled Component Maintenance | SD-08-189 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Recirculation Pump" ,"Control Operation" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"Recirculation Pump" ,"Control Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Zoner rotated properly this year. Replaced cracked pvc coupling that was allowing Advantex vent to wobble (and possible point of infiltration). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
10/17/2023 | Alternative | RoutineScheduled Component Maintenance | 182-98-0593 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 10/17/2023 |  | 2.000000 | [5 empty] | Will be sent separately | Inspected | lab sample normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
08/11/2023 | Alternative | Reportable Incident |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Pump | Pressure | Trenches | Not Applicable | 450.000000 |  | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | AOSS - installed cannister effluent screen in outlet of septic tank. Installed access riser on septic tank. Replaced pump, float sensors and controls with new. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/16/2023 | 06:45 AM
01/16/2023 |  | Reportable Incident | 179-06-0324-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | On site to address high level alarm. Owner stated it started a couple of weeks ago. Effluent was up into the atu and drip tank risers, and soil was soggy around the atu risers. Pilot fuse was blown in the drip panel so no automatic cycles were taking place. Replaced the fuse and started a pump cycle. Big leak observed coming from cracked sch 80 fittings between the flow meter and zone solenoid valve bodies. Replaced those fittings and started a drip cycle. Another leak observed coming from disc filter housing #2. Replaced that filter housing and started the pump again. No further leaks seen, but flow meter was not turning. Flow meter and fittings were damaged by freezing effluent. Replaced the flow meter as well as the heater strip in the hydraulic unit. Pilot fuse did not blow again during all the testing. Owner commented that she had gotten other high level alarms after heavy rains. Buried concrete wedge lids are a very common leak point, and should all be replaced with plastic risers to grade with plastic lids. Deck will need to have hatches made to access these lids. All tanks need to be inspected for points of groundwater infiltration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
04/26/2023 | Alternative | Pump-Out Only | 03-160-0280 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [17 empty] | Pumped Out | - pumped/cleaned septic tank and pretreatment tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/27/2023 | 12:00 AM
08/01/2023 | Alternative | RoutineScheduled | 115-04-0241 | Campbell | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1000 | Septic Tank | MicroFast 0.5 | Pump | Pressure | Drip | Not Applicable | 300.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Other"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Other"] | NA | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/21/2023 | 04:00 PM
03/10/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | Jan 1 1900 7:20PM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
08/31/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 12:00 AM
02/08/2023 | Alternative | Initial Visit | 136-00-0637 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 300.000000 | ["Attached Growth Medium","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Residence System - Initial Visit. Primary septic tank - requires pumpout Processing tank - RSV, recirc pump and effluent screen serviced. Treatment Module - media drapes bridging / sagging - require replacement. Pump Tank - float sensors, pump and controls operating - NOTE - control panel seal is leaking, allowing moisture inside of panel - recommend replacing. DBox & Absorption field NOT FOUND! NO Service conducted on the Inn @ Warner Hall. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/09/2023 | 09:30 AM
05/18/2023 |  | Routine/Scheduled | 234-18-077 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/18/2023 | Jan 1 1900 11:50AM
04/26/2023 |  | RoutineScheduled | 14-192-113 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 2 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/26/2023 | 12:00 AM
07/17/2023 | Alternative | Routine/Scheduled | 234-16-201 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | Dec 30 1899 10:14AM
01/27/2023 |  | Routine/Scheduled | S 800-13-0257 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | EcoPod |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/27/2023 | Jan 1 1900 2:36PM
06/22/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20191 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | 11:24 AM
10/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired pressure gauge and top recirc float Homeowner has agreed to install effluent filter | This AOSS should now return to normal function after having provided the above state routine maintenance | 12/06/2023 | 03:05 PM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
08/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 2.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | grease tank, septic tank needs pumped out | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
03/16/2023 |  | Routine/Scheduled | 127-STS-31894 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1500 | Aqua Klear |  | Pump | Gravity | Trenches | Not Applicable | 150.000000 | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [7 empty] | 03/16/2023 | Pump Chamber | 19.000000 | [5 empty] | Will be sent separately |  | Air compressor filter was cleaned. Sample was taken for BOD5 test for routine compliance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/05/2023 | Jan 1 1900 9:06AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/15/2023 | Alternative | Follow-Up Component Maintenance | SD-04-33 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced Puraflo peat in (4) modules. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
01/06/2023 |  | RoutineScheduled | 11-184-009 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Sand Filter |  | Gravity | Gravity | Mound | Not Applicable | 200.000000 | ["Auxiliary Filter","Dispersal System Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/06/2023 | 12:00 AM
08/08/2023 | Alternative | RoutineScheduled | 06-184-5002 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/08/2023 | 12:00 AM
08/10/2023 | Alternative | Pump-Out Only |  | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 2000 | Clearstream | Clearstream | Pump | Pressure | Trenches | Not Applicable | 1250.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] |  | N/A | [16 empty] | Pumped Out | Owner pumped tanks in "HAND" - wanted ONLY the primary septic tank and grease trap pumped. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 12:15 PM
03/01/2023 |  | Follow-Up | 175-12-0084 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001068 | David | Stewart |  | 2500 | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["SludgeScum Accumulation" ,"Auxiliary Filter" ,"Disinfection" ,"Dispersal System Operation"] | ["SludgeScum Accumulation" ,"Auxiliary Filter" ,"Disinfection" ,"Dispersal System Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Restored squirt height to 4 feet in Advantex pod by repeated flushing and brushing of the laterals. Cleaned drip pump intake and the spin filter, then bleach-flushed the drip system. Added a check valve to the drip pump line after water started running backwards through the flow meter. Rates did not change at all. In light of that, the rate reductions are probably due to crimped tubing. Owners are not getting alarms, and drip mound is not malfunctioning so no further recommendations are made at this time. Removed recirc floats, biotube filter, pump and pump vault to allow the pumper to do a proper pump-out of the Advantex septic tank. A complete pump-out of the discharge pump tank was also done. Removed the concrete wedge lid from pump tank inlet end, and installed a plastic riser and lid (the concrete lid was allowing infiltration.) Video inspected the the drain pipe from the RSV - no problems found. Relocated Orenco uv assembly from a stand-alone basin to the inlet end of the discharge pump tank. This will allow for much easier access to the uv, proper sample collection, and better pump-outs. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
05/22/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge level-some scum-20-24" sludge in Septic zone of tank - Recirculation zone 10-12" Sludge- Recirculation Pump counter 566,195 vs 541,867 (24,328 cycles since last year) Minute meter 282817 vs 270,685 = 12,132 min or sbout 202 hours since last visit -Owner Cleaned Effluent filter and Biofilter, Brushed and flushed manifold, cleaned rsv, and sprayed off media, Owner cleans system twice a year. floats switches appear to work. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
02/15/2023 |  | RoutineScheduled | 179-16-0179-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | YES | Musty | Cloudy | [5 empty] | 02/15/2023 |  | 176.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Removed a lot of trash out of RT dozing pump housing, recommend getting it pumped due to some much trash. RT thank needs pumping due to sludge and quality of water. RT tank was on high level when we arrived due to a bad float, replaced float (pump on/high level alarm). Will send proposal for pump out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
08/10/2023 | Alternative | RoutineScheduled | 001-STS-92420 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 750 | AQUQASAFE |  | Pump | Pressure | Mound | UV | 450.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | SJUDGE JUDGE 2" FROM BOTTOM EVERYTHING IS WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 11:15 AM
12/15/2023 | Alternative | Routine/Scheduled | 09-160-0029 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable | 246.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/15/2023 | 03:15 PM
11/17/2023 | Alternative | RoutineScheduled | 11-142-0031 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/20/2023 | Alternative | RoutineScheduled | 06-192-080 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Level Sensor Operation","Control Operation","BlowerCompressorAerator Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | 12:00 AM
02/10/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-24251 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/10/2023 | 12:00 AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/13/2023 |  | RoutineScheduled | 101-01-0719 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | MicroFast |  | Gravity | Pressure | Drip | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/19/2023 | 12:00 AM
08/26/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex AX20RT |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. Cleaned recirculation pump intake screen. Cleaned treatment unit spray "spinners". 1" of solids in recirculation portion of treatment unit. 14" of solids in discharge portion of treatment unit. Excellent treatment quality. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/22/2023 | 07:03 PM
08/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 2000 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/06/2023 | Alternative | Reportable Incident | 157-12-0113 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm Call: -Customer stated neighbor called in alarm light being on Upon arrival found alarm light to be on and system was at normal level Tested all components and found air pump was functioning properly, discharge pump was functioning properly, discharge float were functioning properly however they are Aged alos found the alarm was due to Bad alarm float in aeration tank Gave customer options and she approved to replace the aeration high level alarm float only. Replaced float on site. All components are functioning properly and system was at normal level Upon departure | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/20/2023 | 09:48 AM
01/24/2023 |  | Routine/Scheduled | 800-04-0179 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 11:48AM
09/06/2023 | Alternative | Pump-Out Only | 228-06-0698 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | Dec 30 1899 11:00AM
09/25/2023 | Alternative | Routine/Scheduled | 093-07-0193 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | Replaced aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | Dec 30 1899 11:15AM
02/07/2023 | Alternative | RoutineScheduled | 047-STS-25519 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | Musty | Clear |  | 7.470000 |  |  |  | 02/07/2023 | Sample Chamber | 4.000000 |  | 38.300000 | 1.900000 |  |  | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
08/28/2023 | Alternative | RoutineScheduled Component Maintenance | 107-04-0483 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Dispersal System Operation"] | ["Control Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Recommend to have pump vault and have primary tank pumped due to high levels of solids | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
06/29/2023 | Alternative | RoutineScheduled Component Maintenance | 033-06-0480-ST | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Effluent Screens"] | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
10/09/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Ace Contracting Services, Inc | 1942001120 | Lawrence | Fellenz Jr. | 1.000000 | 0 | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected | Replaced Lid To One Of The Tanks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 03:09 AM
06/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The breaker for the blower had tripped and it was reset at time of inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/13/2023 | Alternative | RoutineScheduled | 107-94-0338 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 09:30 AM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance | 177-16-0230-SP | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | There is effluent surfacing in the dispersal area. We recommend contacting the Alternative Onsite Soil Evaluator (AOSE) who designed the system, for further evaluation and/or repair options. A&S Environmental (John Sawdy) can be reached at (540) 371-6630. 9/19/23 - MW reached out to A&S | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 09/01/2023 | 07:38 AM
10/18/2023 | Alternative | Pump-Out Only | 127-STS-32683 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/28/2023 | Alternative | RoutineScheduled Component Maintenance | 179-18-0386-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Level Sensor Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection and follow-up. Recirc float had not registered last week because it had gotten wedged up against the sidewall of the pump vault. Rotated float collar on the float collar so that it was free to swing. Discharge tank was in low level alarm. The bottom float was stuck on, and the timer enabler float was intermittently closing. Removed the original narrow angle Connery floats and installed 2 new Orenco float switches. The Connery wide angle float switch for the high level alarm is still working fine. Replaced the broken vent cap for the Advantex AX20. During the drip test cycles, the filter flush valve stuck open and then the field flush valve stuck open. Cleaned small debris from under the diaphragms and restored operation. Added some fresh water to the discharge tank to take it out of low level status. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:19 PM
08/02/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
04/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank lid has some cracks. Strongly recommend before it becomes a safety hazard. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/10/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 3000 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [7 empty] | 01/10/2023 | Sample Chamber | 33.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/03/2023 | Alternative | Reportable Incident | 228-17-0153 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. The septic tank needs additional risers on it to be properly inspected. The Clearstream tank and pump tank should be pumped out. The timer is set to 2 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/03/2023 | Dec 30 1899 9:00AM
05/12/2023 |  | RoutineScheduled | 107-07-0649 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 2000 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","SludgeScum Accumulation","Effluent Screens","Control Operation"] | ["Auxiliary Filter","SludgeScum Accumulation","Effluent Screens","Control Operation"] | YES | [16 empty] | Pumped Out | The MicroFast tank and the pump tank were both pumped and cleaned. The blower and spin filter were both cleaned. The timer enable float was bad at the time of inspection so it was replaced. There were no visible leaks in the drip field. There was return effluent returning to the pump tank so the drip field was operating as designed. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/06/2023 | 09:50 PM
08/23/2023 | Alternative | Routine/Scheduled |  | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Delta Environmental Products, DF Series |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating - NOTE - discharge pump operating at higher than normal amperage - indicates end of life. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | 09:45 AM
03/02/2023 |  |  | 124-STS-2379 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 2250 | 1250 | 1000 | Siphon | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Recirculation Pump"] | YES | None | Black | 8.000000 |  | 7.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/02/2023 | 03:00 PM
02/03/2023 |  | RoutineScheduled | 06-195-518-DIS | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 2 Chlorine 4 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/03/2023 | 12:00 AM
07/26/2023 | Alternative | Routine/Scheduled | 234-03-11324 | Chesapeake | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Chesapeake | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Discharge | Chlorination | 450.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. Biofilter - peatmoss in good condition - raked / turned. Chlorinator - housings serviced - tablets replaced. Discharge Point - clear of debris, freeflowing, signage intact. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/27/2023 | Dec 30 1899 9:00AM
11/17/2023 | Alternative | RoutineScheduled Component Maintenance | 177-06-0247-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Gravity | Gravity |  | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection"] | ["BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
03/15/2023 |  | RoutineScheduled | 001-STS-92578 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Bundick | Pump | 1.000000 | 749 | Septic Tank | Fuji Cen-5 Unit | Gravity | Pressure | Pad | UV | 450.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/27/2023 | 12:10 AM
12/11/2023 | Alternative | RoutineScheduled Component Maintenance | 165-STS-334752 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
03/22/2023 |  | RoutineScheduled | 167-STS-16735 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 4 Chlorine 5 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/22/2023 | 12:00 AM
08/09/2023 | Alternative | Routine/Scheduled | 177-08-0216SR | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 400 | Hoot |  | Pump | Pressure | Mound | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Air filter replaced. Disc filter cleaned. System appears to be operating normally | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | 11:17 AM
11/11/2023 | Alternative | RoutineScheduled | SD-07-289 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | ATU | Polishing Sand Filter | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation"] | NA | Musty | Clear | 7.500000 |  |  | 1.800000 |  | 11/13/2023 | Sample Chamber | 2.000000 |  |  | 12.800000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/01/2023 | 12:00 AM
05/02/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
07/14/2023 | Alternative | Pump-Out Only | 700-STS-7253 | Newport News | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Sandfilter, Recirculating |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Attached Growth Medium","Auxiliary Filter"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Pump and Haul - allow sandfilter to drain and dry to replace biofilter media. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | Dec 30 1899 8:45AM
03/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping Microfast due to recent back up. There appears to be broken tubing underground. Lower zone appears to show signs of surfacing effluent. homeowner has contacted someone for repair. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
04/20/2023 |  | RoutineScheduled | VAG408395 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.610000 |  |  | 0.510000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/15/2023 | 12:00 AM
05/26/2023 | Alternative | RoutineScheduled | 151-10-0133 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/12/2023 | Alternative | Pump-Out Only | 136-06-0531 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [16 empty] | Pumped Out | Refilled tank to appropriate level | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 11:30 AM
01/19/2023 | Alternative | RoutineScheduled | SD-12-423 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 11:08 AM
02/28/2023 |  | RoutineScheduled | 177-STS-88898 | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Auxiliary Filter"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | The UV light and cord are no longer working and should be replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/03/2023 | 08:19 AM
05/24/2023 |  |  | 033-08-0029-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
06/07/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
11/30/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Trenches |  | 450.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:09 PM
12/04/2023 | Alternative | RoutineScheduled | 12-184-5001 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/04/2023 | 12:00 AM
04/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/02/2023 |  | RoutineScheduled | SD-87-163 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Cloverleaf Environmental Consulting, Inc | 1942001135 | Robert | Charnley |  |  | Septic Tank Only |  | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/14/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Rejected | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
06/14/2023 | Alternative | Reportable Incident | 073-STS-105243 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | COSS - Maintenance - GMP2018-02 Replaced dbox with new 8 port concrete DBox. Spliced to existing conveyance line. Installed new 4" PVC header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 11:00 AM
11/03/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1000 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/16/2023 | Alternative | Reportable Incident | 171-11-0041 | Pittsylvania | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20-RT |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | RTU122504 - Sludge level-5-6" scum layer on top(fat,oil,grease)-A trace of sludge on bottom in Septic tank (pumped by hodnett last year)- Recirc zone of tank 6" sludge, Discharge zone of pump tank 14-16" sludge, Pump tank has 14-16" sludge, Clear Effluent on top. We cleaned Effluent filter. Pulled out and cleaned both pumps- working fine. The computer shut them down due to hydraulic overloading, after some investigation and pumping in manual found water leaking into the discharge pump tank through 4 in oultlet hole, repair on next trip. Pump is PF0300311), Cleaned and flushed both pumps and sparyer, DSischagre pump (pf200511), all floats tested operational. spin filter is plumbed hard and not accessable, no drain relief valves found. backwashed and flushed the filter. Pump runs up to 70 PSI but water has hard time leave the tank. Groundwater observed leaking into pump tank causing pump run constantly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/31/2023 | 09:30 AM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance | 175-06-0543 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Air relief valve needs repair. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/11/2023 | 11:24 AM
06/15/2023 | Alternative |  | 154-07-0652 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Amy | Huff | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/23/2023 |  | RoutineScheduled | 065-STS-32366 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Trenches | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 12:00 AM
12/08/2023 | Alternative | Routine/Scheduled | 145-STS-259902 | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/08/2023 | Dec 30 1899 11:30AM
04/12/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | no charmin or wipes use scott or costco brand one load laundry am and pm | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/22/2023 | 11:15 AM
10/18/2023 | Alternative | Follow-Up | 810-STS-3966 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 10/18/2023 |  | 8.000000 |  | 173.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | Dec 30 1899 1:00PM
05/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Pad | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
10/19/2023 | Alternative | Reportable Incident | 147-15-0086 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm Call: -Clearstream. System in Alarm. System at normal level. Found air pump no longer working. Ryan approved to replace Air pump. Replaced the air pump and confirmed everything is working | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | Dec 30 1899 12:00PM
02/01/2023 |  |  | ST-04-664 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
08/22/2023 | Alternative | Routine/Scheduled | 2015-143-0013 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip | UV |  | ["Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | ["Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | [17 empty] | There were 24 recirculation pump overrides in the past 30 days | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/22/2023 | 01:26 PM
09/01/2023 | Alternative | Routine/Scheduled | 228-17-0358 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Microfast |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/01/2023 | Dec 30 1899 8:20AM
10/18/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty |  | 8.210000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/07/2023 | 02:30 PM
05/20/2023 | Alternative | RoutineScheduled | 109-04-0079 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | [18 empty] | Annual inspection. Septic tank - First section - 6" solids crust, 8" solids on bottom. Second section - 12" solids on bottom. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. 1" of solids in recirculation portion of treatment unit. 12" of solids in discharge portion of treatment unit. Excellent treatment qulaity. Septic tank and treatment unit may need to be pumped out next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 07:03 PM
08/17/2023 | Alternative |  | 154-02-0942 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
04/27/2023 |  | RoutineScheduled | 154-03-0851 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | EcoFlow |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/04/2023 | 12:00 AM
03/10/2023 |  | RoutineScheduled | 101-03-0520 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Drip | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/12/2023 | 12:00 AM
02/23/2023 |  | Routine/Scheduled | 124-STS-2379 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Henrico | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 600.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Supervised pumpout of processing tank as recommended during last service visit. Commonwealth Waste Solutions pumped processing tank and pump tank empty and serviced. Refilled processing tank with fresh water for re-start. Serviced air compressor and drip headworks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/27/2023 | 07:30 AM
03/17/2023 | Alternative | Routine/Scheduled | 800-STS-14289 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The septic tank needs to be pumped out. Cleaned out the let tee - was stopped up. The timer is set to 2.5 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/17/2023 | Dec 30 1899 8:30AM
03/01/2023 |  | Reportable Incident |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced split 2" brass check valve. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
10/18/2023 | Alternative | Routine/Scheduled | 04-160-0234 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | 05:00 PM
07/17/2023 | Alternative | Initial Visit | 015-STS-336907 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles","SludgeScum Accumulation","Dispersal System Operation"] | ["Auxiliary Filter","Septic Tank Baffles","SludgeScum Accumulation","Dispersal System Operation"] | [17 empty] | Pumped Out | system has been maintained and appears to be functioning as designed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 12:00 AM
04/14/2023 |  | RoutineScheduled | 175-10-0081 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Bio Barrier | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 04:23 AM
04/25/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
03/15/2023 | Alternative | Reportable Incident | 151-93-205 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | COSS - Maintenance - GMP2018-02 Removed existing DBox - installed new 8 port concrete DBox. Spliced to existing conveyance line. Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/16/2023 | 08:30 AM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/05/2023 |  | Routine/Scheduled | 2006-143-0322 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/05/2023 | 04:25 PM
07/12/2023 | Alternative | RoutineScheduled | 43-STS-32513 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | septic | Advantex | Pump | Pressure | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [17 empty] | Had some alarms but wasn't in the log. Alarm page said recirc clogged filter. Cleaned effluent filter and opened valve for effluent to recirc back to septic tank it was closed. Checked the sludge and scum. Minimal scum, sludge hard to tell a lot of black effluent in tank sludge seemed to minimal. effluent in outlet side was a lot cleaner and effluent in advantex tank looked clean with a little sludge in bottom. I ran the pumps, alarm, and floats are all working. I adjusted the bottom recirc float down some to keep from alarming that its low it was floating horizonal. I ran system in test mode for 20 mins or so to make sure it didn't alarm anymore. everything seemed to be operational when I left. Client to follow up with anymore alarms. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | 10:30 AM
02/27/2023 |  | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 |  |  | Pump | Pressure | Trenches |  | 750.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/28/2023 | 10:01 AM
02/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1500 | Septic | Puraflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/25/2023 | Alternative | RoutineScheduled | 95-197-A6 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination | [22 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
04/19/2023 | Alternative | RoutineScheduled | 165-STS-334284 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation","Effluent Screens"] | ["Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | There was a leak in the manifold line dug up and repaired | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/06/2023 | 12:00 AM
05/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/13/2023 | Alternative | RoutineScheduled | SD-99-232 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1500 | septic | Multi-flo | Gravity | Pressure | Discharge | Chlorination |  | [] | [] | YES | None | Clear | [15 empty] | Informal | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/28/2023 | 08:05 AM
11/02/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | Dec 30 1899 2:02PM
06/09/2023 |  | RoutineScheduled | 2008-143-0216 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Microfast |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Level Sensor Operation","Control Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/09/2023 | 12:00 AM
09/20/2023 | Alternative | RoutineScheduled | 101-16-0223 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Aquasafe |  | Gravity | Gravity | Trenches | Not Applicable | 150.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/10/2023 | 11:50 AM
01/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | Septic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2023 | Dec 30 1899 8:47AM
11/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chickahominy | All In Septic Services | 1942001442 | Dennis | Mitchell | 3.000000 | 2500 | Multi Flow |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Auxiliary Filter","Other"] | NA | Musty | Clear | [14 empty] | Inspected | Multi Flow Socks Need Cleaned - Scheduled for February Sludge/Scum Accumulation - Septic 8", Pump Station 6", ATU 20" | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | Dec 30 1899 3:00PM
06/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/26/2023 | Alternative | Routine/Scheduled | 166-06-076 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. BioFilter - Fiberglass - 2 small fractures noted - biofilter / peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | 08:15 AM
05/04/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
03/20/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Needs UV Bulb & chord. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/31/2023 | Jan 1 1900 12:26PM
11/30/2023 | Alternative | RoutineScheduled | 10-167-038 | Nottoway | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Retaw Engineering LLC | 1965008335 | Ginasiyo | Mutoti | 10.000000 | 60,000 Gallons | Settling | Equalization/Pre-Anoxic | Pump | Gravity | Pad | Not Applicable | 500.000000 | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | None | Clear | 7.030000 | 8.500000 | 0.000000 | 0.000000 | None | 11/30/2023 | Sample Chamber | 13.600000 | 0.000000 | 1730.000000 | 1.200000 | 37.380000 | 7.630000 | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/11/2024 | Dec 30 1899 7:00AM
11/21/2023 | Alternative | Routine/Scheduled | 151-06-0325 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal level 4 in of sludge less than 1 in of solids Pulled and cleaned filter No signs of infiltration -Discharge/Pump Tank Pump chamber: Normal level Tested floats and pump all working as should All plumbing intact and pump moving water properly No signs of infiltration -Peat Moss: Tipping bucket and dispersal trays intact Peat moss broken down and heavily root bound Raked out peat moss -Control Panel: 120 volts coming in All visual and audible Alarms functioning properly Pump pulled 6.34 amps All components working as should -Drain Field Inspection port: No signs of standing water or surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 03:36 PM
12/21/2023 | Alternative | RoutineScheduled | 165-STS-335555 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 RT |  |  | Pressure | Trenches | Not Applicable |  | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/04/2024 | 12:00 AM
05/11/2023 | Alternative | Routine/Scheduled | 147-15-0086 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Pumped system for repairs - removed non-functioning UV system - Installed new sleeve, head controls and bulb. Distal end of LPD field damaged by lawn care operations. Excavated end of laterals - installed new 90 degree sweeps. System refilled with fresh water for re-start. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/25/2023 | Dec 30 1899 11:00AM
02/06/2023 |  | Routine/Scheduled | 234-14-297 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | Jan 1 1900 1:30PM
07/20/2023 | Alternative | Routine/Scheduled | 159-10-185 | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | UV | 450.000000 | ["Control Operation","Disinfection","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | System requires pumpout for pump replacement and UV replacement. Septic Tank - riser below grade - requires pumpout. Aeration Tank - recommend pumpout and refill due to high settleable solids, mixing present - compressor serviced. U.V. - Salcor - head has failed - UV bulb blown - sleeve is torn - recommend replacing with new. Pump Tank - recommend pumpout - check valve failed - pump heavily clogged and recently replaced. Drip field - headworks serviced, spin filter heavily clogged. System is operating, but requires a full pumpout with refill, and another full service following that. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/24/2023 | 07:45 AM
12/12/2023 | Alternative | RoutineScheduled | 150-07-044 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters, checked sludge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/19/2023 | Alternative | RoutineScheduled Component Maintenance | 175-06-0298 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Home is unoccupied and it is unknown for how long. As such, it is difficult to determine if the filterbed is taking effluent correctly. The filterbed does not show any obvious signs of distress - grass is cut and there are 3 mature trees. Four trees are recommended, but will struggle to survive if occupants don't use much water. The vent closer to the house is broken (below grade) at the hub, and the 4" pvc 90's that make up the "candy cane" are glued on (supposed to be a friction fit so that they can be removed to inspect the manifold for standing water or root intrusion). The blower should have been running, but was not and determined to be locked up. The blower and air filter will need to be replaced before the diffusers can be evaluated for proper aeration. The pump did run, but at about 20% slower than at start-up. The timer can be adjusted to compensate. The fiberglass manway (mechanical end of tank) is damaged in multiple spots and both electrical LB connections are broken. Riser and LB's will need to be replaced. The high level alarm float for the control panel is stuck on. The other float switches are working but could be original - recommend replace all. Float elevations need to be adjusted. The tank is missing the sanitary tee at the inlet. The clean-out next to the house is broken (below grade) at the hub fitting. Three bulbs are burnt out in the control panel and the power on light lense is missing. The inside alarm panel does give a visual alert, but no audible. The alarm horn is either disconnected or burnt out. These issues will need to be corrected before using the system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 07:39 AM
03/10/2023 |  | RoutineScheduled | 099-11-0056-SR | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | There is no power getting to the Norweco control panel. Aerator/alarm are not functioning due to this. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
03/16/2023 |  |  | 08-120-0097R | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Aquaworx | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Inspected | Replaced the remediator bacteria catalyst. Installed a 24" EZ set riser on the inlet of the septic tank and a 6" polylok riser on the outlet | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/01/2023 | 12:00 AM
01/09/2023 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 01:28 PM
12/19/2023 | Alternative | RoutineScheduled |  | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | Jet |  | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | YES | Musty | Clear | 6.700000 |  |  | 1.160000 |  | 12/19/2023 | Sample Chamber | 3.000000 | 0.000000 |  | 12.500000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/12/2024 | 08:45 AM
05/26/2023 | Alternative | RoutineScheduled | 151-11-0167 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1250 | Ecopod |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 12:00 AM
12/05/2023 | Alternative | RoutineScheduled Component Maintenance | 2002-93-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | Chlorination |  |  |  | NA | Musty | Clear | 7.000000 | 5.900000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 12/08/2023 | 08:29 AM
09/05/2023 | Alternative | RoutineScheduled | 03-183-001 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | WHITEWATER |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Level Sensor Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 4 - Blue Crystal tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/05/2023 | 12:00 AM
12/04/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | Replaced UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/04/2023 | Dec 30 1899 2:35PM
05/04/2023 | Alternative | Initial Visit | 800-06-0161 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit by Millers Services - Last known service 2008 - unknown service provider between CPEG and Now. Processing tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | Dec 30 1899 7:30AM
01/31/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic And Pumping | 1942001330 | Michelle | McKim |  |  |  |  | Pump | Pressure | Drip | UV |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | Dec 30 1899 4:00PM
06/05/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-89560 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | As noted on our last inspection report, the Advantex module has settled and should be releveled by the installer. We are again copying Pruitt Construction Group to remind them of this situation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
02/15/2023 | Alternative |  | 101-17-0365 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Jake | Thackston | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/07/2023 |  | Reportable Incident |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | [18 empty] | COSS - Maintenance - GMP2018-02 Replaced failing DBox with new 8 port concrete DBox. Spliced to existing conveyance line Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | 08:15 AM
10/10/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Other"] | ["Other"] | NA | [7 empty] | 10/10/2023 | Sample Chamber | 11.000000 | [5 empty] | Attached to this report |  | Septic Tank-6"sludge 1"scum/ Microfast Tank-4"sludge 0"scum/ Pump Tank-0" sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working properly/ Controls, pumps, floats and alarms are functioning correctly/ Repaired broken riser & riser lid/ Counts: Pump1-209 ETM-8h 1m/ Pump2-191 ETM-7h 28m On-2m 24s Standard Off-6h Peak Off-4h 48m/ Peak counts-5/ High counts-9/ No breakout or spongy areas on the LPD Pad site and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/01/2023 | Alternative | Routine/Scheduled | 13-0140 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/01/2023 | Dec 30 1899 9:15AM
08/21/2023 | Alternative | RoutineScheduled | 05-100-1333 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | ECOFLO |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | [] | [] | YES | [17 empty] | SLUDGE JUDGE 5" FROM BOTTOM EVERYTHING WORKING AS IT SHOULD PEAT REPLACED RECENTLY, LOOKS GOOD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/11/2023 | 10:20 AM
09/27/2023 | Alternative | RoutineScheduled | 07-197-A5 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 4.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
05/05/2023 | Alternative | Reportable Incident | 103-STS-103684 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | [18 empty] | COSS - Maintenance - GMP2018-02 Replaced existing DBox with new 8 port concrete DBox. Spliced to existing Conveyance Line Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | 09:00 AM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/16/2023 |  | Routine/Scheduled | 228-06-0125 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  |  |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | Jan 1 1900 12:35PM
06/19/2023 | Alternative | RoutineScheduled | 153-STS-20342 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic/ Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank- 6"sludge 3"scum/ .5 Microfast ATU-6"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ Blower controls and alarm functioning properly/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/10/2023 | Alternative | RoutineScheduled | 107-02-0308 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Dispersal System Operation"] | [18 empty] | Septic/FAST needs to be pumped out. Customer to schedule | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | 12:00 AM
12/06/2023 | Alternative | RoutineScheduled | S10-237-0003 | Salem | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | 1.000000 | 1000 | MICROFAST |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | Septic | Cloudy | [14 empty] | Inspected | Annual Inspection of Alternative Septic System This system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 - recommend 6in pipe on treatment side of tank be brought up to ground level - installed riser on tank - retrieved required sample | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/11/2023 | 12:00 AM
05/31/2023 | Alternative | RoutineScheduled Component Maintenance | SD-12-19 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"Recirculation Pump"] | ["Control Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Replaced return line pressure gauge (cloudy and unreadable). Recommend addition of flow meter in order to be able to measure flush rate. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
04/27/2023 |  | Reportable Incident |  | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | COSS - Maintenance - GMP2018-02 Replaced failing distribution box - with new 8 port concrete DBox. Spliced to existing conveyance line. Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | 06:23 AM
08/02/2023 | Alternative | RoutineScheduled | 015-STS-333692 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
10/03/2023 | Alternative | Follow-Up | VAG408301 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty |  | 7.900000 |  |  | 1.110000 | [11 empty] | Blower was not operational at time of visit. Inboden revisited on 10/31/2023 and replaced blower. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/07/2023 | 02:30 PM
01/19/2023 |  | Reportable Incident | 175-12-0016 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced blower under warranty. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
03/21/2023 |  |  | 16-113-100 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 03/21/2023 |  | 4.520000 | [5 empty] | Will be sent separately |  | BOD: 4.52 TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/21/2023 | 12:00 AM
03/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | UV |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | Dec 30 1899 7:20AM
03/09/2023 |  | Routine/Scheduled | {FIPSCode}-STS-3880 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - rSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | Jan 1 1900 8:30AM
05/01/2023 |  | RoutineScheduled | 133 17 0230 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Whitewater ATU |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Septic tank 1" scum 8-12" sludge - Treatment tank 2-3" scum layer and trace sludge with good aeration, The scum is getting thick and may need to be pump next year. pump tank 6 in sludge, alarm works and sounds on pump, alarm good and sounds on blower, pump is operational and alarm is good and float switches all test operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
03/09/2023 |  | Initial Visit | 124-STS-2379 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | AOSS - Initial Visit - Real Estate Inspection. Primary septic tank - pumped empty for inspection - Outlet appears to be lower than Inlet for ATU, causing high level in septic tank - effluent screen serviced. Aeration Tank - compressor diaphragm failure - repaired on property and placed back into operation. Mixing present on departure. Pump Tank - float sensors, pump and controls operating. DBox - intact - all 7 laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | 08:00 AM
01/11/2023 | Alternative | RoutineScheduled | SD-07-128 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Pungent | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the Septic Tank and the Aerobic Treatment Unit due to scum & sludge accumulation in the tanks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
08/04/2023 | Alternative | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [6 empty] | Control Operation | Control Operation | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/12/2023 | 02:23 PM
03/13/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank plastic riser lid replaced. The valve box lid replaced. Both gate valves replaced. System is in working condition at this time. This repair does not guarantee the life of any of the components | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
07/25/2023 | Alternative | Reportable Incident | 166-13-134 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. The timer is set to 2 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/25/2023 | 05:00 PM
06/02/2023 |  |  | SP-05-481 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
07/10/2023 | Alternative | Pump-Out Only | 151-13-0055 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | ["Distribution Pump Operation","Level Sensor Operation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Chesapeake Bay Pump Out. Pumped trash tank as recommended during last service visit. Found discharge tank alarming - but at normal level - referred to maintenance for evaluation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | 06:45 AM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/17/2023 | Alternative | RoutineScheduled | 154-08-0193 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/08/2023 | Alternative | Reportable Incident | 2018-143-0186 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Other"] | ["Other"] | [18 empty] | Replaced pump and contacter | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/27/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/29/2023 | 11:35 AM
04/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/14/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/14/2023 | Dec 30 1899 9:00AM
05/02/2023 | Alternative | RoutineScheduled | SD-07-164 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 75.000000 | ["Effluent Screens","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | 10:00 AM
10/16/2023 | Alternative | Reportable Incident | 151-08-0126 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm call: -Ecoflo. The mound is starting to blow out in the same corner as before when the chamber was flooded. I found that the tipping bucket was broken on one of the pivots and is forcing the water to dump to one side which is why that side is blowing out again. I sent Kenneth the estimates for the tipping bucket replacement and pumping of the septic tank to give the chamber some time to dry, he is not answering the phone. Used 1st alarm call for today's visit Repair (10/19): -Installation of a new Tipping Bucket in the Ecoflo Treatment Module | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/30/2023 | 09:23 AM
01/10/2023 |  | Routine/Scheduled | {FIPSCode}-STS-5200 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | Jan 1 1900 11:15AM
03/15/2023 | Alternative | RoutineScheduled | 159-17-0218 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Aquasafe |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | [] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
06/27/2023 | Alternative | RoutineScheduled | 031-STS-25917 | Campbell | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Septic Tank | Advantex AX20 | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | YES | [16 empty] | Inspected | Alarm visit due to an electrical issue and system was shutdown - Found a fuse inside the control panel was bad and after replacement it worked fine. Sludge levels were measured and the system does not need pumping at this time. 6 inch sludge in septic tank and 6-8" trace in the treatment unit. System has 44,6 hours of use on the pump and 3,756 cycles- alarms in history on April 6th, 10th and 11th - System is fully operational. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/30/2023 | 09:30 AM
12/27/2023 | Alternative | RoutineScheduled | 09-177-1081 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | 1.000000 | 1000 | RETROFAST |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | Septic | Cloudy | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 12:00 AM
07/17/2023 | Alternative | Routine/Scheduled | 11-163-0061 | New Kent | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | System alarming - aeration alarm active. Trash Tank - normal level - Inlet "T" clogged with grease! Aeration Tank - Aspirator crow foot missing - requires replacement! Clarifier - normal level - effluent screen serviced. - has high suspended solids / sludge and recommend pumping of processing tank - refill required. DBox - heavy sludge present - recommend jetting of absorption laterals to clear debris. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/18/2023 | Dec 30 1899 7:30AM
09/22/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  | 1500 |  | Pump | Pressure | Drip | UV |  | ["Dispersal System Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [17 empty] | Septic tank needs pumped out a lot of wipes. Also there is a wet spot in drain field that need to be investigated. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/23/2023 | Dec 30 1899 2:45PM
11/14/2023 | Alternative | RoutineScheduled | 027-STS-15314 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 15 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/14/2023 | 12:00 AM
01/31/2023 |  | RoutineScheduled | 181-05-0169 | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 2.000000 | 4500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","Effluent Screens","SludgeScum Accumulation","Dispersal System Operation"] | ["Auxiliary Filter","Effluent Screens","SludgeScum Accumulation","Dispersal System Operation"] | YES | [16 empty] | Pumped Out | Filters checked and cleaned. Effluent filter checked and cleaned. Treatment unit/septic tank pumped and cleaned. Control panels functioning properly No apparent leaks in system or drain field area. Repaired valve. Lids properly secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/14/2023 | 08:45 PM
09/27/2023 | Alternative | RoutineScheduled Component Maintenance | 177-16-0009-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Attached Growth Medium" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the septic/ATU tank and pump tank due to scum and sludge accumulation in the tanks. Roots are growing through the top seam of the ATU tank and into the media. If the roots are not removed, the media can clog and stop providing treatment. We recommend excavating by machine to remove the roots and reseal the tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
10/23/2023 | Alternative | RoutineScheduled | 13-158-191 | Mecklenburg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Southside | Environmental Services of Virginia | 1942001182 | Steve | Haley | 1.000000 | 450 | ADVANTEX AX250 | 2 | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["Other"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/23/2023 | 12:00 PM
04/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] |  | NA | [15 empty] | Will be sent separately | Inspected | Delta Compressor is bad and needs replaced. Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 12:48 PM
05/23/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump was replaced and the system appears to be functioning as designed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/18/2023 | Alternative | Routine/Scheduled | 085-STS-33464 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1060 | BioCoir |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [17 empty] | Cleaned effluent filter. Checked system operation. System appears to be operating normally. Etm 49, cc 2961 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/18/2023 | Dec 30 1899 1:12PM
07/05/2023 | Alternative | RoutineScheduled Component Maintenance | 177-09-0212-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | There are roots growing in the Puraflo modules. At some point in the future this may make it difficult to service the peat. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
05/10/2023 |  | RoutineScheduled | 175-13-0244 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
02/06/2023 |  | Routine/Scheduled | {FIPSCode}-STS-2497 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | Jan 1 1900 1:55PM
03/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NO | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/10/2023 | 11:17 AM
03/07/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic and atu needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
01/23/2023 |  | RoutineScheduled | SWP 03-769 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
05/08/2023 |  | Routine/Scheduled | {FIPSCode}-STS-1358 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | Jan 1 1900 3:00PM
08/17/2023 | Alternative |  | 182-19-0123 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex RT |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","SludgeScum Accumulation","Control Operation","Dispersal System Operation"] | ["Auxiliary Filter","Dispersal System Operation","SludgeScum Accumulation","Control Operation"] | [17 empty] | Pumped Out | Septic pumped out. Control panel replaced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/27/2023 | 12:00 AM
06/24/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 13" of accumulated solids in septic tank. Cleaned septic tank solids filter. 12" of solids in recirculation portion of treatment unit. 14" of solids in discharge portion of treatment unit. Flushed treatment unit spray manifold. Cleaned recirculation pump intake screen, Tested floats, pumps and alarm. Excellent treatment quality. The treatment unit may need to be pumped out next year based on the amount of solids. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/26/2023 | 07:03 PM
11/01/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Replaced pump | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/01/2023 | Dec 30 1899 11:00AM
01/24/2023 |  | Routine/Scheduled | {FIPSCode}-STS-4754 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 11:10AM
04/11/2023 |  | RoutineScheduled | 13-100-0237 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | AQUASAFE |  | Pump | Pressure | Mound | UV | 600.000000 | [] | [] | [18 empty] | EVERYTHING WORKING AS IT SHOULD. REPLACED UV LIGHT UNIT | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/27/2023 | 11:35 AM
09/22/2023 | Alternative | Pump-Out Only | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | UV |  | [] | [] | NA | [16 empty] | Exempt | Home has 2 people living in it. Sludge judge was done at inspection found 4" scum 7" sludge At time of inspection the level in tank did not require being pumped out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/15/2023 | Dec 30 1899 10:00AM
12/31/2023 | Alternative |  | SD-09-90 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
08/16/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Appears all electrical cables have been cut. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 09/15/2023 | Dec 30 1899 2:41PM
01/10/2023 |  | RoutineScheduled | 077-STS-36900 | Grayson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Bio Flim Reactor |  | Pump | Gravity | Mound | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | 12:00 AM
02/27/2023 |  | Follow-Up | {FIPSCode}-STS-4034 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Control Operation","Disinfection"] | ["Control Operation","Disinfection"] | N/A | [17 empty] | Replaced Norweco UV unit | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/27/2023 | Jan 1 1900 11:00AM
08/18/2023 | Alternative | RoutineScheduled | 02-197-351 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/18/2023 | 12:00 AM
03/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/06/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic/ Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic tank side-4"sludge 0"scum/ Microfast-2"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower functioning properly/ Microfast blower alarm functioning properly/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/18/2023 | Alternative | RoutineScheduled | 153-STS-20348 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | [7 empty] | 10/19/2023 | Sample Chamber | 28.000000 |  | 1600.000000 |  |  |  | Attached to this report |  | Septic Tank-4"sludge 0"scum/ Microfast ATU-6"sludge 0"scum/ Pump Tank-2"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms are functioning properly/ BOD Sample of 28 is within permitted limits but the UV-Light is faulty and the sample of >1600 is not within the permitted limits/ Require UV-Light replacement, owner informed/ Counts: Pump-5243 ETM-630/ High level-63/ Watermeter-0,399792.98/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12:00 AM
02/16/2023 |  | Routine/Scheduled | 02-174-0191 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary Septic tAnk - nomral level Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced - bridging is present. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | Jan 1 1900 9:00AM
01/19/2023 |  | RoutineScheduled | 179-08-0019-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation"] | ["Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The peat in the Puraflo modules is dry and in good condition, but we recommend adding peat to the Puraflo modules. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
12/12/2023 | Alternative | Routine/Scheduled | 095-STS-7101 | Williamsburg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [16 empty] | SEE VENIS REPORT | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | Dec 30 1899 12:00PM
11/02/2023 | Alternative | Routine/Scheduled | 166-14-081 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | 05:35 PM
05/04/2023 | Alternative | Routine/Scheduled | 14-160-0043 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/04/2023 | 01:45 PM
02/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
12/08/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-86713 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
08/27/2023 | Alternative | RoutineScheduled |  | Madison | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1500 | septic | Puraflo | Gravity | Gravity | Discharge | Chlorination |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Cloudy | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/28/2023 | 08:40 AM
05/02/2023 |  | RoutineScheduled | 133 04 1026 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | BioWheel |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | April 2023 monthly report. Total flow for month of April 2023 - 53,361 gallons. Average daily flow - 1,779 gallons | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/11/2023 | 07:03 PM
08/07/2023 | Alternative | RoutineScheduled Component Maintenance | 2105-11-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity |  | UV |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | 7.000000 | 12.900000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 08/15/2023 | 01:44 PM
05/10/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Bush was cut back, electric box was reattached replaced alarm float and added weights to the on and off floats. The alarm light was replaced. At this time the septic system is in working condition | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
08/29/2023 | Alternative | Reportable Incident | 179-07-0363-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 3.000000 |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | [17 empty] | Inspected | replaced contactor in the panel | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/29/2023 | 02:00 PM
08/31/2023 | Alternative | RoutineScheduled | 14-183-006 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | CLEARSTREAM |  | Pump | Pressure | Drip | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation","Control Operation","Dispersal System Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","Septic Tank Baffles","Recirculation Pump"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/31/2023 | 12:00 AM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Multiflo FTB | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/02/2023 | Alternative | RoutineScheduled | 151-10-0133 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/18/2023 | Alternative | Reportable Incident | SD-08-298 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for blower alarm going off due to clogged media in treatment unit. Adjusted pressure switch. Proposal to be sent to clean media and replace broken inlet riser on the septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
04/26/2023 |  | Routine/Scheduled | 234-18-085 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | Jan 1 1900 10:55AM
06/16/2023 | Alternative | RoutineScheduled Component Maintenance | SWT-02-1168 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"SludgeScum Accumulation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the pump tank due to sludge accumulation in the tank. There were several placed where drip tubing appeared to have been damaged by fence installation. Owner made repairs. There was no effluent coming to the surface during the follow-up visit on 7/3/2023. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/10/2023 | 10:02 AM
11/15/2023 | Alternative | RoutineScheduled | 115-09-0199 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 4000 | Biomicrobics Fast 0.5 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","BlowerCompressorAerator Operation"] | ["Effluent Screens","BlowerCompressorAerator Operation"] | NA | Musty | [15 empty] | Inspected | Yearly inspection Sludge levels- minimal Scum layer and 8-12" in. sludge in EQ/surge Septic tank - Fast Treatment zone - observation port OK, 24-18" sludge may pump prior to next year visit. Alarm functional, System includes 6 pumps,, all operational, Fawellreplaced 2 pumps and blower motor and Paul small replaced some floats switches over the past year. Cleaned blower air filter. Good Aeration from Blower, Observation of treatment trough from 6" Vent pipe when opened. System is fully operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
06/14/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | Dec 30 1899 11:24AM
10/05/2023 | Alternative | RoutineScheduled | 061-16-468 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters, system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/12/2023 | Alternative | RoutineScheduled Component Maintenance | 175-13-0446 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
08/24/2023 | Alternative | RoutineScheduled | 175-13-0236 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-4"sludge 1"scum/ Microfast ATU-6"sludge 0" scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, floats, pump and alarms are functioning properly/ Counts: Pump-015548 ETM-0042396 On-1m 28s Off-2h 58s Dose-52.50/ Pump: Zoeller N-98 115 volts/ No breakout or spongy areas on the LPD Pad site and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/21/2023 | Alternative | Routine/Scheduled | 150-93-153 | King William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Sandfilter, High rate |  | Gravity | Gravity | Discharge | UV | 450.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Primary septic tank - normal level Flow Equalization / recirc tank - float sensors, pump and controls operating. Sand Filters - THREE - Sand raked - spray grid serviced. U.V. - bulb and housing serviced. Discharge point located under water. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/24/2023 | 09:00 AM
09/06/2023 | Alternative | Reportable Incident | 16-142-0341 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 46.900000 | [7 empty] | Owner called due to the red light. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 3 minutes every 2 hours. Took 5 year BOD sample. NOTE - BOD sample was a little high - system should function properly after service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | Dec 30 1899 8:15AM
01/24/2023 |  | RoutineScheduled | 175-00-0896 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["Distribution Pump Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | On site for annual inspection. Started by replacing all pressure regulators and replacing the spin filter (starting to crush). Drip rates and flush rates were much better than in recent years. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
03/01/2023 | Alternative | Reportable Incident | 073-STS-103870 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | COSS - Maintenance - GMP2018-02 Installed access riser on septic tank & effluent screen in outlet. Replaced access riser on pump tank, replaced plumbing, and float sensors. Installed new control panel . Replaced Distribution box with new 8 port concrete DBox. Spliced to existing conveyance line. Spliced to existing header lines. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/02/2023 | 07:30 AM
01/19/2023 |  | Routine/Scheduled | {FIPSCode}-STS-25837 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2023 | Jan 1 1900 7:00AM
02/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1875 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/07/2023 | Alternative | Routine/Scheduled | 136-15-0052 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 2 minutes every 2 hours. The septic tank did not need pumping at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/07/2023 | 02:30 PM
11/16/2023 | Alternative | Routine/Scheduled | 151-10-0067 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank 1 Primary Septic tank: Customer did not want us to dig up at this time -Septic Tank 2 Secondary Septic tank: Normal level 3 in of sludge less than 1 in of solids Pulled and cleaned filter No signs of infiltration -Discharge/Pump Tank: Normal level Less than 1 in of suspended solids Tested floats and pump all working as should All plumbing intact and pump moving water properly No signs of infiltration -Aeration: Normal level 14 in of suspended solids Recommend pumping Aerating properly No signs of infiltration -Air Pump/Blower: 120 volts coming in Cleaned air filter Air pressure sensor functioning properly Air pump pulled 3.64 amps -Control Panel: 120 volts coming in All visual and audible alarms functional Pump pulled 8.47 amps All components working properly -Distribution Box: 3 lines all intact and taking water properly Speed balancers intact and functional Pulled minor grass roots -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:54 AM
09/23/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [17 empty] | Replaced pump and timer enable float | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/23/2023 | Dec 30 1899 1:00PM
11/14/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0178-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Completed annual inspection and routine maintenance. Discharge pump flow rate has slowed since last year and pulled high start-up amps for almost 3 seconds before settling down, recommend replace pump. Septic/recirc tank needs pumped out due to excessive sludge around the recirc pump. Owner to make arrangements. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
07/17/2023 | Alternative | Routine/Scheduled | 228-06-0239 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | Dec 30 1899 10:15AM
06/16/2023 | Alternative | Reportable Incident | 550-STS-6509 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Replaced pump relay | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/16/2023 | Dec 30 1899 10:30AM
11/17/2023 | Alternative | Reportable Incident | 03-120-0390A | Chesterfield | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Repairs: -Enter tank to remove roots and evaluate structural integrity of tank. -Entry of tank to reseal and parge seams and penetrations in tank to prevent further root intrusion and ground water infiltration. No guarantee on longevity.-Replacement of rsv slide adapter -Resealing of an existing Orenco Riser reqires excavation around the outside of each Riser includes use of specialized caulking inside and outside the Riser -Advantex Engineered Textile Media Filter Replacement in Treatment unit: Removal & disposal of existing Engineered Textile Media Filters Installation of new Engineered Textile Media Filters Includes installation of new Bars & Hangers -Installation of new Advantex Treatment Unit Lid Support Struts | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/28/2023 | Dec 30 1899 9:59AM
06/23/2023 | Alternative |  | 101-09-0284 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Charles 'Chas' & Arika | Cocke | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/26/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/26/2023 | Dec 30 1899 1:45PM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance | 175-10-0346 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Gravity | Gravity | Trenches | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection"] |  | NA | [15 empty] | Will be sent separately | Inspected | Compressor is bad and needs replaced. Uv unit is also damaged and needs to be replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 09/15/2023 | 02:41 PM
04/11/2023 | Alternative | RoutineScheduled | 061-17-219 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/17/2023 | 12:44 PM
04/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/06/2023 | Alternative | Routine/Scheduled | 199-06-0005 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes and spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact - some portions of infiltrator chambers exposed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | Dec 30 1899 7:30AM
03/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Clearstream | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
01/12/2023 | Alternative | Reportable Incident | 073-STS-93314 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to a sewer smell, toilet levels going up and down and tanks are gurgling - weir filter was stopped up. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. There is a lot of grease in the septic tank. Visible wetness on the drainfield - most likely from rain - once it dries need to keep an eye on it. The timer is set to 4 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/12/2023 | 12:00 PM
10/16/2023 | Alternative | RoutineScheduled Component Maintenance | 179-11-0050-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Roots are growing through the distribution box fitting. Owner is going to treat with copper sulfate. If that does not stop root growth, it may be necessary to excavate by machine to remove roots and replace and reseal fittings. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
09/28/2023 | Alternative | RoutineScheduled | 101-STS-92740 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/28/2023 | 12:00 AM
09/02/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20 |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 10" of accumulated solids in septic tank. 4" of solids in discharge pump tank. Flushed treatment unit spray manifold. Sprayed off solids from treatment unit "sheets" Cleaned recirculation pump solids basket filter. Tested floats, pumps and alarm. Excellent treatment quality. Visited home on 6-24-2023 to inspect alarm. Found system in good condition with no sign of alarm issues. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/24/2023 | 07:03 PM
04/17/2023 | Alternative | Initial Visit | 075-STS-34617 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 14.700000 |  | 2419.600000 | [5 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream and cleaned the UV light bulb. Changed the filter in the aerator. Fixed the grade on the pipe in the Clearstream. The timer is set to 1.1 minutes every 2 hours. Took initial BOD and Fecal samples. NOTE : Fecal sample was high - system should function properly after service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | Dec 30 1899 11:30AM
03/23/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
03/15/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.890000 | [14 empty] | Replaced 6 floats. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 08:40 AM
05/03/2023 | Alternative | RoutineScheduled | 171-12-0216 | Pittsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Pittsylvania-Danville | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1000 | Aquaklear |  | Gravity | Gravity | Discharge | UV | 450.000000 | ["Auxiliary Filter"] | ["Auxiliary Filter"] |  | None | Discolored | 7.600000 |  |  |  |  | 05/03/2023 | Sample Tap |  |  | 60000.000000 | 58.500000 | 110.000000 | 17.900000 |  |  | Another water sample will need to be taken. customer is aware of filter being stopped up by products being disposed of down drains. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/23/2023 | 03:00 PM
02/14/2023 |  | RoutineScheduled | SWP-00-009 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | As noted previously, the blue valves are sticking, but are currently working. Due to the location of the hydraulic unit, we would recommend continuing to operate as-is until it is necessary to replace the hydraulic unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
09/15/2023 | Alternative | Reportable Incident |  | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | 9/15 Alarm Call: -Upon arrival, I found aerator sounding louder than normal. I checked amperage and found that it was pulling 3.8 amps. Aerator is rated up to 3.4 amps @ 115 volts. Spoke with Mr. Gregg and informed him that the higher than normal amperage is an indication of impending failure. 9/25 Repair -replaced bad air pump and installed new tested and confirmed everything is functioning properly | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/05/2023 | Dec 30 1899 2:08PM
06/22/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | ["None"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | 12:00 AM
08/30/2023 | Alternative | RoutineScheduled | 04-197-A6 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 | [11 empty] | None | Clear | 7.000000 | 6.000000 |  | 0.000000 | [11 empty] | Tank may need pumped | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
02/07/2023 |  | RoutineScheduled | 179-STS-90548 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Disinfection" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Disinfection"] | NA | None | Clear | [5 empty] | 02/07/2023 |  | 2.000000 |  | 1.800000 |  |  |  | Will be sent separately | Inspected | Routine inspection. Sample taken. 2 bad floats for discharge pump (off and enabler). Uv light housing was almost empty, filled up. No water for testing zones Due to bad floats. Spoke to installer he said he will take care next day. DISCHARGE: HL 11, ETM 0. PEAK CNTS 13, ETM 15H14M. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
10/06/2023 | Alternative | RoutineScheduled Component Maintenance | 177-06-0074-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. System is not processing paper due to the use of fabric softner. Avised home owner and gave them a copy of the do's and dont's. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
04/11/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
09/05/2023 | Alternative | Routine/Scheduled | 04-172-0274A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Real Estate Inspection Routine Service Processing Tank - normal level - RSV, recirc pump & effluent screen serviced. Pumped and serviced - refilled for restart. Treatment Module - media drapes and spray grid serviced. Pump Tank - float sensors, pump and controls operating. Dbox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | Dec 30 1899 11:00AM
07/20/2023 | Alternative | Reportable Incident Component Maintenance | SD-04-525 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | On site to repair mower damage. Repaired clean-out with new piece of 4" pipe, female adapter and plug. Replaced broken Puraflo sample box. Effluent dripping into the new sample box looked pretty clean in spite of the peat being 18.5 years old. Inspected and raked the peat. Should be good for one more year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 07:01 AM
12/18/2023 | Alternative | Reportable Incident | 810-STS-4095 | Virginia Beach | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Contractor contacted us due to an alarm. Risers are all leaking. Replaced pump test butt cover - was split and full of H20 causing it to short out. Filter assembly - full of H20. Installed screws in all lids. The splice box on the panel is only 2" off the ground. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/18/2023 | Dec 30 1899 12:00PM
01/05/2023 |  | Reportable Incident | PPIE-AD5HJ5 | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Replaced the UV bulb, replaced the UV cord, and replaced the UV ballast. Meet with the pumping company and pumped and cleaned out the Clearstream tank and pumped out the septic tank. Disconnected the UV due to the pumping and as well as the pressure switch on the aerator. Need to go back to hook pressure switch up, turn UV back on, and get the samples. H20 trickling in the tank from the house. The timer is set to 9 minutes every 1 hour. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/05/2023 | Jan 1 1900 12:00PM
03/30/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank to Puraflo Modules | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-4"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Turned Puraflo Peat in all 6 Modules and peat is in good condition/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-018258 ETM-0018131/ Pump2-018179 ETM-0018170 On-35s Off-2h Dose-37.5 gal Pumps-63gpm/ No breakout or spongy areas on the drainfield and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/17/2023 | Alternative | Reportable Incident Component Maintenance | 175-06-0477 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] |  | NA | Septic | Clear | [13 empty] | Will be sent separately | Inspected | Control panel indicated high level alarm, pump fail alarm, and blower alarm. Pump and blower motor starters had tripped, processor timer was set incorrectly, blower was locked up, and pump was confirmed to have failed. Also observed that there were no rodent guards installed in the filterbed vent pipes, none of the green or yellow indicator lights were working, and the conduit had settled and separated at the control panel. Provided a repair proposal to the homeowner. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/08/2023 | 06:43 AM
07/06/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Level Sensor Operation"] | ["Level Sensor Operation"] | [18 empty] | Service call to replace Timer-enable float/ tested system- functioning properly | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
02/14/2023 |  | Routine/Scheduled | 03-142-0460 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen s erviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact, but small fracture noted in bottom of box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/15/2023 | Jan 1 1900 11:00AM
10/16/2023 | Alternative | Routine/Scheduled | 199-05-0028 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Normal level 1 in of sludge less than 1 in of solids No signs of infiltration -Recirculation Tank: Normal level 12 in of suspended solids Tested floats and pump all working properly Pulled brushed and sprayed bio tube filter Filter housing intact Pulled and cleaned pump All plumbing intact and pump properly moving water -RSV (Recirculating Splitter Valve): Pulled and cleaned until water ran clear Intact and properly working -Discharge/Pump Tank: Normal level 6 in of suspended solids Tested floats and pump all working as should All plumbing is intact and pump properly moving water Lb is used for junction box Riser is leaking -Media Sheets: Brushed and flushed laterals Sprayed media sheets Flushed module until water ran clear All laterals are intact and properly working -Control Panel: 120 volts coming in All visual and audible alarms properly working Discharge pump pulled 8.4 amps Recirc pump pulled 13.2 amps Everything is working properly however the panel is aged -Distribution Box: Normal level 6 lines all intact and properly taking water Speed balancers intact and properly working -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | Dec 30 1899 8:56AM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | One of the pumps is not functioning. Lots of scum in pump chamber. Recommend pumping all tanks. Drainfield is waist high grasses. Recommend mowing and keeping it shorter, but there were no signs of failure in the field. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
12/08/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | Dec 30 1899 2:30PM
05/18/2023 |  | RoutineScheduled | 179-16-0221-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Septic tank needs pump out. Spoke to customer about pump out and she said she will call pumper right away to schedule it. Blower 3.04 amps. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
10/05/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"Disinfection" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Disinfection" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | Dec 30 1899 2:02PM
06/15/2023 | Alternative | Routine/Scheduled | 023-STS-42831 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Aqua Safe |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/15/2023 | Dec 30 1899 11:00AM
12/27/2023 | Alternative | RoutineScheduled | 165-STS-333817 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | E-Z Treat |  |  | Pressure | Trenches | Not Applicable |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | [] | [18 empty] | Pumping to be scheduled | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/27/2023 | 12:00 AM
03/10/2023 |  | RoutineScheduled | 099-07-0215-SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter" ,"Attached Growth Medium"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The Pump Tank was pumped & cleaned in conjunction with this inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
01/02/2023 |  |  | 09-113-091 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/02/2023 |  | 5.280000 |  |  | 1.400000 |  |  | Will be sent separately |  | BOD: 5.28 TSS: 1.40 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/02/2023 | 12:00 AM
12/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | RSV clog hair | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
03/06/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1875 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/14/2023 |  | Routine/Scheduled | 147-15-00130 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Trash Tank - normal level - recommend pumpout Aeration Tank - mixing present - aspirator serviced. Clarifier - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/16/2023 | Jan 1 1900 7:15AM
03/22/2023 |  | RoutineScheduled | 179-08-0123-ST | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
11/16/2023 | Alternative |  | 051-STS-17706 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/16/2023 |  | 7.410000 |  |  | 2.600000 |  |  | Will be sent separately |  | BOD: 7.41 TSS: 2.60 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/16/2023 | 12:00 AM
06/05/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | DeHaven's Backhoe Service Inc. | 1942001541 | Wayne | Edmonson | 2.000000 | 2500 | Microfast |  | Pump | Pressure | Drip | Not Applicable | 225.000000 | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 08:00 PM
10/04/2023 | Alternative | Follow-Up Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | UV |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired broken air relief valves. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/16/2023 | Dec 30 1899 12:58PM
09/01/2023 | Alternative | Routine/Scheduled | 157-17-0062 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Delta Environmental Products, UC Series |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - high level - clogged effluent screen - serviced. Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. Dbox - normal level - hairline fracture above inlet | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | 07:45 AM
11/03/2023 | Alternative | RoutineScheduled | 019-STS-24187 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20RT-3 to Trenches |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Septic tank under 1" scum -6-10" sludge, recirculation zone 3-7" sludge and discharge zone 10" light trace of sludge. System does not need pumping at this time. filter was clean, Checked floats, alarm and wiring, All Test ok, recir pump has 851.2 hrs and 71,471 cycles on it and discharge pump has 3.6 hrs 190 cycles. system is good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
06/28/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/30/2023 | 09:23 AM
09/13/2023 | Alternative | RoutineScheduled | 095-STS-6924 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Hutchens Septic Services LLC | 1942001509 | Robert | Hutchens, Jr. | 1.000000 | 1500 | Advantex Ax25-RT |  | Pump | Gravity | Pad | UV |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear | [5 empty] | 03/29/2023 | Pump Chamber | 7.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
05/01/2023 |  | RoutineScheduled | -STS-40132 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Septic tank 1" scum layer 20" sludge Owner had it pumped 4 years ago by Foutz, - reccomened to pump- Treatment tank zone - (No observation port availabvle or view port). Alarm good on aerator/blower. Cleaned Blower airfilter. Pump runs whencalled for by float switch, alarm sounds in basement, System appears operational at this time. Large tree grows above the tank and is reccomended to be removed to prevent roots issues. Blower Alarm box appeares age but operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Lines were unevenly nitrified upon arrival. The Distribution Box was uncovered and re-leveled. The system should return to proper function. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/19/2023 | Alternative | RoutineScheduled | 17-192-155 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Pump | Pressure | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Septic Tank Baffles","Auxiliary Filter","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Septic Tank Baffles","Auxiliary Filter","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 8 - Blue Crystal tablets 18 - Bio Max tablets | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/19/2023 | 12:00 AM
09/19/2023 | Alternative | RoutineScheduled Component Maintenance | 154-05-0954 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
04/28/2023 |  | Initial Visit | VAG408110 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 2.000000 |  | Constructed Wetlands |  | Pump | Gravity | Discharge | Chlorination |  | ["Disinfection"] | ["Control Operation","Disinfection","Distribution Pump Operation"] |  | None | [17 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/07/2023 | 09:30 AM
07/20/2023 | Alternative |  | 07-197-A15 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/20/2023 |  | 6.550000 |  |  | 23.200000 |  |  | Will be sent separately |  | BOD: 6.55 TSS: 23.2 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | 12:00 AM
02/17/2023 | Alternative | RoutineScheduled | 154-06-0007 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | There is a tree growing next to the Advantex module that should be removed. Its roots are pushing in the side walls of the module. We recommend replacing the EZ Set riser lid on the pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
01/26/2023 |  | RoutineScheduled | 2090-04-153 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Chlorination |  | ["Dispersal System Operation" ,"Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 02/13/2023 | 08:47 AM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/11/2023 |  | RoutineScheduled |  | Cumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1500 | Aqua Safe |  | Pump | Pressure | Trenches | Not Applicable | 600.000000 | ["Effluent Screens"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/11/2023 | Jan 1 1900 10:00AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance | SD-05-416 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity |  | Chlorination |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
06/28/2023 | Alternative | Initial Visit | 095-STS-6406 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. There is no outlet tee in the septic tank and there is no riser on the inlet end to inspect - should be to properly inspect in the future. The timer is set to 2 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | Dec 30 1899 12:30PM
07/25/2023 | Alternative | RoutineScheduled Component Maintenance | 182-13-0296 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Main house tank pumped Microfast tank pumped at lower house | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
11/06/2023 | Alternative | Reportable Incident | 157-05-229 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Found broken forcemain on outside of the ecoflo pump chamber System is an Alternative Septic system. System needs to have maintenance done once a year, required by the state Made repair to forcemain and tested it leaked. Knocked out an opening through the tank replumbed forcemain back through and resealed the pipe with concrete. Tested all components working as they should. Service agreement needs to be done another day, Unable to complete while onsite | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 10:51 AM
01/06/2023 | Alternative | Reportable Incident | 157-14-0066 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | COSS - Maintenance - GMP2018-02 Replaced existing DBox with new 8 port concrete DBox. Spliced to existing header lines Spliced to existing conveyance line. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 09:00 AM
03/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/09/2023 | Alternative | RoutineScheduled Component Maintenance | 182-13-0291 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced blower panel | This AOSS should now return to normal function after having provided the above state routine maintenance | 12/06/2023 | 03:05 PM
10/02/2023 | Alternative | RoutineScheduled Component Maintenance | SWP 99-725 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
04/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/21/2023 | Alternative | RoutineScheduled | 2098-05-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 3.000000 |  |  |  | Pump | Gravity | Discharge | UV |  | [] | ["SludgeScum Accumulation","Septic Tank Baffles","Level Sensor Operation","Effluent Screens","Distribution Pump Operation","Disinfection","Control Operation","Attached Growth Medium"] | YES | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/28/2023 | 10:45 AM
07/26/2023 | Alternative | RoutineScheduled |  | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock-Rapidan | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | 2023 Annual | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
04/18/2023 | Alternative | Initial Visit | 093-STS-15198 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 2.000000 | [7 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream and cleaned the filter in the aerator. The timer is set to 1 minute every 2 hours. Took initial BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/18/2023 | Dec 30 1899 2:15PM
01/26/2023 |  | Routine/Scheduled | 550-STS-6519 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | Jan 1 1900 9:00AM
10/18/2023 | Alternative | RoutineScheduled | 09-197-A6 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  | ["Disinfection"] |  |  | Musty | Clear | 7.500000 | 5.000000 |  | 0.000000 | [11 empty] | Chlorine and de-chlorinator chambers are both empty. | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/03/2023 | Alternative | RoutineScheduled | 132-02-0357 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Trenches | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 12:00 AM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Ace Contracting Services, Inc | 1942001120 | Lawrence | Fellenz Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Distribution Pump Operation"] | ["Effluent Screens" ,"Distribution Pump Operation" ,"Recirculation Pump"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected | Replaced Sewage Effluent Pump And Check Valve | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 03:09 AM
07/30/2023 | Alternative | RoutineScheduled | 151-86-463 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Elite Onsite | 1942001726 | Drew | Saunders | 2.000000 | 1500 | 750 | 750 | Pump | Gravity | Mound | Not Applicable | 350.000000 | [] | [] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | 05:55 PM
04/26/2023 | Alternative | RoutineScheduled | 166-17-141 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/19/2023 | Alternative | RoutineScheduled | 107-97-0178 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.610000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 09:30 AM
05/12/2023 |  | RoutineScheduled | 179-14-0372-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Distribution Pump Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"Distribution Pump Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Pump tank needs pumped out due to excessive sludge accumulation (level getting near pump intake), and the septic tank is recommended due to poor access to clarifying chamber (where most of the solids are located). Owner agreed to contact local pumper and set it up. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
11/13/2023 | Alternative | RoutineScheduled | 17-142-0273 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/05/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation","BlowerCompressorAerator Operation"] | ["Control Operation","BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-6"sludge 3"scum/ Microfast-8"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Two contactors are rusty in the control box and were replaced on 7/7/2023 Controls, pumps, floats and alarms are now functioning properly/ Counts: Pump1-11953 ETM-62h 29m/ Pump2-1020 ETM-40h 20m On-2m 15s Off-6h Peak off-4h 48m/ Peak-33/ High-25 / No breakout or spongy areas on the drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/13/2023 |  |  | 177-STS-86647 | Spotsylvania | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock | All In Septic Services | 1942001442 | Dennis | Mitchell | 3.000000 | 2500 | Aquasafe |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Auxiliary Filter"] | NA | Septic | Cloudy | [14 empty] | Inspected | Aerator Replaced Sludge/Scum - Septic 2", Aerator 0", Pump Station 0" | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/13/2023 | 12:00 AM
01/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Replaced filter element for blower canister filter. Single point of aeration has developed, repair is required. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
04/14/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
07/31/2023 | Alternative | Routine/Scheduled | 550-STS-6912 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear |  | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | Dec 30 1899 11:02AM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/26/2023 | Alternative | RoutineScheduled | 175-15-0247 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon |  |  | Septic / Ecopod ATU Treatment Tank | EZ-Treat | Pump | Gravity | Discharge | UV |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA |  |  | 6.600000 |  |  |  | Ecoli 1 MPN/100 mL | 07/26/2023 | Sample Chamber | 7.000000 |  | 1.800000 | 3.000000 |  |  | Attached to this report |  | Septic Tank3"sludge 0"scum/ Ecopod ATU-2"sludge 0"scum/ EZ-Treat Recirculation Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ UV-Light sleeve cleaned and functioning properly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-007655 ETM-0034503 On-3m 4s Off-29m | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Microfast blower filter was missing. It was replaced. Bell cap for the hydraulic unit filter had broken. It was replaced. System appears to be functioning as designed now. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-509 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
08/11/2023 | Alternative | RoutineScheduled | 063-STS-12704 | Floyd | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 0.000000 | 1000 | Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Septic | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | 12:00 AM
03/27/2023 | Alternative | Follow-Up | {FIPSCode}-STS-17791 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Discharge | UV |  | None | None | N/A | [17 empty] | Riser sealed. This should help eliminated some of the overrides. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/09/2023 | Dec 30 1899 7:57AM
09/28/2023 | Alternative | RoutineScheduled Component Maintenance | VAG401997 | Rockingham | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Rejected | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Pad | Chlorination |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | ET Bed vegetation needs to be managed properly Sandfilters are buried and should be exposed per design Uncovered septic tank,added riser below grade per homeowner requests. I have notified owner concern of safety | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/22/2023 | 09:18 AM
05/18/2023 |  | Routine/Scheduled | 13-142-0259 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [17 empty] | Cleaned effluent filter. Flushed manifold. Changed recirc off time from 19.5 to 22 min. Lots of wipes in septic tank may require a more frequent pump out. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/18/2023 | Jan 1 1900 10:43AM
03/27/2023 |  | RoutineScheduled | 03-125-034 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/27/2023 | 12:00 AM
04/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
07/26/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-91774 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [5 empty] | 07/26/2023 |  | 9.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
04/27/2023 | Alternative | RoutineScheduled | C-06-111-0137 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Delta Whitewater |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 2" solids crust in first chamber of septic tank, 5" of accumulated solids. Second chamber 0" crust, 8" of accumulated solids. Cleaned septic tank solids filter. 24" of solids in treatment unit. 0" of solids in discharge pump tank. Excellent treatment quality. Cleaned drip manifold spin filter. Cleaned blower air filter. Tested pump, floats and alarms. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/16/2023 | Jan 1 1900 7:03PM
06/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was replaced. Aquaworx bugs were replaced. Bristle filter was added. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/08/2023 |  | RoutineScheduled | 175-03-0448 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Advantex Tank is ready for pumping. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/31/2023 | 12:26 PM
03/13/2023 | Alternative | Routine/Scheduled | 136-11-0105 | Gloucester | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Drip | UV | 450.000000 | Disinfection | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Aeration Tank - weir serviced - mixing present - compressor serviced. UV - Salcor - head shorted - water present inside - requires replacement. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/14/2023 | 07:45 AM
12/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1875 | Septic | Pureflwo | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/09/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | Septic Tank-3"sludge 4"scum/ Microfast-6"sludge/ Pump Tank-2"sludge/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-1060 ETM-66h 59m/ Pump2-1017 ETM- 64h 46m/ Peak-393/ High-53/ No breakout or spongy areas on the LPD Trench area and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/28/2023 |  | RoutineScheduled | 175-04-0445 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
05/31/2023 | Alternative |  | SD-10-247 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 12:00 AM
07/06/2023 | Alternative | Reportable Incident | S-175-14-0019 | Southampton | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/06/2023 | Dec 30 1899 8:30AM
01/27/2023 |  | Routine/Scheduled | 093-09-0224 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Puraflo |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/27/2023 | Jan 1 1900 10:55AM
10/31/2023 | Alternative | Follow-Up Component Maintenance | ST-02-195 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Resealed inlet end of septic tank top-seam. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 182-06-0032 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 10/10/2023 |  | 58.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
09/11/2023 | Alternative | RoutineScheduled | 08-197-A9 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 0.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | Musty | Clear | 7.000000 | 2.000000 |  | -1.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
06/03/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 5.000000 |  | Clearstream | Clearstream | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump and floats were replaced. System appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/21/2023 | Alternative | Reportable Incident | 151-07-0064 | Lancaster | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | ["Attached Growth Medium","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Biofilter changeout 02/21/2023 - septic tank pumped empty - replaced effluent screen and risers to grade. 02/24/2023 - Started removing Peat was alot of water in Chamber got water down To gravel could see water coming through gravel as fast as the truck was removing it filled vac truck almost full stopped pumping water kept rising in Chamber water came back up to trays before we left will probably be flooded before days end spoke with Zack and Trapper they will need to come out and do some soil testing did not install Peat would have ruined it immediately only removed a small amount of peat near center support pumped 2000 gallons of water out with vac truck | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 02/27/2023 | 08:00 AM
04/04/2023 | Alternative |  | 179-16-0219-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
07/25/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
09/08/2023 | Alternative | Routine/Scheduled | 115-STS-95147 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | - Trash Tank at Normal Level 12 in of sludge Less than 1 in of solids No signs of infiltration - Pump Tank at Normal Level Pulled and cleaned pump and filter Tested all floats working properly Pulled and cleaned uv light and housing No signs of infiltration -Aeration 1 at Normal Level 6" of sludge and less than 1"of solids Cleaned media No signs of infiltration - Aeration 2 at Normal Level 2 in of suspended solids Worked valves to break up sludge Aerating properly No signs of infiltration - Air pump has 120 volts coming in Cleaned filter Pulled 0.55 amps Visual and audible alarm working properly - Control Panel has 120 volts coming in Pump pulled 11.2 amps All visual and audible alarms working properly - Drip Field has no signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/03/2023 | 03:05 PM
05/20/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 300 | BioMicrobics MicroFast |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 6" solids crust in septic tank. 6" of solids on bottom of septic tank. 24" of accumulated solids in septic tank. Cleaned blower air filter. Excellent aeration and treatment. The septic tank and treatment unit will most likely need to be pumped out next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 07:03 PM
05/10/2023 | Alternative | Reportable Incident | 115-STS-101672 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Gravity | Gravity | Trenches | UV | 300.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | AOSS - Install - VDH Permit 157-22-0131 Pumped existing septic tank empty, crushed and removed. Installed new Clearstream DAC2 Installed Presby trench system as permitted. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/25/2023 | 07:15 AM
03/07/2023 |  | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 04/03/2023 |  | 65.000000 | [5 empty] | Will be sent separately | Inspected | filter clog return line was closed | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/28/2023 | 02:17 PM
05/11/2023 | Alternative | RoutineScheduled | 165-STS-333761 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/06/2023 | 12:00 AM
10/06/2023 | Alternative | RoutineScheduled | 02-197-077 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  | [] |  |  | None | Clear | 4.500000 | 4.000000 |  | 0.400000 | [11 empty] | de-chlorinator tablets needs to be stocked. Aerator working. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
12/27/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-90483 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We remain concerned about wet areas in the dispersal field. Current weather conditions do not allow us to fully evaluate. A follow-up visit is planned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2024 | 07:56 AM
03/23/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | inlet clogged | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
08/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"SludgeScum Accumulation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Poor aeration observed. Tank pumped out today by local pumper (Paul Ruffner). Existing manifold removed from tank and found to be clogged with an unknown material (slimy/ sludge-like) which was preventing aeration from the diffusers. Manifold cleaned, new diffusers installed, and a 2" pvc check valve installed to prevent backflow into the blower housing during high level events. Added minimum amount of fresh water back to the tank (flow from the house was low). Cleaned the air pre-filter and the spin filter (very dirty). Used Septic Scrub to flush/clean the drip tubing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 06:43 AM
08/23/2023 | Alternative | RoutineScheduled | 13-197-A1 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | JET |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/23/2023 | 12:00 AM
09/14/2023 | Alternative | RoutineScheduled Component Maintenance | 175-15-0400 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
09/18/2023 | Alternative | RoutineScheduled Component Maintenance | 033-06-0128-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
09/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Alarm was unplugged | This AOSS should now return to normal function after having provided the above state routine maintenance | 10/13/2023 | 01:07 PM
05/04/2023 | Alternative | Routine/Scheduled | 09-160-0050 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 79.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/04/2023 | 09:00 AM
09/27/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:00 AM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 179-14-0303-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The surge protector in the control panel is not working and should be replaced. We also recommend a 4" tee in the distribution box to ensure even flow of water to the drain field lines. Pumping of the septic tank and the Advantex RT Tank with our staff present is also recommended. Additionally, we would recommend that the trees growing on the far end of the drain field be removed to prevent root intrusion into your drain field lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
09/20/2023 | Alternative | RoutineScheduled | 107-01-0142 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [18 empty] | follow up on wet spot in yard | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/20/2023 | 12:00 AM
02/20/2023 |  | RoutineScheduled | 07-113-079 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 3 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/20/2023 | 12:00 AM
04/25/2023 |  | RoutineScheduled | SP-04-52 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 1-3 | 0-1 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear |  |  | 8.000000 | [11 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | 09:00 AM
03/09/2023 |  | RoutineScheduled | 175-06-0036 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
01/18/2023 | Alternative | Routine/Scheduled | 151-15-0074 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 4.000000 | 4000 | EcoPod |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | 07:12 PM
12/14/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | Dec 30 1899 10:05AM
05/12/2023 | Alternative | RoutineScheduled Component Maintenance | 177-18-0405-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
08/03/2023 | Alternative | RoutineScheduled | 18-160-0019 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 | 1000 | ATL |  | Gravity | Gravity | Pad | Not Applicable |  | [] | ["SludgeScum Accumulation"] | YES | Septic | Dark Brown | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | 12:00 AM
08/15/2023 | Alternative | Routine/Scheduled | 550-STS-6793 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 2 minutes every 2.5 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | Dec 30 1899 12:30PM
01/05/2023 |  | RoutineScheduled | 169-STS-25805 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/05/2023 | 12:00 AM
05/02/2023 | Alternative | Pump-Out Only | 121-STS-12043 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | YES | [16 empty] | Pumped Out | - levels appear to be high on inlet line, could be from filter settling or being clogged - recommend checking levels at next service date | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/03/2023 | 12:00 AM
07/18/2023 | Alternative | RoutineScheduled | 153-STS-20256 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic / Advantex Recirculation Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [17 empty] | Septic Tank-10"sludge 3"scum/ Advantex-10"sludge/ Pump Tank-2"sludge / No pump out needed at this time/ Advantex Bio-Filter and recirc. pump intake were cleaned/ AX-20 media in good condition and spraying properly/ Controls, pumps, floats and alarms are functioning properly/ Counts: Recirc. Run Time-1179.4/ Total cycles-53511 On-13.2m Off-3h 47m/ Watermeter-0698635/ Z1 cycles-4410 ETM-1239h 10m/ Z2 cycles-4408 ETM-1218h 13m/ No breakout or spongy areas on the drip field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/13/2023 | Alternative | RoutineScheduled | SD-10-100 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1500 | BEST 1 | sand filter | Gravity | Gravity | Discharge | Chlorination |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/17/2023 | 02:00 PM
06/06/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Clearstream | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced AP 80 compressor. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
09/26/2023 | Alternative | RoutineScheduled | 08-100-0860 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | BIOCOIR |  | Pump | Gravity | Mound | Not Applicable | 650.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | SLUDGE JUDGE SEPTIC TANK 5-6" FROM BOTTOM EVERYTHING WORKING AS IT SHOULD MEDIA LOOKS GOOD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/27/2023 | 12:25 PM
01/24/2023 |  | RoutineScheduled | 101-08-0527 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | MicroFast |  | Gravity | Pressure | Mound | Not Applicable | 500.000000 | [] | ["Auxiliary Filter","Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/28/2023 | 12:00 AM
03/08/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Septic Tank pumped by another company | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
09/06/2023 | Alternative | RoutineScheduled | 08-195-219-DIS | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | FAST |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/06/2023 | 12:00 AM
04/07/2023 | Alternative | Reportable Incident Component Maintenance | 177-STS-92825 | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Gravity | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Changed oringinal run tgime from 7:10 to 5:10. system required 2 min to pressurize. Peak OFF time chnaged to 1 hr. 20 mins. Standard run time 25 galx12 doses, peak OFF 25galx18 doses. System saturated on 1st third from header side. Tank leaks prfevioulsy resealed by others. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/26/2023 | 07:01 AM
03/15/2023 | Alternative | RoutineScheduled | 159-17-0214 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Aquasafe |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | [] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
07/19/2023 | Alternative | Routine/Scheduled | 550-STS-6479 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | Dec 30 1899 1:35PM
03/09/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | septic | Advantex | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump","SludgeScum Accumulation","Dispersal System Operation"] | YES | [17 empty] | 6" of sludge little scum. Loose sludge in outlet side. Effluent filter was clogged. Cleaned out. recirc pipe was laying on curtains fixed that. Pumps, Alarms, Floats are all operational. Field looks good and dry. 976 discharge pump cycles, 105h 44m run time. 73577 recirc pump cycles, 1214 h 12 m rum time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/27/2023 | 12:20 PM
04/05/2023 | Alternative | Pump-Out Only | 05-160-0032 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 3.000000 | 2200gal | Microfast | [6 empty] | [] | [] | [17 empty] | Pumped Out | - recommend septic system evaluation, drainfield is bleeding/leaking - recommend inlet and outlet line repair/upgrade | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/10/2023 | 12:00 AM
04/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/24/2023 | Alternative | Routine/Scheduled | 136-08-0639 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Routine Service Primary septic tank - normal level - effluent screen serviced. Aeration Tank - normal level - pumped empty - mixing present - compressor serviced - client refilling aeration tank - not responsible for alarm events. Pump tank - float sensors, pump and controls operating. DBox- Plastic - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 10:30 AM
05/01/2023 | Alternative | RoutineScheduled | 154-05-0237 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | puraflo 3 module |  | Pump | Gravity | Trenches |  | 150.000000 | ["Control Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | 09:20 AM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/11/2023 | Alternative | RoutineScheduled | 153-STS-20470 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 05/11/2023 | Sample Chamber | 17.000000 | [5 empty] | Attached to this report |  | Septic Tank-3"sludge 2"scum/ Microfast-0"sludge / Pump Tank-0"sludge/ No pump out needed at this time/ Blower air filter cleaned and working properly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-175 ETM-7h 42m On-2m 41s Off-6h / High-2/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/13/2023 | Alternative | RoutineScheduled Component Maintenance | 107-10-0277 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Best 1 | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | buzzer replaced air tube repaired All tanks pumped | This AOSS should now return to normal function after having provided the above state routine maintenance | 01/15/2024 | 10:39 AM
03/31/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | Delta Environmental Products, DF Series | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air release valve was repaired. System should resume proper function | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/30/2023 | Alternative | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/29/2024 | 02:39 PM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 2.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Effluent Screens" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | None | Cloudy | [13 empty] | Will be sent separately | Inspected | 2 of the 3 bags have been ripped by mice and need to be replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/11/2024 | 01:04 PM
01/17/2023 |  | Reportable Incident | 057-STS-99112 | Essex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | ["Dispersal System Operation","SludgeScum Accumulation"] | YES | [17 empty] | COSS - Maintenance - GMP2018-02 Replaced existing DBox with new 8 port concrete DBox. Spliced to existing conveyance line Spliced to existing header lines. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/18/2023 | 08:45 AM
06/29/2023 | Alternative | RoutineScheduled Component Maintenance | 179-16-0332-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
09/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Gravity | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Needs compressor replaced and normal open solenoid for zone master valve. Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | 12:58 PM
02/22/2023 |  | Follow-Up | 177-15-0199-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Clean FAST unit. Pump out of tank by others. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
07/03/2023 | Alternative | RoutineScheduled | 175-18-0495 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Mckim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/20/2023 | 07:35 AM
11/11/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [13 empty] | Replaced aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/11/2023 | Dec 30 1899 11:30AM
01/13/2023 |  | Routine/Scheduled | {FIPSCode}-STS-1293 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/13/2023 | Jan 1 1900 9:00AM
08/08/2023 | Alternative | RoutineScheduled | C-13-111-0002 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 2.000000 | 2000 | Orenco Advantex |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 15" of accumulated solids in septic tank near home. 23" of accumulated solids in septic/recirculation tank. 11" of solids in discharge pump tank. The recirculation tank and discharge pump tank may need to be pumped out next year. Cleaned recirculation pump solids basket filter. Flushed treatment unit spray manifold. Cleaned drip manifold spin filter. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/24/2023 | 12:00 AM
10/27/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | Dec 30 1899 2:02PM
09/07/2023 | Alternative | Routine/Scheduled | 550-STS-6535 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | Dec 30 1899 11:05AM
07/05/2023 | Alternative | Routine/Scheduled | 228-06-0798 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 8.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | Dec 30 1899 8:33AM
02/09/2023 |  | Routine/Scheduled | 228-06-0898 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Drip | UV |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/09/2023 | Jan 1 1900 3:30PM
07/11/2023 | Alternative | Initial Visit | 127-STS-34008 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 21.000000 | [7 empty] | Received a call about some problems. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The septic tank needs additional risers on it to be properly serviced in the future. The timer is set to 2 minutes every 2 hours. Took BOD sample. NOTE - The BOD sample was a tad high - system should function properly after service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | Dec 30 1899 7:30AM
09/05/2023 | Alternative | Routine/Scheduled | 234-18-084 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | Dec 30 1899 8:45AM
08/09/2023 | Alternative | RoutineScheduled | 06-113-241 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/09/2023 | 12:00 AM
07/31/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | YES | [17 empty] | Septic Tank-4"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ No pump out needed at this time/ Cleaned filters in the hydraulic unit/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-5437 ETM-371h 10m On-4m 10s Off-1h 30m/ High counts-113/ Watermeter-1,269,775/ No breakout or spongy areas on the drip field and dosing correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/04/2023 | Alternative | RoutineScheduled | 019-STS-24863 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20RT |  | Gravity | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | Annual inspection. 6" of accumulated solids in septic tank. 0" of solids in recirculation portion of treatment unit. 6" of solids in discharge portion of treatment unit. Flushed treatment unit spray manifold. Removed roots that have entered under the treatment unit lid. Tested floats, pump and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 07:03 PM
05/03/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | A sale inspection of an alternative septic system. All alternative septic systems in Virginia are required to be inspected every year and filed with the state and county. The septic control panel is an exterior time dose. There is a cleanout near the house that we ran the camera snake thru to the Anua tank. The sewer line was clear. The Anua tank has an air blower in it. There is a control panel for that also. If the air blower stops working the alarm will sound. The tank was pumped out and appears to be in good condition. The pump tank, risers, pump, floats, force main and electric box were inspected. The 8 port concrete surge box and the 10 port concrete d-box were dug up. All 5 header lines were camera snaked and the drain field was probed and dry. At time of inspection the septic system was in working condition. This inspection does not guarantee the life of any component. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
09/05/2023 | Alternative | Initial Visit | 550-STS-6779 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the panel, pump, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Airlines in the Clearstream for the lift assembly were backwards. The Clearstream and pump tank should be pump out and cleaned. The timer is set to 4 minutes every 2 hours. Need to take BOD and Fecal samples. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/05/2023 | Dec 30 1899 1:20PM
11/14/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["Other"] | ["None"] | YES | [17 empty] | Needs audible alarm | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/12/2023 | 12:00 AM
07/31/2023 | Alternative | Reportable Incident | 157-14-0082 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. Re-secured the pump float. Replaced the alarm float and replaced the UV light bulb. The timer is set to 6.5 minutes every 2 hours. Could not take 5 year samples due to the aerator not working on arrival. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/31/2023 | 12:00 PM
08/22/2023 | Alternative | RoutineScheduled Component Maintenance | 175-17-0429 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"Distribution Pump Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Disinfection" ,"Distribution Pump Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | None | Clear | [5 empty] | 08/22/2023 | Pump Chamber | 4.000000 |  | 1600.000000 |  |  |  | Will be sent separately | Inspected | Completed annual inspection, maintenance, and 5-year sampling. Treatment looked great. Fecal number (>1600 MPN/100ml) was most likely high due to a haze on the UV sleeve (cleaned after sampling). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
08/08/2023 | Alternative | Routine/Scheduled | 228-18-0018 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | Dec 30 1899 10:35AM
02/02/2023 | Alternative | RoutineScheduled | 103-STS-102083 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/01/2023 | Alternative | RoutineScheduled | 011-STS-27126 | Appomattox | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Septic Tank | Aqua Safe AS500L | Gravity | Gravity | Trenches | Not Applicable | 350.000000 | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/01/2023 | 04:00 PM
09/07/2023 | Alternative | RoutineScheduled | SD-13-480 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic |  | Pump | Gravity | Mound | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | 0 scum, 2" of loose sludge. Filter clean, Alarm, transducer, pump working. field dry. 7625 Doses, 99:39:53 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/19/2023 | 11:30 AM
01/03/2023 |  | RoutineScheduled | 175-13-0246R | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Gravity | Gravity |  | UV |  | ["Disinfection" ,"BlowerCompressorAerator Operation"] | ["Disinfection"] | NA | Musty | Cloudy | 7.300000 | 2.300000 |  |  |  | 01/03/2023 |  | 8.000000 |  | 73.000000 |  |  |  | Will be sent separately | Inspected | ATU compressor needs replacing. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 02/02/2023 | 11:08 AM
08/21/2023 | Alternative |  | 099-18-0113 C-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
01/23/2023 | Alternative | Routine/Scheduled | -STS-101821 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 1000 | None | None | Pump | Pressure | Trenches | Not Applicable | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | STE to Alternative Dispersal (LPP) Primary septic tank - normal level Secondary septic tank - normal level - noticed fracture in tank. Pump Tank - float sensors, pump and controls operating. LPP appears intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 07:45 AM
01/11/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
10/04/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.640000 | [14 empty] | Inspection was submitted for John Baker on 10/9/2023 with the wrong address. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 12:00 AM
05/19/2023 |  | Reportable Incident | 228-11-0426 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Cleaned Weir filter | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/19/2023 | Jan 1 1900 11:00AM
09/12/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
05/22/2023 | Alternative | RoutineScheduled | 171-14-0140 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Advantex AX20-RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Sludge level-1-2" scum layer on top-6-10" sludge on bottom in Septic tank - Recirc zone of tank 8-12" sludge, Discharge zone of tank 6" fine sludge - Clear Effluent on top, Cleaned Effluent filter. Recirculation pump operational it is a PF150311, discharge pump is a PF300511 and operational - alarm operational, all floats tested operational. RTU130805 treatment Box 420838 - System has active online monitoring- recirc pump run time 1406.1 Hours and 84,128 cycles discharge pump run time 20.3 hour and 2089 cycles, 2971 days trended in memory. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
10/03/2023 | Alternative | RoutineScheduled | 061-18-260 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-87937 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | Header lines are exposed in two places. We recommend adding topsoil and reseeding this fill. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
11/24/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-11298 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | ATU | Polishing Sand Filtetr | Pump | Gravity | Discharge | Chlorination | 500.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | 7.500000 |  |  | 1.800000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/27/2023 | 12:00 AM
07/05/2023 | Alternative | RoutineScheduled Component Maintenance | 113-STS-25897 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
01/04/2023 |  | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Disinfection"] | ["Disinfection"] | [18 empty] | Installed new Norewco UV Unit. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/04/2023 | Jan 1 1900 4:00PM
01/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["Level Sensor Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Air pre-filter cleaned as preventative maintenance. Timer enabler float switch was found to have a bare spot in the cord insulation so that wire was exposed. Replaced the float. Minor root penetration observed at manway seal. Will monitor during future services. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
01/19/2023 |  | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/08/2023 | 01:24 PM
07/25/2023 | Alternative |  | 195-Discharge-19263 North Fork River | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/25/2023 |  | 3.980000 |  |  | 1.400000 |  |  | Will be sent separately |  | BOD: 3.98 TSS: 1.40 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/25/2023 | 12:00 AM
04/26/2023 | Alternative | Follow-Up | 105-15-0002 | Appomattox | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1500 | Aqua Safe - Singulair 960 ATU 600 GPD |  | Pump | Pressure | Mound | Not Applicable | 600.000000 | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation"] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | 09:25 AM
01/09/2023 |  | RoutineScheduled | 175-06-0440 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected | Control panel cracked needs replacing & needs new sample box lid. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 01/17/2023 | 01:27 PM
06/07/2023 | Alternative |  | 16-183-003 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 06/07/2023 |  | 6.720000 | [5 empty] | Will be sent separately |  | BOD: 6.72 TSS: BDL | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/07/2023 | 12:00 AM
08/30/2023 | Alternative | RoutineScheduled | 02-125-087 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | Installed new aerator | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/30/2023 | 12:00 AM
06/29/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | [18 empty] | Repair only: Installed new pump #2 at the club house. Liberty FL 152M-2 (208- 230 Volts) with 25' cord in 10,000 gal. tank. Tested and functioning properly. Counts: Pump1- 17989 ETM-3600h 21m/ Pump2-29093 ETM-2728h 14m/ Peak-8993/ High level-2024 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
09/29/2023 | Alternative | RoutineScheduled | 2009-143-0101 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/20/2023 |  | Follow-Up | SWP-03-136 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Cleaned FAST media. Both tanks pumped out by Marshalls Septic. OFF float was not replaced, working fine. Replaced check valves in both drip zones. Replaced N/C solenoid for filter #2. Replaced N/O solenoids for zone 1 & 2. Repaired broken joint on top zone flex connection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
02/01/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.140000 |  | 20.000000 |  |  | 02/01/2023 |  | 9.000000 |  |  | 7.400000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2023 | 08:00 AM
10/04/2023 | Alternative |  | 98-197-A6 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 5.000000 |  | 0.000000 | [11 empty] | No tables in chambers. No odor, aerator working. | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
08/08/2023 | Alternative | RoutineScheduled Component Maintenance | 179-18-0449-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Attached Growth Medium" ,"Control Operation" ,"Disinfection" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Control Operation" ,"Disinfection" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Replaced bulb. 33 psi. RECIRC: HL-2, LL -11, OVERRIDE-0. DISCHARGE: HL-2, LL-9, OVERRIDE-0. "R" counts back to zero. Minerals building up on pump and other septic components, recommend to install a water filtration system or filter inside to help with that problem (Make sure return line does not go into sewer). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
07/27/2023 | Alternative | Follow-Up Component Maintenance | 175-15-0248 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Gravity | Gravity |  | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection"] | ["BlowerCompressorAerator Operation" ,"Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Installed Ecopod blower & repaired UV Unit. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 08/15/2023 | 01:44 PM
12/01/2023 | Alternative | RoutineScheduled | C-122-09-0046 | Craig | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | King's Alternative Septic | 1942001112 | William | King, II | 1.000000 | 1000 | BioMicrobics Microfast 0.5 |  | Pump | Gravity | Trenches | Not Applicable | 200.000000 | ["None"] | ["None"] | NA | [17 empty] | System is working correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/03/2023 | 12:00 AM
09/15/2023 | Alternative | Reportable Incident | 073-STS-106142 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | 9/15 Alarm Call: -Alarm for control panel on the pump is going off. No smells or backing up. Said that the switch controlling the pump may be in a fully on position because the pump is constantly running. His tank is mostly empty. He said it is possible that maybe the lawn service bumped the switch. Everything thing regarding the system is located on the west side of the house 9/15 Maintenance Report: -Septic Tank: Normal level 12 in of sludge 2 in of solids Pulled and cleaned filter Crock lid is broken -Discharge/Pump Tank: Normal level 6 in of suspended solids Pulled and tested floats all functioning properly Plumbing intact however it is aged and has brass valves Roots running through riser -Aeration: Normal level Less than 1 in of suspended solids Non serviceable airline Riser lid is broken -Air Pump/Blower: Notes for above Component 120 volts coming in Pulled and cleaned filter Pulled 1.4 amps Alarm is not working because it's not connected Air pump is aged -Control Panel: 120 volts coming in All visual and audible alarms functioning properly Pump pulled 6.83 amps Panel is aged -Distribution Box: 5 lines in distribution box all infiltrated with roots pulled roots from three lines but couldn't pull the other two -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 01:42 PM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Lower line might be receiving slightly more effluent than the other lines. Recommend uncovering Distribution Box and re-leveling if necessary | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/25/2023 | Alternative | RoutineScheduled Component Maintenance | SD-12-174 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001236 | Stuart | Lynn | 2.000000 | 16800 | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation"] | ["Attached Growth Medium" ,"Dispersal System Operation"] | NA | Musty | Clear | 7.100000 | 4.200000 |  |  |  | 09/25/2023 | Pump Chamber | 8.000000 |  |  | 5.000000 | 34.000000 |  | Will be sent separately | Inspected | Pump Outs 08/01/2023 17195071223 FQCPH (Commercial Pump and Haul) 4,200.00 08/01/2023 17272072023 FQCPH (Commercial Pump and Haul) 4,200.00 08/01/2023 17310072623 FQCPH (Commercial Pump and Haul) 4,200.00 08/02/2023 17377080223 FQCPH (Commercial Pump and Haul) 4,200.00 08/10/2023 17491081023 FQCPH (Commercial Pump and Haul) 4,200.00 08/17/2023 17490081723 FQCPH (Commercial Pump and Haul) 4,200.00 08/24/2023 17681082423 FXCPH (Commercial Pump and Haul) 4,200.00 08/31/2023 17686083123 FQCPH (Commercial Pump and Haul) 4,200.00 09/14/2023 17791091423 FQCPH (Commercial Pump and Haul) 4,200.00 09/22/2023 17734092223 FQCPH (Commercial Pump and Haul) 4,200.00 09/28/2023 17771092823 FQCPH (Commercial Pump and Haul) 4,200.00 Zones teset between 22 & 26 gpm, rotating through. Monitoring well and wwtp sample results summary attached WWTP meeting treatment stabdards,, no increase in Nitrogen in Monitoring wells, COnsent order signed and returned | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/15/2023 | 02:02 PM
10/24/2023 | Alternative | RoutineScheduled Component Maintenance | 182-03-0011 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 10/24/2023 |  | 225.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample abnormal, pumped all tanks to help with this Added riser on inlet Replaced discharge pump Homeowner to clean out valve boxes in field | This AOSS should now return to normal function after having provided the above state routine maintenance | 11/22/2023 | 09:18 AM
05/22/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-02-174 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We have several recommendations for this system: We recommend installing a new recirculating splitter valve. We also recommend repairing the plumbing for the recirculation pump. Finally, we recommend relevelling the sewer line coming into the Advantex Tank. Both the fence and pavers beside the tanks will have to be removed before we commence this work. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
08/16/2023 | Alternative | RoutineScheduled | 196-11-018 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters, checked floats | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-471 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Replaced 30" concrete lid on pump tank. System has 7 lines coming out of D-box, 3 lines draining good, 2 lines partially draining and 2 lines not taking any water. Pine tree were removed from around the box but there is couple big trees close to headers. recommend digging up and replace lines with pvc pipe due to big trees to close to headers. Recommend root-x to be applied every year at time of inspection to prevent roots from growing in. Will send proposal for repairs. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
01/17/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Lord Fairfax | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Panel indicated a blower alarm. Replaced old, failed loaner blower with another loaner blower. A new one is on order. Air filter replaced. Single-point aeration has developed, repair required. Owner has tentatively agreed to repairs. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
08/02/2023 | Alternative | RoutineScheduled Component Maintenance | 181-05-0421 | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Pump Intake was clogged able to clean | This AOSS should now return to normal function after having provided the above state routine maintenance | 08/23/2023 | 06:57 AM
03/14/2023 |  | Follow-Up | 175-17-0098 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Lowered conveyance line between Micofast and pump tank to obtain proper fall. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
03/27/2023 | Alternative | RoutineScheduled | C08-180-0130 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. Flushed treatment unit spray manifold. Cleaned recirculation pump basket filter. Cleaned drip manifold spin filter. Tested floats, pumps and alarm. 10" of accumulated solids in septic tank. 10" of solids in discharge pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | Jan 1 1900 7:03PM
05/15/2023 |  | RoutineScheduled | 154-14-0193 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
01/16/2023 |  | Routine/Scheduled | 228-12-0077 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Puraflo |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | None |  | 7.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | Jan 1 1900 12:30PM
03/10/2023 |  | Initial Visit | 033-STS-89034 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to some issues. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The septic tank needs to be pumped out as well as the trash out of the Clearstream tank. The timer is set to 3 minutes every 2 hours. Did not take initial sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 11:15 AM
02/02/2023 | Alternative | RoutineScheduled | 103-STS-95980 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance | 179-15-0141-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Strongly recommend getting recirc tank pumped out due to sludge level close to pump intake. Will send proposal for pump out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
11/14/2023 | Alternative | RoutineScheduled | 175-09-0106 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ Aquaworx Remediation | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-6"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower is working correctly/ Interior controls, pump, floats and alarms are functioning properly/ Counts: Pump-022929 ETM-0067620/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/26/2023 | Alternative | RoutineScheduled | 107-06-0491 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Best 1 |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/26/2023 | 12:00 AM
12/11/2023 | Alternative | RoutineScheduled | 182-00-0237 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | [17 empty] | Pumped Out | All tanks pumped | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2024 | 12:00 AM
06/07/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
09/18/2023 | Alternative | Follow-Up Component Maintenance | 099-10-0043-SP | King George | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Follow up. Bad air release valve for supply, replaced. Bleach flushed drip field but gallons per minute did not improve but there is a lot of bleach solution in the system might help clear emitters, will check next visit. HL-6961. 37 psi. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/02/2023 | 05:18 AM
01/31/2023 |  | RoutineScheduled | SP-02-607 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Level Sensor Operation" ,"Control Operation" ,"Distribution Pump Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Replaced end pod lid that was damaged. That pod also had shoots growing up, presumably from the bottom at the drain holes. No pods were ponding, but all had varying amounts of roots intertwined in the peat. There is some treatment taking place, but that could taper off quickly as peat appears to be original (possibly 20 years old). Will evaluate next year for possible replacement. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
10/27/2023 | Alternative | RoutineScheduled | 085-STS-35899 | Hanover | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chickahominy | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2000 | PURAFLOW 3 POD |  | Pump | Gravity | Mound | Not Applicable |  | ["Attached Growth Medium"] | ["Auxiliary Filter","Level Sensor Operation"] | NA | [16 empty] | Inspected | EFFLUENT FILTER CLEANED SLUDGE/SCUM ACCUMULATION - SEPTIC 6", PUMP STATION <2' FAULTY FLOAT/CONTROLS IN PUMP STATION, FLOAT NOT TURNING PUMP OFF, PUMPS UNTIL TANK IS EMPTY ***PEAT MOSS MEDIA HEAVILY SATURATED, PONDING, EFFLUENT POURING OUT OF THE LIDS | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/27/2023 | Dec 30 1899 2:00PM
04/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/24/2023 |  | Routine/Scheduled | 07-163-0090 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Pad |  | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Basin - bulging present - 2 minor fractures present - float sensors, and pump functioning. Biofilter - peatmoss in poor condition - ponding present - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/27/2023 | Jan 1 1900 8:30AM
07/14/2023 | Alternative | Follow-Up | 550-STS-6944 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Hooked up the pressure switch, hooked up the UV and UV alarm. Replaced the buzzer. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/14/2023 | Dec 30 1899 12:00PM
11/10/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | Replaced float | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | Dec 30 1899 2:00PM
06/05/2023 |  | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 |  |  | Pump | Pressure | Trenches |  | 600.000000 | ["Effluent Screens","Level Sensor Operation"] | ["Effluent Screens","Level Sensor Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/07/2023 | 12:25 PM
06/07/2023 | Alternative | Initial Visit | 550-STS-6687 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 9.000000 |  | 18.000000 | [5 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. There is paint in the tanks - they need to be pumped and cleaned. It was raining at the time of service and could not check out the drainfield or mound. The timer is set to 4 minutes every 2 hours. Took initial BOD and Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/07/2023 | Dec 30 1899 11:30AM
04/03/2023 | Alternative |  | SWP-05-109 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
02/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-3"sludge 2"scum/ Microfast-20"sludge 0"scum (Requires Pump Out) Pump Tank-2"sludge 0"scum/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-4701 ETM-567h 12m/ Peak-35 ETM-3h 43m/ Dose-40.6 gal / Watermeter-0427661.1/ Drip rates for 4 zones-5.06/ No breakout or spongy areas on the drip field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/22/2023 | Alternative | RoutineScheduled | 153-STS-20445 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens"] | ["Effluent Screens" ,"Auxiliary Filter"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Two lateral ends are broken. Homeowner has scheduled repair | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/15/2023 | 06:51 AM
10/13/2023 | Alternative | RoutineScheduled | 196-15-0048 | Westmoreland | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12:00 AM
01/03/2023 |  | Reportable Incident | 179-10-0079-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Bionest | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | Owner called about yellow alarm light on (compressor alarm). Replaced torn diaphragms/heads. Verified strong air flow to the airline disconnect in atu, but did not observe any bubbling. Air drop/ manifold is evidently clogged. Tank will need to be pumped, media removed and cleaned in order to identify and repair the blockage. Rigged up a temporary diffuser to provide some treatment until repairs are completed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 09:31 AM
01/12/2023 |  | RoutineScheduled | 153-STS-20273 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NO | Musty | Clear | [5 empty] | 01/12/2023 |  | 9.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
02/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-02 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Yellow jacket nest on last pod close to trees. Media showing its age but still have fiver left. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
03/16/2023 |  | RoutineScheduled | 06-192-065 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/16/2023 | 12:00 AM
10/12/2023 | Alternative | Reportable Incident Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired broken air relief valves. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
10/30/2023 | Alternative | RoutineScheduled | 05-197-A7 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.500000 | 7.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
05/16/2023 |  | Routine/Scheduled | 09-142-0020 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1500 | None |  | Pump | Gravity | Trenches | Not Applicable |  | SludgeScum Accumulation | SludgeScum Accumulation | N/A | [17 empty] | Septic tank pumped out. Fixed force main to allow for filter removal. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/22/2023 | Jan 1 1900 9:35AM
01/07/2023 |  | Initial Visit | 133 04 0818 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex AX20RT |  | Gravity | Gravity | Trenches |  |  | ["Control Operation","Recirculation Pump"] | ["Control Operation","Recirculation Pump"] | NA | [17 empty] | Initial start-up inspection. Set up recirculation pump timers based on homeowner correspondence concerning frequency of occupation and number of individuals per visit. Adjusted recirculation pump flow rate appropriate for an AX20RT. Tested floats, pump and alarm. Verified proper installation by licensed installer. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/13/2023 | 07:03 PM
01/12/2023 |  | RoutineScheduled | 033-07-0269-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
07/24/2023 | Alternative | RoutineScheduled | 163-STS-335982 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Control Operation","Dispersal System Operation"] | ["Auxiliary Filter","Control Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | 12:00 AM
04/17/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | All 6 pods full of effluent. Surge box has no lid. Bottom 2 lines are wet. Further investigating needs done. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
04/12/2023 |  | Pump-Out Only | 550-STS-6550 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  | Drip | UV |  |  |  | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/12/2023 | Jan 1 1900 10:00AM
02/11/2023 |  | RoutineScheduled | 2000-91-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | ATU | Polishing Sand Filter | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | NO | Musty | Clear | 6.900000 |  |  | 2.100000 |  | 02/13/2023 | Sample Chamber | 2.000000 |  |  | 2.200000 | [5 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/23/2023 | 12:00 AM
06/29/2023 | Alternative | RoutineScheduled |  | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Replaced alarm float on discharge side, other floats operational | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/30/2023 | 09:30 AM
12/06/2023 | Alternative | Follow-Up | 15-160-0038 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | 1.000000 |  | MICROFAST |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | 11-20-2023 - blower is non-functional and needs to be replaced - recommend septic tank be pumped/cleaned 12-06-2023 - replaced blower | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/07/2023 | 12:00 AM
05/04/2023 |  | RoutineScheduled | 182-13-0160 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal | [9 empty] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/04/2023 | 12:00 AM
11/03/2023 | Alternative | RoutineScheduled Component Maintenance | 182-07-0409 | Rockingham | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | System requires pumping due to high levels of sludge Zone valve is leaking as well as a supply line to valve | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 01/16/2024 | 12:30 PM
11/27/2023 | Alternative | Routine/Scheduled | 157-02-099 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | annual maintenance: -Septic Tank: Found at normal level, 3in of sludge and less than 1in of solids. Pulled and cleaned filter. -Discharge/Pump Tank: Found at normal level, less than 1in of sludge and solids. Tested floats and pump all working as they should. -Aeration: Found at normal level, 6in of suspended sludge. Pulled and cleaned weir and diffuser. High level float working. -Air Pump/Blower: Pulled and cleaned air filter. Air pressure sensor working as it. Air pump pulled 1.4 amps -Control Panel: 120 volts audio and visual alarms working as they should. Pump pulled 5.6 amps -Drain Field: Unable to locate dbox, no signs of surfacing in drainfield area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 12:42 PM
11/16/2023 | Alternative | RoutineScheduled | 136-05-364 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Advantex AX20 |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation"] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | 12:00 AM
10/23/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/23/2023 | 12:00 AM
04/14/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | replaced recirc pump | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/22/2023 | 11:15 AM
11/06/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | Western Virginia Water Authority | 1942001145 | Michael | Doss |  |  |  |  | Gravity | Pressure | Drip | UV |  | [] | [] | YES | None | Clear | [5 empty] | 11/08/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 02:00 PM
08/07/2023 | Alternative | RoutineScheduled | 043170189 | Clarke | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lord Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/11/2023 | 11:00 AM
10/16/2023 | Alternative | RoutineScheduled Component Maintenance | SD-13-154 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Effluent filter was very dirty but eventually cleaned up. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
10/23/2023 | Alternative | Routine/Scheduled | 041-STS-259815 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Fuji |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/23/2023 | Dec 30 1899 9:17AM
09/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 09/20/2023 | Sample Chamber | 48.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/07/2023 |  | Initial Visit |  | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Owner called due to the pump being bad. Replaced P-20 pump (new serial # 2204-136325) and replaced the relay. Re-wired the panel. The UV cord and UV bulb are bad and the tube also might be bad. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/07/2023 | Jan 1 1900 10:00AM
01/02/2023 |  | RoutineScheduled | 051-STS-17412 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Effluent Screens","Disinfection","BlowerCompressorAerator Operation","Control Operation","Auxiliary Filter","Attached Growth Medium","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 2 Chlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/02/2023 | 12:00 AM
10/14/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 2000 | Extended Aeration |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["Auxiliary Filter"] | YES | [17 empty] | 3rd Quarter 2023 inspection. First inspection performed since 2nd Qtr. 2022 due to non-payment. Grease trap #1 and #2 need to be pumped out. 2,000 gallon septic tank needs to be pumped out due to solids accumulation. Treatment unit blower is defective. Signs of apparent electrical issue that caused one of the two capacitors to "blow-up" No aeration or recirculating of settled mixed liquor back to aeration chamber from clarifier due to blower being defective. At the very least the first chamber of the treatment unit needs to be pumped out due to excessive solids accumulation. Septic tank filter cleaned. Effluent solids filter in clarifier cleaned. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/24/2023 | 07:03 PM
08/30/2023 | Alternative | RoutineScheduled | 115-05-0384 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Other conventional maintenance performed | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 12000 | Biomicrobics Fast 2.5 |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Group meeting with engineers and contractors to discuss the new school addition | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | 09:30 PM
02/14/2023 |  | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2023 | 01:23 PM
06/14/2023 | Alternative | Routine/Scheduled | PPIE-AD5HJ5 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | Dec 30 1899 5:30PM
02/22/2023 | Alternative | Initial Visit | 093-STS-14533 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed a 3/4" brass check valve on the headworks. The timer was set at 1.25 minutes every 2.5 hours changed it to 2 minutes every 2.5 hours. Did not take initial samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | Dec 30 1899 9:30AM
10/11/2023 | Alternative | RoutineScheduled Component Maintenance | 182-17-0037 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 | 2500 | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 10/11/2023 |  | 8.000000 | [5 empty] | Will be sent separately | Inspected | Lab normal Treatment tank pumped | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
09/06/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-87379 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
06/13/2023 | Alternative | Routine/Scheduled | 234-13-300 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Could not locate valve boxes. The timer is set to 6 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/13/2023 | Dec 30 1899 9:00AM
03/29/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
04/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/30/2023 |  | RoutineScheduled | 177-10-0242-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Jbox in RT tank was full of water, vacuumed. 2 header pipes settled and pulled out of dbox. 2 lines backing up into box. Recirc pump intake was clogged, cleaned. Will send proposal for fixing pipes and to camera snake lines (trees close ) | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
12/14/2023 | Alternative | RoutineScheduled | VAG408174 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Clear | 7.660000 |  |  | 0.430000 |  | 12/14/2023 |  | 10.000000 |  |  | 153.300000 |  |  |  |  | Sludge level at 60%. Recommended pumping. Will resample after. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/14/2023 | 11:00 AM
11/29/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 12:00 AM
01/24/2023 |  | Routine/Scheduled | {FIPSCode}-STS-1355 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 11:40AM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/04/2023 |  | Routine/Scheduled |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Cajun Aire ATU |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Aeration - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/05/2023 | 09:30 AM
07/07/2023 | Alternative |  | 18-100-0472 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 12:00 AM
03/23/2023 |  | RoutineScheduled | 033-06-0277-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend removing the trees growing next to the Advantex modules and cutting back the bushes around the module and risers. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
11/03/2023 | Alternative | Routine/Scheduled | 041-STS-259656 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/03/2023 | Dec 30 1899 4:43PM
11/13/2023 | Alternative |  | 109-STS-34169 | Louisa | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 3000 | Microfast |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation"] |  | Septic | Cloudy | [14 empty] | Inspected | Aerator Control Circuit Replaced - Power Surge, not operational at time of inspection Sludge/Scum Accumulations - Septic 18", ATU 8", Pump Station 2" | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/13/2023 | 12:00 AM
09/25/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | Dec 30 1899 11:45AM
09/13/2023 | Alternative | Initial Visit Component Maintenance | 099-STS-92867 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Startup | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
04/06/2023 |  | RoutineScheduled | 153-STS-20287 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
08/24/2023 | Alternative | RoutineScheduled | SD-13-265 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic |  | Pump | Gravity | Mound |  |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | 1" Scum, 6" of Sludge, 4' Liquid depth, pump working . Transducer not reading. Client had transducer replace all good now. 208:23:35 hrs 13608 events | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | 02:30 AM
09/18/2023 | Alternative | RoutineScheduled | 05-165-0909 | Northampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | ECOFLO |  | Pump | Gravity | Pad | Not Applicable | 600.000000 | [] | [] | YES | [17 empty] | SLUDGE JUDGE 3-4" FROM BOTTOM REPLACED PEAT EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 12:40 PM
11/15/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Microfast needs pumping. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/01/2023 | Dec 30 1899 10:33AM
11/20/2023 | Alternative | RoutineScheduled | 001-STS-91728 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [8 empty] | 11/20/2023 | [9 empty] | cleaned filters, replaced diffusers. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/30/2023 |  | RoutineScheduled | 179-06-0107-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Supply line pressure on first test run, with ball valves throttled, was only 2 psi. Cleaning the pump intake and plugging the weep hole brought the pressure up to about 20 psi (acceptable, but not great). Testing drip rate on a continuous flush system (with no flow meter) has to be done with a tape measure and stopwatch (not terribly accurate), and flush rate cannot be calculated at all. Drip rate was well below design. No mention of flush rate in engineered plans obtained from the health department. This time, no wet spots appeared during the test runs, but the supply end was saturated for about the first 30 feet. Advised owner to add topsoil, seed and straw to lawnmower ruts that were holding puddles of water. Also advised owner to look into a water treatment system that would raise his pH to 7.0 to provide a better environment for treatment. High level count at 96, and low level count at 91. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
12/07/2023 | Alternative | Reportable Incident | C 800-18-0257 | Suffolk | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm a couple of days previously. Serviced system. Checked the panel and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Replaced the relay in the panel. The UV is not working. Meet with the pumping company and pumped our the Clearstream tank, septic tank, and pump tank. Disconnected the pressure switch on the aerator due to the pumping. The timer is set to 4 minutes every 2 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/07/2023 | Dec 30 1899 10:00AM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
04/13/2023 |  | RoutineScheduled | 177-06-0087-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | New concrete lid on pump tank was installed on 4/14/23 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
02/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/15/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Advantex | Pump | Pressure | Drip |  |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | YES | [7 empty] | 06/15/2023 | Pump Chamber | 16.200000 | [5 empty] | Attached to this report |  | 0 scum, 6" of sludge, cleaned filter, floats, pump, alarms work. Field looks good and dry. Conduit pulled from panel, Contractor to fix. Dist. pump 902 events, 43hrs 40 min run time, Recirc. pump 19249 events, 381 hrs 39 mins | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/29/2023 | 11:30 AM
08/15/2023 | Alternative | Routine/Scheduled |  | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. BioFilter - standing effluent in inspection port - peatmoss in fair condition | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | Dec 30 1899 7:00AM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
05/30/2023 |  |  | 00-192-350 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 05/30/2023 |  | 2.480000 |  |  | 1.400000 |  |  | Will be sent separately |  | BOD: 2.48 TSS: 1.40 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/30/2023 | 12:00 AM
09/13/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  | 1000 | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
02/09/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 1.000000 |  | Septic | Microfast | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | [18 empty] | 2" scum and 2" of sludge in the septic area. Loose sludge in treatment side from Blower being off. Turned blower on. Everything was running good and operating when I was there. I checked the d-box effluent was clean. Recommend changing out panel with updated audio alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/09/2023 | 04:20 PM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | UV |  |  |  | NA | Musty | Clear | 7.100000 | 5.900000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/16/2023 | Dec 30 1899 12:58PM
12/21/2023 | Alternative | RoutineScheduled | 86-197-244 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/21/2023 | 12:00 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Aerator was not functioning | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/10/2023 |  | RoutineScheduled | 132-19-0010 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Aerator motor broke PVC fittings inside the blower housing. ATU was not receiving aeration. Homeowner has contacted someone for repair. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/04/2023 | 06:02 AM
10/10/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 8.190000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 03:45 PM
05/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/29/2023 | Alternative | Routine/Scheduled | 136-06-0342 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - normal level - RSV, recirc pump, Effluent screen serviced. Treatment Module - Media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operting. DBox - plastic - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | 07:00 AM
07/27/2023 | Alternative | Routine/Scheduled | 157-03-055 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Aeration Tank - normal level - mixing present - compressor serviced. PUmp Tank - float sensors, pump and controls oeprating. DBox - plastic - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | 07:30 AM
01/19/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | J&G Septic Service |  | James | Kleindl | 2.000000 | 3000 | Mirco fast |  | Pump | Pressure | Drip | UV |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/07/2023 | Dec 30 1899 8:00PM
09/26/2023 | Alternative | Routine/Scheduled | 128-08-116 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level Has 15" of overall sludge and solids and should be pumped -Discharge/Pump Tank: At normal level Pump and floats are working Floats are aged 1" of sludge -Aeration: Can hear the treatment working -Air Pump/Blower: Working properly Pulling 4.5amps Pulled and cleaned filter -Control Panel: Both panels working properly Visual and audible alarms working Discharge pump pulling 12amps -Drain Field: Showing no signs of surfacing or blowouts | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | 01:50 PM
08/09/2023 | Alternative | Reportable Incident | 043180114 | Clarke | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Multiflo FTB | [6 empty] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/12/2023 | 02:41 PM
11/16/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Needs new UV bulb ,housing & control head. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/06/2023 | Dec 30 1899 9:34AM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-89972 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
12/01/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 09:30 AM
04/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Strongly recommend flushing and balancing lines in the near future | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/05/2023 |  | RoutineScheduled | 2022-06-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | UV |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 11:08 AM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance | 2045-02-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Chlorination |  | ["Effluent Screens"] | ["Effluent Screens"] | YES |  |  | 7.000000 | 12.600000 |  |  |  | 06/28/2023 |  | 5.000000 |  |  | 8.000000 |  |  | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | 11:24 AM
02/02/2023 |  | Pump-Out Only | 10-160-0196 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 | 1500 | Microfast | [6 empty] | [] | [] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | 12:00 AM
05/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | needs new concrete lid and supply pressure gauge need new owner info | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
11/21/2023 | Alternative |  | {FIPSCode}-STS-61330 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/21/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
01/23/2023 |  | RoutineScheduled | 177-08-0273-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Hoot | Hoot | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Replaced defective pump. Installed a new Orenco PF300511 pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
11/13/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-91940 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment is crystal clear. Some wipes in septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
05/19/2023 | Alternative | Reportable Incident | VAG401940 (LEGACY DISCHARGE) | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Gravity | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | Musty | Clear | [15 empty] | no discharge during visit, Owner called because blower quit working replaced blower. tablets in feeders | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/06/2023 | 12:00 AM
08/24/2023 | Alternative | RoutineScheduled | 06-100-1254 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | JEFulbright Septic, LLC | 1942001131 | Jason | Fulbright | 8.000000 | 10000 | Nitrex Denitrification Unit | Eco Flo Biofilter | Pump | Gravity | Pad | UV | 3900.000000 | [] | [] | NA | None | Clear | 7.250000 | 3.500000 |  |  |  | 08/24/2023 | Sample Chamber | 15.000000 |  | 0.900000 | 0.900000 | 3.700000 |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/24/2023 | 12:00 AM
08/26/2023 | Alternative | RoutineScheduled | SD-11-241 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2000 | septic | Advantex | Gravity | Pressure | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | 08:50 AM
09/05/2023 | Alternative | RoutineScheduled | 175-19-0215 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation","Recirculation Pump"] | ["Recirculation Pump"] | YES | [17 empty] | Septic Tank-12"sludge 4"scum/ EZ-Treat Tank-14"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ Pump out required on the Septic EZ-Treat Tank/ Recirculation pump intake cleaned and media in good condition/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-1212 ETM-100h 13m/ Peak-0/ High-13 On-2.5m Off-14m/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/24/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 3000 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/04/2023 |  |  | 2016-143-0155 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 2.000000 |  | Advantex |  | Pump | Gravity | Trenches | UV |  | [] | ["Attached Growth Medium","Effluent Screens","Recirculation Pump","Control Operation","Distribution Pump Operation","Level Sensor Operation"] | YES | Musty | Cloudy | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/04/2023 | 12:00 AM
07/28/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Fast | Pump | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","SludgeScum Accumulation","Level Sensor Operation"] | [18 empty] | 0 scum, 3" of sludge. Very little use. cleaned filter. Blower wasnt running. Blower is on timer. Leak in the force main going out of pump tank. it was repaired and good now. Field dry. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/04/2024 | 12:00 AM
10/30/2023 | Alternative | Routine/Scheduled | 103-STS-97450 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2600 | Clearstream |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 35.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 01:29 PM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance | 154-08-0374 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | Air pump filter will be replaced in the near future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
05/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
08/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Heavy amount of solids recommend to pump all tanks before a clog could occur | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
03/03/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Fast | Pump | Pressure | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | 0 scum 6" of sludge in the septic tank. o sludge in other tanks. Runtime 657h 33m 39s. 4331 doses. leaned filters, Verified alarm, ran pump, and walked field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/06/2023 | 08:30 AM
10/16/2023 | Alternative | Reportable Incident | 228-14-0493 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/16/2023 | Dec 30 1899 7:30AM
12/11/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/11/2023 | Dec 30 1899 11:10AM
03/30/2023 |  | RoutineScheduled | 033-06-0543-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
09/05/2023 | Alternative | Reportable Incident | 199-05-0058 | York | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Repair - Service Primary septic tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - control panel replaced - float sensors and pump operating. DBox - intact | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/07/2023 | Dec 30 1899 10:15AM
08/29/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | septic | pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 08/29/2023 | Sample Chamber | 10.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/05/2023 | Alternative | RoutineScheduled | 027-STS-15637 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Clearstream |  | Pump | Pressure | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Level Sensor Operation","Effluent Screens","Dispersal System Operation","Control Operation","Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/05/2023 | 12:00 AM
04/05/2023 |  | RoutineScheduled | 033-STS-91813 | Caroline | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Upon arrival, water level in tank was lower than normal. Additional investigation showed tanks are leaking. Installer & tank manufacturer have been notified. Tank manufacturer is taking steps to repair. Adjusted pump settings to design. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/02/2023 | 07:49 AM
07/25/2023 | Alternative | Reportable Incident | 196-07-195 | Westmoreland | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Last documented service conducted 2017 - owner contacted office regarding wetness around modules. Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. BioFilter - four modules - all four modules have standing effluent - overflowing from vent holes when pump operates. Sample port is DRY! Biofilter has failed and requires replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/27/2023 | 07:30 AM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/06/2024 | 10:42 AM
03/30/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/28/2023 |  | Initial Visit | 181-02-0445 (LEGACY ALT. SYSTEM) | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | Sand Filter | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation","Other","Effluent Screens"] | ["Dispersal System Operation","Other","Effluent Screens"] | YES | [17 empty] | The system didn't need to be pumped. The zone valve box was dug out to expose the air release valves and they were extended to prevent future clogging. The return effluent line was dug up and repaired due to settling soil around the pump tank. A ball valve and pressure gauge was added in the effluent line. This was added to be able to adjust the pressure on the drip field. The controls were operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/24/2023 | 08:40 PM
07/14/2023 | Alternative | RoutineScheduled Component Maintenance | SD-12-174 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001236 | Stuart | Lynn | 2.000000 | 16000 | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation"] | ["Dispersal System Operation" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | NA | Musty | Cloudy | 6.400000 | 4.500000 |  |  |  | 06/22/2023 | Sample Chamber | 40.000000 |  |  | 32.000000 | 24.000000 |  | Will be sent separately | Inspected | Pmp Outs 06/01/2023 16890052323 FQCPH (Commercial Pump and Haul) 4,200.00 06/01/2023 16926060123 FQCPH (Commercial Pump and Haul) 4,200.00 06/08/2023 16971060823 FQCPHG (Commercial Pump and Haul by the gallon) 4,200.00 06/15/2023 17029061523 FQCPH (Commercial Pump and Haul) 4,200.00 06/22/2023 17070062223 FQCPH (Commercial Pump and Haul) 4,000.00 06/28/2023 17116062823 FQCPH (Commercial Pump and Haul) 4,000.00 07/06/2023 17157070623 FQRPH (Fauquier County Residential Pump and Haul) 4,200.00 ZOnes tested 23 - 25 gpm each, rotating between zones dosing 2 at a time Effluent clearing up. Identified a broken air line and water blocking air transfer between AX MAx 1 & 2. Aeration imp[roving color on sheets improving Steve Barry with AQWA has control of the recirciuation rates | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/15/2023 | 02:02 PM
04/20/2023 | Alternative | RoutineScheduled | C-03-111-0047 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation","Auxiliary Filter"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/20/2023 | 12:00 AM
04/18/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 12:48 PM
08/25/2023 | Alternative | RoutineScheduled | 03-125-095 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 4 - Blue Crystal tablets installed 11 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/25/2023 | 12:00 AM
11/27/2023 | Alternative | RoutineScheduled Component Maintenance | 179-13-110-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The pump line is broken inside the fourth Puraflo Module. We recommend moving enough peat to make the plumbing accessible and repairing as needed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
12/19/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 6.000000 |  | Septic Tank | Septic Tank #2 | Pump | Pressure | Trenches | Not Applicable |  | ["SludgeScum Accumulation","Recirculation Pump"] | ["Recirculation Pump"] | YES | [17 empty] | Septic Tank #1-10"sludge 10"scum (Requires pump out) Septic Tank #2-4"sludge 4"scum (Cleaned filters) EZ-Treat Recirculation Tank #1-6"sludge 0"scum/ EZ-Treat Tank #2-6"sludge 0"scum/ EZ-Treat Tank #3-6"sludge 0"scum/ Pump Tank to LPD Trenches- 0"sludge/ Pump out only required on the Septic Tank #1/ Cleaned the pump intakes on all recirculation pumps/ Counts: Pump1-0016257 ETM-0024002/ Pump2-0018556 ETM-0023813/ Pumps to LPD: Pump1-819 ETM-165h 56m/ Pump2-780 ETM-158h 28m/ Peak-22/ High-22/ No breakout or spongy areas on the LPD Site and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/10/2023 | Alternative | Routine/Scheduled | 15-142-0091 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1250 | Multiflo ATU |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [17 empty] | Multiflo needs to be pumped out, cleaned and refilled. Septic tank could use a pumpout also. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/10/2023 | Dec 30 1899 10:48AM
01/27/2023 |  | Routine/Scheduled | 234-15-469 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/27/2023 | Jan 1 1900 12:40PM
04/10/2023 |  | RoutineScheduled | 175-04-0084 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Prince William | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Three companies have attempted to fix the zoning valve. Each company replaced it with a new one, only to have it fail within a year. When the zoner plunger is removed the system works flawlessly. When the system plunger is inside, it always sticks on one zone and causes issues. Currently the system needs the blower replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/10/2023 | 12:00 AM
11/13/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Replaced UV control panel | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | Dec 30 1899 8:00AM
05/30/2023 | Alternative | Initial Visit | 150-04-189 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 3 minutes 30 seconds every 2 hours. Did not take sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 03:00 PM
06/29/2023 | Alternative | Reportable Incident | 234-17-0040 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/29/2023 | Dec 30 1899 7:15AM
07/05/2023 | Alternative |  | 2006-143-0252 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 3250 | 1250 | 1000 | Pump | Gravity | Discharge | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | None | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | 12:00 AM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
06/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/26/2023 | 09:42 AM
06/30/2023 | Alternative | Routine/Scheduled | 234-16-14 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | Replaced alarm float in pump tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | Dec 30 1899 12:20PM
03/08/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Trenches |  |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/08/2023 | 12:00 AM
10/02/2023 | Alternative | RoutineScheduled | 095-STS-5455 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Hutchens Septic Services LLC | 1942001509 | Robert | Hutchens, Jr. | 1.000000 | 1250 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/02/2023 | 12:00 AM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/18/2023 | Alternative | Routine/Scheduled |  | Richmond City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Richmond | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 5.000000 | 7500 | Microfast | Microfast | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 35.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/18/2023 | Dec 30 1899 4:55PM
11/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 11/08/2023 | Sample Chamber | 10.000000 | [5 empty] | Attached to this report |  | Septic Tank-4"sludge 6"scum/ Microfast ATU Tank-4"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower is working correctly/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-1063 ETM-14h 3m/ Pump2-1046 ETM-12h 9m/ Peak-10/ High-7/ No breakout or spongy areas on the drainfield and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/11/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Rec keep drainfield maintained | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
08/30/2023 | Alternative | RoutineScheduled | 07-195-197-SP | Washington | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Eco Flo |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Distribution Pump Operation"] | ["Attached Growth Medium","Level Sensor Operation","Distribution Pump Operation","Effluent Screens","Dispersal System Operation","Control Operation","Auxiliary Filter"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | 12:00 AM
10/18/2023 | Alternative | Reportable Incident | 061-STS-21336 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | EZ Treat Sandfilter | [5 empty] | ["Dispersal System Operation","Distribution Pump Operation"] | ["Dispersal System Operation","Distribution Pump Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/29/2024 | 02:55 PM
10/10/2023 | Alternative | RoutineScheduled | 13-163-0086 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/05/2023 | Alternative | Reportable Incident |  | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Weekend Alarm Event - last known service conducted March 2020 System alarming due to diaphragm failure on the compressor. Trash Tank - normal level Aeration Tank - no mixing present - compressor failure - replaced. Pump Tank - float sensors, pump and controls operating - riser lid replaced due to lawn care damage. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/07/2023 | 11:00 AM
04/19/2023 | Alternative | Routine/Scheduled | 157-12-0095 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream, cleaned the mesh screen in the spinfilter, and cleaned the filter in the septic tank. Changed the filter in the aerator. There is a spot on the drainfield - needs to be checked out. The timer is set to 6 minutes every 1 hour. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/19/2023 | 03:00 PM
10/24/2023 | Alternative | RoutineScheduled | 128-06-198 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  |  |  | Pad |  |  | ["None"] | ["None"] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/22/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-88024 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for routine inspection. All tanks have infiltration. Junction box inside of the pump tank is not up to code. Zone 3 drip rate is very low. Proposal to be sent. Repaired zone 2 Arv. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
05/17/2023 | Alternative | RoutineScheduled | 18-160-0027 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000 | Whitewater |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Distribution Pump Operation","SludgeScum Accumulation"] | [] | NA | Septic | [6 empty] | 05/17/2023 | Sample Tap | [6 empty] | Will be sent separately | Inspected | - recommend riser installation for future maintenance | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/23/2023 | 12:00 AM
03/17/2023 |  | RoutineScheduled | 132-05-0043 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/19/2023 | 12:00 AM
12/22/2023 | Alternative | Routine/Scheduled | 810-STS-3959 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/22/2023 | Dec 30 1899 8:00AM
12/15/2023 | Alternative | RoutineScheduled Component Maintenance | 175-04-0852 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | 01:58 PM
01/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | Dec 30 1899 2:21PM
07/26/2023 | Alternative | Follow-Up Component Maintenance | SWP-04-161 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank and pump tank pumped out by others on the 24th. Degraded peat was removed by hand and new peat was installed. Lots of roots in bottom of pods, added root destroyer. Replaced 1 support bar. Degraded peat was dumped at Spotsylvania Refuse. Peat was purchased by Driller Services. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:19 PM
10/17/2023 | Alternative | RoutineScheduled Component Maintenance | SD-02-717 | Culpeper | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity |  | Chlorination |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [7 empty] | 8.000000 | 0.030000 | 2419.600000 | 3.800000 |  |  | Will be sent separately | Inspected | Dissolved Oxygen 2.3. We continue to recommend replacing the junction box inside the Advantex tank and remounting the aerator panel. We also continue to recommend replacing the concrete lids and aerator stone. The Advantex sheets have stretched. We recommend installing new sheets. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/01/2023 | 07:38 AM
11/06/2023 | Alternative | Routine/Scheduled | 136-13-0041 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Found at normal level with less than 1" of solids and 6" of sludge. -Discharge/Pump Tank: Found water at normal level. All components are working properly. Less than 1" of solids and sludge -Aeration: Water at normal level. Pulled and cleaned weir and diffuser. -Air Pump/Blower: Raised platform All components are working properly and functioning properly. Air pump is pulling 1.44 amps -Control Panel: Inside air pump and all components are working properly. 120v -LPD: No signs of ponding or soft wet spots | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 09:54 AM
06/07/2023 | Alternative | RoutineScheduled | 14-142-0040 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Effluent Screens","Distribution Pump Operation"] | ["Attached Growth Medium","Control Operation","Effluent Screens","Distribution Pump Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/09/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-87780 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Clogged sim-tech filter and pump intake, cleaned and also spoke to customer about problems with using garbage disposal. Raked media. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
05/16/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20-RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Scum level-1-2"- 13-16" sludge in Septic tank -treatment unit recirc zone of tank - 8" sludge - Discharge zone 5" sludge, clear effluent on top. Cleaned Effluent filter, Ran in test mode, Good spray on media , all floats tested ok, Alarm functional., Recirc pump ran 1869.3 hours and 61,470 cycles and discharge ran 52.8 hours and 2509 cycles, it has 2697 days trended in history. Aalarm log 2-25-23, 12-30-22 ad 12-14-22, 1 alert on 12-30-22 high use. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
05/19/2023 | Alternative | RoutineScheduled | 43080118 | Clarke | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lord Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/14/2023 | 12:10 PM
01/09/2023 |  | RoutineScheduled | 177-06-0591-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation" ,"Control Operation" ,"Dispersal System Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation" ,"Control Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Upon arrival, fuses were blown in the main panel and remote zone panel. Lightbulbs for zone 1, zone 2, and zone master are not working and should be replaced. The filter media in the aerobic treatment unit is clogging and beginning to float. We recommend treating the media and pumping the tank afterwards. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
08/21/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation","Recirculation Pump"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | 12:00 AM
02/01/2023 | Alternative | Pump-Out Only | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 | 500 | 1000 |  | Pump | Pressure | Drip | UV |  | [] | [] | NA | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/05/2023 | Dec 30 1899 1:30PM
10/12/2023 | Alternative |  | 179-STS-91869 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
10/06/2023 | Alternative | Routine/Scheduled | 15-120-0435A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Aqua Klear |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/06/2023 | Dec 30 1899 9:24AM
01/26/2023 | Alternative |  | SD-08-135 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan |  |  | Grace & Tom | Fullman | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/06/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/06/2023 | Dec 30 1899 2:00PM
09/26/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Attached Growth Medium"] | ["Auxiliary Filter"] | [18 empty] | FAST appears clogged and tanks need pumping | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/13/2023 | 12:00 AM
06/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump chamber concrete lid was replaced. Recommend pumping ATU and possibly the pump chamber as there is some scum. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/16/2023 |  | Routine/Scheduled | 10-118-0010 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Hoot |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - sensor probe operating - pump & controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | Jan 1 1900 7:15AM
08/04/2023 | Alternative | RoutineScheduled | 107-08-0497 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
09/13/2023 | Alternative |  | 02-125-270 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 09/13/2023 |  | 9.160000 |  |  | 4.800000 |  |  | Will be sent separately |  | BOD: 9.16 TSS: 4.80 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
05/02/2023 | Alternative | Routine/Scheduled | 151-04-110 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | Dispersal System Operation | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Routine Service Real Estate Inspection. Primary septic tank pumped empty / inspected - multiple toilet fixture leaks! Biofilter - concrete - peatmoss in good condition - wet - hydraulically overloaded - raked / turned. Pump Basin - float sensors, pump and controls operating. DBox - plastic - intact - above normal level - believe hydraulically overloaded due to toilet fixture leakage. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/03/2023 | 06:30 AM
01/02/2023 |  | RoutineScheduled | 05-125-105 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 2 Chlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/02/2023 | 12:00 AM
08/30/2023 | Alternative | RoutineScheduled | 196-14-139 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters, peat check | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/08/2023 |  |  | 16-142-0096 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Ecopod | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/08/2023 | 12:00 AM
02/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/07/2023 | Alternative | RoutineScheduled | SD-89-475 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2000 | septic | ATU | Gravity | Pressure | Discharge | Chlorination |  | [] | [] | YES | Musty | Clear |  | 10.500000 |  | 1.010000 |  | 05/07/2023 | Pump Chamber | 16.000000 | 0.000000 |  | 12.600000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/26/2023 | 08:35 AM
11/01/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-88840 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"Attached Growth Medium"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend mowing the tall grass growing at the edges of the dispersal area and maintaining this in a mowed condition to prevent root intrusions. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
07/13/2023 | Alternative | RoutineScheduled | 043-STS-34600 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | EZ Treat | Pump | Pressure | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | High water alarm in 1st pump tank. Pump wasn't working to pump to EZ Treat. Fixed revisited on 7/31/2023. 0 Scum very little sludge. Filter is clean. 104 cycles in 2nd pump tank 3 hrs 25 min run time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | 12:30 PM
09/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. Septic & ATU needs pumping. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | 12:58 PM
01/25/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | DeHaven's Backhoe Service Inc. | 1942001541 | Wayne | Edmonson | 2.000000 | 2500 | Advantex |  | Pump | Pressure | Drip | Not Applicable | 175.000000 | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/25/2023 | 05:00 PM
04/18/2023 |  | RoutineScheduled | 101-12-0405 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/23/2023 | 12:00 AM
11/13/2023 | Alternative | RoutineScheduled | 2005-143-0144 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Ecoflo |  | Pump | Gravity | Trenches |  |  | [] | ["Control Operation","Distribution Pump Operation","Level Sensor Operation"] |  | None | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 12:00 AM
11/03/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-12"sludge 4"scum/ Microfast ATU Tank-14"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ Recommend pump out of the Septic-Microfast Tank very soon/ Blower air filter cleaned and blower is working correctly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-6773 ETM-858h 30m On 11m 10s Standard Off-3h Peak Off-2h 8m/ Peak count-33/ High level-40/ Watermeter-02148058/ No breakout or spongy areas on the 3 zone American Drip System and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced contactor Pump is bad and took a electrical surge | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/06/2023 | 03:05 PM
06/30/2023 | Alternative |  | SD-10-247 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [16 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 09:25 AM
04/26/2023 |  | RoutineScheduled |  | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 0-0 0-0 | 0-0 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Level Sensor Operation","Distribution Pump Operation","Control Operation","BlowerCompressorAerator Operation","Attached Growth Medium"] |  | None | Clear |  |  | 0.000000 | [11 empty] | Inspected | sysyem pumped out by others. system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | 09:00 AM
05/11/2023 | Alternative | Reportable Incident | 107-04-0368 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | YES | Pungent | Clear | [15 empty] | Blower inoperable. Replaced Blower | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/06/2023 | 12:00 AM
12/04/2023 | Alternative | Routine/Scheduled | 19-120-0091AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Septic Tank Condition of above Component Notes for above Component Water level normal. Flushed and cleaned effluent screen. Not due for pump out. Noted signs of groundwater infiltration within septic tank riser. Effluent screen assembly is deteriorating. Effluent screen is obsolete and discontinued Discharge/Pump Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. Peat Moss Condition of above Component Notes for above Component Raked and tilled peat moss. Peat moss is in good condition. Structural integrity of tipping bucket appears to be intact. Checked and confirmed tipping bucket is functioning properly. Distribution Box Condition of above Component Notes for above Component Low water level. Structural integrity of distribution box appears to be intact. Four header lines clogged with roots Drain Field Condition of above Component Notes for above Component Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 9:40AM
03/07/2023 |  | RoutineScheduled | 13-197-A2 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 3 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/07/2023 | 12:00 AM
08/14/2023 | Alternative | Reportable Incident Component Maintenance | SD-11-325 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Septic | [14 empty] | Will be sent separately | Inspected | Atu alarm. Replaced failed capacitor. Blower resumed running at 3.05 amps (maximum is 3.6 A). Septic odor should be gone in 24 to 48 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
09/22/2023 | Alternative | RoutineScheduled | 121-STS-12601 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Southwest Soils, Inc. | 1942001494 | Stephen D. | Dalton | 1.000000 | 1000 | AS 500 | N/A | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["Other"] | ["SludgeScum Accumulation","Other"] | NA | Musty | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/22/2023 | 01:30 PM
06/26/2023 | Alternative | Reportable Incident Component Maintenance | 179-STS-88746 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for ez treat panel in alarm. Homeowner had the tank pumped out prior. Pump was drawing 5.4 amps. Normal running amps are around 11.0. Replaced failed pump and replumbed it with pressure pipe. Recomend adding a sim tech filter to ez treat pump to help its lifespan during the next yearly inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
01/20/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/31/2023 |  | Pump-Out Only | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | [] | NA | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | Jan 1 1900 4:00PM
11/13/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | Dec 30 1899 9:50AM
08/01/2023 | Alternative | RoutineScheduled | 166-19-0016 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/20/2023 |  | RoutineScheduled |  | Warren | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Blower panel silence and visual not functioning still needs repair Inlet blocked and pumped | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/28/2023 | 02:17 PM
11/02/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | Dec 30 1899 2:02PM
09/11/2023 | Alternative | RoutineScheduled Component Maintenance | 165-STS-333615 | Rockingham | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | ET BED overgrown and unable to check properly and ponding present when pump activated | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/13/2023 | 01:07 PM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
03/03/2023 |  | RoutineScheduled | 08-113-245 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/03/2023 | 12:00 AM
01/31/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [8 empty] | 1059.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/10/2023 | 12:00 AM
09/28/2023 | Alternative | Reportable Incident | 107-02-0610 LEGACY ALT. SYSTEM) | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Pressure | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | Musty | Clear | [15 empty] | replaced vpeat moss | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/09/2024 | 12:00 AM
04/03/2023 |  | RoutineScheduled |  | Frederick | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | McKim Septic & Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/08/2023 | 02:00 PM
02/02/2023 |  | Routine/Scheduled | S 800-13-0161 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | Jan 1 1900 2:00PM
09/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 3:40PM
03/01/2023 |  | RoutineScheduled | 177-14-0211-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. 1 spinner came apart, cleaned and put back in place. Treatment looks cloudy probably due to spinners not working or something being used in the house. Will check next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
02/10/2023 |  | RoutineScheduled | {FIPSCode}-STS-24251 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/10/2023 | 12:00 AM
11/20/2023 | Alternative | Routine/Scheduled |  | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Aqua Klear |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/20/2023 | Dec 30 1899 2:26PM
01/05/2023 |  | RoutineScheduled | 196-18-0021 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"Distribution Pump Operation" ,"Dispersal System Operation" ,"BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
04/20/2023 |  | Reportable Incident | 153-STS-19007 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Recirculation Pump"] | ["Recirculation Pump"] | [18 empty] | Service call only: Replaced faulty Recirc. Pump Model# 5031-0009 Pump cnts-74987 ETM-465583 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
01/30/2023 |  | RoutineScheduled | 033-STS-87594 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
08/10/2023 | Alternative |  | 003-STS-32299 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Josh | Sheline | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/09/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 RT |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | [18 empty] | 180 day | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/09/2023 | 12:00 AM
04/25/2023 |  | RoutineScheduled | 2032-96-153 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity |  | Chlorination |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Disinfection"] | ["Disinfection"] | NA | Musty | Clear | 7.200000 | 5.600000 |  | 0.000000 |  | 04/26/2023 |  | 3.000000 |  |  | 3.000000 |  |  | Will be sent separately | Inspected |  | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 05/15/2023 | 12:48 PM
03/08/2023 |  | Follow-Up | SP 00-250 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | On site to attempt to restore drip and flush rates. On arrival, zone 2 (lower zone) ARV was stuck in closed position so tubing is not venting properly. Bleach-flushed both zones and rates came back to acceptable levels. Zone 2 ARV was stuck again at end of testing, zone 1 dropped normally. Recommend installing new top-feed manifolds an inch or two above the drip tubing, per American Mfg recommendations. This should correct any venting issues and will take care of any roots causing problems at the manifolds. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
12/18/2023 | Alternative |  | 04-184-5004 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/18/2023 |  | 19.700000 |  |  | 7.600000 |  |  | Will be sent separately |  | BOD: 19.7 TSS: 7.60 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 12:00 AM
05/24/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 15000 | Large Treatment System |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Large Treatment unit Not listed in VDH list - Sludge levels--septic front zone 7' and n activated sludge section 24-26" . Clarfier zone had 3-4 ft of sludge, System is doing good at this time and does not need pumping. Operators on site be backwashing and to keep suldge from getting very thick on the bottom. Both Blowers are operational and alternating as they should. Discharge Pump1 ct 44,390 vs 39,489 = 4,901 cycles since last visit. etm 184153min vs 169983=14,170 min or 236 hours - Pump#2 ct40898 vs 36001= 4,897 cycles- ETM 257,329 vs 241549 = 15,780 min, or 263 hours run time- Continue to backwash to prevent blocking up of sludge. Drip Drainfield he trees down and is being repair by owner. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
05/10/2023 |  |  | 033-STS-89067 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
04/21/2023 |  |  | 033-06-0157-ST | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
02/02/2023 | Alternative | RoutineScheduled Component Maintenance | 175-04-0113 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Cleaned air pre-filter as preventative maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 06:43 AM
02/17/2023 |  | Pump-Out Only | 196-07-098 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 300.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Pumped all tanks empty to conduct "saturation" test to locate leaks in tanks if any. Found pump tank fractured. Does not appear to be "repairable". Refilled processing tank with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 10:45 AM
10/31/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | NONE |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | Meters - A - 950, B -680, C - 910. Tested both discharge pumps in "HAND", both pumping. Still no gallons pumped to drain field. Water has added to model home on Cliffs Drive. Approximately 2,400 gallons added over several days. Owner is looking into pressure testing the force main system again to look for leaks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | 07:03 PM
04/17/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, UC Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend evaluation of the distribution boxes. Trees on neighboring lot could potentially cause damage to the system (Force main, Distribution Boxes, Headers, Lines). The septic tank is listed as a plastic tank but was replaced in 2014 with concrete tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
12/04/2023 | Alternative | RoutineScheduled Component Maintenance | 179-16-0238-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | There is a wet area below the mound. There was not enough water to test the drip system to see if it is the source of the water. A follow-up visit to add water to the system and complete a drawdown is planned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
01/17/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | Dec 30 1899 11:08AM
04/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
12/27/2023 | Alternative | RoutineScheduled | 12-135-3075 | Giles | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | 2.000000 | 1080 | ECOFLO |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Septic | Cloudy | [6 empty] | Pump Chamber | [6 empty] | Will be sent separately |  | - peat moss needs to be replaced - both tanks need to be serviced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/28/2023 | 12:00 AM
03/09/2023 |  | RoutineScheduled | 087-STS-6545 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1000 | EZ Treat |  | Pump | Pressure | Pad |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/10/2023 | 12:00 AM
09/08/2023 | Alternative | Reportable Incident Component Maintenance | 099-STS-88845 | King George | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Disinfection" ,"Dispersal System Operation" ,"Attached Growth Medium" ,"SludgeScum Accumulation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Disinfection" ,"Dispersal System Operation" ,"Attached Growth Medium" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for wet spots in drip field. Low level and enable float failed in dischargr tank. Replaced both floats. Will follow up to dig up emitters in drip field. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/02/2023 | 05:18 AM
01/17/2023 |  | RoutineScheduled | 108-14-0011 | Bath | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens","SludgeScum Accumulation"] | ["Auxiliary Filter","Effluent Screens","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | The septic/microfast tank and the pump tank were both pumped and cleaned. The controls were operating as designed. The blower and spin filters were both cleaned. The effluent screen was cleaned on the discharge pump. There were no visible leaks in the drip field. There was return effluent returning to the pump tank so the drip field is operating as designed. The pressure was adjusted on the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/25/2023 | 05:10 PM
04/10/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Rejected | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/10/2023 | 12:00 AM
12/06/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | Dec 30 1899 4:00PM
10/05/2023 | Alternative | Routine/Scheduled | 087-STS-6561 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out. Noticed root infiltration around base of riser -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Flushed and cleaned vortex filter. Discharge pump has exceeded life expectancy. Discharge pump is pulling high amperage showing signs of impending failure. -Aeration: Water level normal. Not due for pump -Air Pump/Blower: Checked and confirmed aerator is functioning properly. Flushed and cleaned aerator air intake filter -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Drip Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 09:39 AM
04/24/2023 |  | RoutineScheduled | 067-STS-38051 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20-RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | Sludge level-minimal scum layer on top-10" sludge trace on bottom in Septic tank zone - Recir zone 8" sludge - Pump tank - light Trace sludge, Discharge zone 6" sludge, Pulled out and Cleaned Effluent filter, media looks clean, good spray on media. Float switches tested good, alarm test good. Recirc pump run time 458.1 hours and 38414 cycles and discharge pump has 10.2 hours run time and 311 cycles, one Alarms in history on 11/25/22, 575 days trended since 9-26-2021 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
05/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/19/2023 | Alternative | RoutineScheduled | 166-16-026 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
02/08/2023 | Alternative | Routine/Scheduled | 151-10-0075 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/09/2023 | 10:00 AM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Fittings that connect blower to downshaft are damaged | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
01/19/2023 |  | RoutineScheduled |  | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 11:08 AM
07/28/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Other"] | ["Other"] | [18 empty] | Replaced Clearstream Blower, Control Panel and Distribution box lid. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
04/10/2023 |  | RoutineScheduled | 177-STS-91748 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation"] | NA | Musty | Clear | [5 empty] | 04/10/2024 |  | 34.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. HL 14, HL ETM 44M, PEAK 17, PEAK ETM 12H17M. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
08/10/2023 | Alternative | RoutineScheduled | 16-183-003 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation"] | NA | Musty | Clear | [15 empty] | 3 - Blue Crystal tablets added 6 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/10/2023 | 12:00 AM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | System is connected to 36001 and has the same issues. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/08/2023 | Alternative | RoutineScheduled | 05-160-0324 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | King's Alternative Septic | 1942001112 | William | King, II | 2.000000 | 2000 | Orenco Advantex |  | Gravity | Pressure | Drip | Not Applicable | 150.000000 | ["Auxiliary Filter","Effluent Screens","Other"] | ["Auxiliary Filter","Effluent Screens","Other"] | YES | [17 empty] | Pump tank is not holding fluids, tank needs to be replaced and customer was advised this information. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/08/2023 | 12:00 AM
01/24/2023 |  | RoutineScheduled | 04-192-236 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 12 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/24/2023 | 12:00 AM
12/05/2023 | Alternative | RoutineScheduled Component Maintenance | {FIPSCode}-STS-74680 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend pumping the Advantex recirculation tank due to sludge accumulation in the tank. We also recommend replacing the Advantex pod vent cap. You can pick one up at a local home improvement store, or we can replace this for you. Please contact our office if you would like our assistance with this repair. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
08/30/2023 | Alternative | RoutineScheduled | 150-06-128 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | [] | [] | [18 empty] | We replaced an Orenco UV Bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 12:00 AM
08/02/2023 | Alternative | RoutineScheduled | 06-100-1288 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | ECOFLO |  | Pump | Gravity | Pad | Not Applicable | 300.000000 | [] | [] | [18 empty] | SLUDGE JUDGE 4" FROM BOTTOM REPLACED PEAT | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/01/2023 | 01:55 PM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
03/13/2023 |  | RoutineScheduled |  | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Rappahannock-Rapidan | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
02/10/2023 |  |  | 05-142-0469 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Ecoflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/13/2023 | 12:00 AM
11/27/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Replaced pump | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/27/2023 | Dec 30 1899 8:30AM
04/17/2023 |  | RoutineScheduled | 179-15-0023-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Inlet side on septic tank has a 10" thick layer of hard grease, wipes and condoms. Spoke to tenants about Do's and Don'ts. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
12/19/2023 | Alternative | RoutineScheduled | 2059-99-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | SBR |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | NA | Musty | Clear | 7.700000 |  |  | 1.900000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/20/2023 | 12:00 AM
03/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/21/2023 |  | RoutineScheduled | 067-STS-38686 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. 0" of solids in discharge pump tank. Flushed treatment unit spray manifold. Cleaned recirculation pump basket filter. tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/16/2023 | 07:03 PM
02/21/2023 |  | Routine/Scheduled | 800-05-0351 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/21/2023 | Jan 1 1900 1:08PM
05/23/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 12:00 AM
04/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/07/2023 | Alternative | Routine/Scheduled | 228-16-0099 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Replaced the buzzer. The septic tank need additional risers on it to be properly inspected in the future. The timer is set to 12 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | Dec 30 1899 1:15PM
12/18/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2024 | Dec 30 1899 11:49AM
11/16/2023 | Alternative | RoutineScheduled | 18-142-0421 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/20/2023 | Alternative | Initial Visit |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream (was broken off), changed the filter in the aerator, and changed the mesh screen in the spinfilter. Fixed the airlines - they were backwards. The timer is set to 4 minutes every 2 hours. Did not take samples. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/20/2023 | Dec 30 1899 12:00PM
05/10/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1875 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/11/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Lines were unevenly nitrified upon arrival. The Distribution Box was uncovered and re-leveled. The system should return to proper function. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/03/2023 | Alternative | Reportable Incident | SD-12-381 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | replaced compressor, cleaned filters | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/30/2023 |  | RoutineScheduled | 179-06-0276-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 1-6 0-0 | 0-0 | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear |  |  | 12.000000 | [11 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 10:00 AM
11/20/2023 | Alternative |  | 027-STS-17817 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/20/2023 |  | 7.240000 |  |  | 1.300000 |  |  | Will be sent separately |  | BOD: 7.24 TSS: 1.30 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | 12:00 AM
07/24/2023 | Alternative | Routine/Scheduled | 157-11-0014 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Aeration Tank - normal level - mixing present - compressor serviced. High settleable solids, recommend pumpout and refill. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/25/2023 | 07:15 AM
01/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | DSS replaced septic pump. System appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
02/16/2023 |  | Reportable Incident | 107-08-0117 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Distribution Pump Operation","Effluent Screens"] | ["Distribution Pump Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | Replaced pump | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/08/2023 | 12:00 AM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
05/30/2023 |  | Initial Visit | 17-120-0456A | Chesterfield | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Rejected | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit Owner reports that aeration alarm has been active for over a year! Trash Tank - normal level Aeration Tank - normal level - NO MIXING - Aspirator Failed. Clarifier - normal level - effluent screen serviced. DBox - intact. Ordered replacement aspirator | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/05/2023 | Jan 1 1900 1:30PM
02/11/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | AUNA BioCoir |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. System was converted from a PuraFlo peat system to a Anua BioCoir system. 10" of accumulated solids in first chamber of septic tank. 10" of accumulated solids in second chamber of septic tank. 6" of solids in recirculation tank. Cleaned septic tank solids filter. Septic tank level was slightly elevated due to clogged septic filter. Returned to normal after cleaning the filter. Good spray pattern on spray nozzles in treatment unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 07:03 PM
06/20/2023 | Alternative | Routine/Scheduled | 07-137-0015 | Goochland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Aquaworx Remediator |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/20/2023 | Dec 30 1899 8:52AM
10/27/2023 | Alternative | Routine/Scheduled |  | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/27/2023 | Dec 30 1899 2:22PM
04/03/2023 |  | RoutineScheduled | 179-14-0324-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 2-3 0-1 | 0-0 | [5 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] |  | None | Clear |  |  | 9.000000 | [11 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | 09:00 AM
11/13/2023 | Alternative | Follow-Up |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | [9 empty] | ["Control Operation","Distribution Pump Operation"] | ["Control Operation","Distribution Pump Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/30/2024 | 12:07 PM
03/24/2023 | Alternative | RoutineScheduled | 02-163-0408 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Advantex |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","Effluent Screens","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/24/2023 | 12:00 AM
11/13/2023 | Alternative | RoutineScheduled Component Maintenance | 033-STS-90182 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | There is a damaged riser lid on the Advantex tank which should be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
03/09/2023 |  | RoutineScheduled | 153-STS-20183 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
06/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/10/2023 |  | RoutineScheduled | 177-STS-88308 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Dispersal System Operation"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
01/27/2023 |  |  | 132-14-0068 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Virginia Soils Inc, dba VSI Supply / AG Onsite | 1942001291 | Archie | Arnold | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/15/2023 | 12:00 AM
01/11/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Cloudy | 7.410000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2023 | 12:15 AM
01/18/2023 |  | Initial Visit |  | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Three Rivers | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit Primary septic tank - normal level - effluent screen serviced. Aeration Tank - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/19/2023 | 08:00 AM
09/27/2023 | Alternative | RoutineScheduled | 04-100-0266 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 2.000000 | 750 | ECOFLO |  | Pump | Gravity | Pad | Not Applicable | 300.000000 | [] | [] | [18 empty] | SLUDGE JUDGE OF SEPTIC TANK REVEALED 2-3" FROM BOTTOM AUGERED PEAT -LOOKS GOOD EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/08/2024 | 10:50 AM
06/14/2023 | Alternative | Routine/Scheduled | 234-16-403 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | Replaced UV Bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | Dec 30 1899 11:25AM
06/05/2023 | Alternative | Routine/Scheduled | 087-STS-6518 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. BioFilter - peatmoss in good condition - raked / turned. Pump Basin - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | 07:30 AM
11/02/2023 | Alternative | RoutineScheduled | 08-100-0872 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | BOICOIR |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | [] | [] | YES | [16 empty] | Pumped Out | SLUDGE JUDGE REVEALED 6-8" FROM BOTTOM AND 5-6" FROM TOP-PUMPED SEPTIC REPLACED 4 BOICOIR NOZZLES THAT WERE RUSTED EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/07/2023 | 02:35 PM
11/01/2023 | Alternative | Follow-Up Component Maintenance | 175-14-0514 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed SCL06 compressor. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
11/09/2023 | Alternative | RoutineScheduled | 101-STS-96058 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 1.000000 | 1500 | Clearstream ATU |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation","Distribution Pump Operation"] | ["Distribution Pump Operation","Control Operation","BlowerCompressorAerator Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear |  |  | 10.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/21/2023 | 10:45 PM
09/01/2023 | Alternative |  | 033-07-0264-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
11/01/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Clear | 7.100000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 02:10 PM
09/27/2023 | Alternative | RoutineScheduled Component Maintenance | 099-06-0122-SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend replacing the PSI Gauge on the drip dispersal system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
03/20/2023 | Alternative | Reportable Incident | 073-STS-105169 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | COSS - Maintenance - GMP2018-02 Replaced damaged / deteriorated DBox with new. Spliced to existing conveyance line. Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/21/2023 | 06:30 AM
03/07/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 270505173 | Joshua | Hott | 1.000000 | 1250 |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/14/2023 | Alternative | Routine/Scheduled | 234-17-0040 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | Dec 30 1899 10:45AM
05/22/2023 |  | Routine/Scheduled | 228-05-0550 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/22/2023 | Jan 1 1900 10:20AM
03/16/2023 |  | RoutineScheduled | 17-192-154 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/16/2023 | 12:00 AM
08/23/2023 | Alternative | RoutineScheduled | 195-STS-27217 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 | [11 empty] | Pungent | Clear | 7.500000 | 6.000000 | [13 empty] | The odor may be fixed by adding a cap to the septic side. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
06/20/2023 | Alternative | RoutineScheduled | 154-14-0133 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | 12:00 AM
05/09/2023 | Alternative |  | 2016-143-0245 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1750 | 1000 | 750 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation","Control Operation","Auxiliary Filter","Disinfection"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/09/2023 | 12:00 AM
11/30/2023 | Alternative | RoutineScheduled | 90-184-003 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
12/18/2023 | Alternative | RoutineScheduled | 15-160-0158 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | 1.000000 | 1500 | Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | Septic | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 12:00 AM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
10/05/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Meet with the pumping company and pumped and cleaned the Clearstream tank and pump tank. Appears midseam tank maybe leaking around the seam and outlet pipe. Recommend installing a filter in the septic tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | Dec 30 1899 12:00PM
05/10/2023 | Alternative |  | 08-160-0183 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [18 empty] | - inspected on 05-10-23, recommend tank be pumped and cleaned, recommend repair to correct aerator as air was not making it to tank - customer's brother in law completing the work, will reevaluate at next inspection unable to clear system as functional until that point | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/26/2023 | 12:00 AM
04/03/2023 |  | RoutineScheduled | 03-192-073 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 2 Chlorine 4 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/03/2023 | 12:00 AM
03/16/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | SEPTIC TANK AND FUJI TANK NEED PUMPED OUT | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
04/06/2023 |  | Routine/Scheduled |  | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Routine Service - System way overdue for service - no contract. Processing tank - pumped - RSV, Recirc pump & effluent screen serviced. - Panel appears to have taken lighting strike / power surge - Replaced 04/07/2023! Treatment Module - media drapes bridging - spray grid serviced. Pump Tank - pumped down - float sensors, pump and controls operating. DBox - at grade - intact. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/10/2023 | Jan 1 1900 8:00AM
12/06/2023 | Alternative | RoutineScheduled | 04-165-0096 | Northampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 750 | Septic Tank | Biomicrobics / Microfast | Gravity | Pressure | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/11/2023 | 12:30 AM
01/23/2023 |  | RoutineScheduled |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith | 1.000000 |  | EZ Treat Sandfilter | none | Gravity | Gravity | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/27/2023 | 07:00 PM
12/11/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Clear | 7.310000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/27/2023 | 01:45 PM
09/05/2023 | Alternative | RoutineScheduled | 079-STS-31687 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/22/2023 | 12:00 AM
03/24/2023 |  | Routine/Scheduled | 2011-143-0003 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | SludgeHammer |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/24/2023 | 12:00 PM
02/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Septic/ Microfast and Pump Tank- No effluent due to the house is not occupied/ No samples taken at this time. Blower air filter cleaned and working/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-1 ETM-2m/ Pump2-1 ETM-2m/ Peak-1/ High-1/ No breakout or spongy areas on the drainfield. Samples will have to be taken after the system is in use. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/03/2023 |  | RoutineScheduled | 179-09-0183-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Removed small roots in all 5 pods. 3 lines had water not flowing into them so adjusted dialflows to aloud them to dry. Will check and adjusted them next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 09:31 AM
03/30/2023 |  |  | 2006-143-0345 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | [9 empty] | [] | ["Effluent Screens","Attached Growth Medium"] | YES | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/30/2023 |  | Routine/Scheduled | 196-02-588 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Biofilter - 4 modules - peatmoss spent - requires replacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 01:15 PM
02/10/2023 |  | RoutineScheduled | 177-06-0048-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Broken riser on septic tank outlet riser, replaced. Sealed inlet riser of septic looks like it was leaking. Sealed inlet riser on pump tank looks like it was leaking a little. Customer replaced all lids with new ones. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
02/14/2023 |  | Reportable Incident | 132-05-0289 | Fluvanna | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2500 | Norweco |  | Pump | Pressure | Mound | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["Control Operation","Effluent Screens"] | YES | Septic | Black | [15 empty] | Faulty Control Panel Replaced - Time Dose not operating correctly on old panel Floats re-wired into splice box Effluent Screen Cleaned *Needs an Aerator* | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 02/14/2023 | 04:00 PM
05/12/2023 | Alternative | RoutineScheduled | C-13-111-0059 | Botetourt | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Delta whitewater |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Routine inspection visit, Both Alarms are operatrional, blower motor running but was in silence mode and treatment had no aeration. The Blower air filter was cleaned and suldge volumes measured, The septi tank has 4-5" scum and 14" sludge, the treatment tank has thin scum layer and trace of sludge, the pump tank has about 24" sludfe. The blower runs but no aeration is observed, the air line needs replacement or reconnection running from tank to home. Sink Septic pumped out treatment tank last year. Air line needs replacement to return to normal operation. The owner reached out to an installed to contduct the repairs. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/30/2023 | Jan 1 1900 9:30AM
03/25/2023 |  | RoutineScheduled | 2007-143-0130 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Ecoflo |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Control Operation","Auxiliary Filter","Distribution Pump Operation","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/25/2023 | 12:00 AM
08/01/2023 | Alternative | Reportable Incident | 109-02-0784 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 500 | Bio Microbics-Fast |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [16 empty] | Inspected | Replaced the blower motor and system returned to normal operation | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/30/2023 | 09:30 AM
07/19/2023 | Alternative | RoutineScheduled | 109-STS-34549 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | 12:00 AM
12/14/2023 | Alternative | Pump-Out Only | 228-16-0058 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | Dec 30 1899 1:00PM
04/11/2023 | Alternative | RoutineScheduled | SD-09-13 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | EcoPod needs pumping. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/02/2023 | 04:23 AM
07/17/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-89946 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation"] | ["Distribution Pump Operation" ,"Dispersal System Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/07/2023 |  | Reportable Incident | 107-08-0398 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | blower alarm blower wire had to be repaired | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/08/2023 | 12:00 AM
10/27/2023 | Alternative | RoutineScheduled | VAG408110 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 2.000000 |  | Constructed Wetlands |  | Pump | Gravity | Discharge | Chlorination |  | [] | ["Control Operation","Disinfection","Distribution Pump Operation"] | NA | None | [16 empty] | Not discharging at time of inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/12/2023 | 09:20 AM
09/30/2023 | Alternative |  | SD-09-90 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [18 empty] | See attachment | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 12:00 AM
08/15/2023 | Alternative | RoutineScheduled | 107-04-0154 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
04/29/2023 |  | RoutineScheduled | 067-STS-39729 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | NONE |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | Verified discharge meter readings. Battery backup for control panel was dead, and did not reset. Electrician is scheduled to replace and re-wire. Meters -A - 940, B -670, C - 910 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | 07:03 PM
01/27/2023 |  | RoutineScheduled | 099-STS-87264 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Auxiliary Filter"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
05/24/2023 |  |  | 033-17-0027-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/22/2023 | Alternative | Routine/Scheduled | 810-STS-3966 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/22/2023 | Dec 30 1899 11:58AM
11/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Pad | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | NA | [7 empty] | 11/14/2023 | Sample Chamber | 62.000000 | [5 empty] | Attached to this report |  | Septic Tank-12"sludge 6"scum/ Microfast ATU-20"sludge/ Pump Tank-2"sludge/ Septic-Microfast ATU Tank requires pump out and spray the media/ Replaced a faulty off float during inspection/ Blower air filter cleaned and blower is working correctly/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-1805 ETM-167h 33m/ Pump2-1754 ETM-163h/ Peak-53/ High level-20/ On-5m 36s Off-11h 54m and Peak off-9h 54m | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
10/27/2023 | Alternative | RoutineScheduled | 031-STS-29652 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 3.000000 | 5500 | Septic Tank | EZ Treat | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Pumped Out | The grease was pumped off the top of the effluent. The pump tank was also pumped. The effluent filter was pulled and cleaned. The recirculating and discharge pumps were all pulled and cleaned. The EZ Treat pods were both cleaned. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/09/2023 | 01:00 PM
05/31/2023 | Alternative |  | 121-STS-13581 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000 | LPD |  | Pump | Pressure | Trenches | Not Applicable |  | [] | ["Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | NA | [16 empty] | Inspected | - pump chamber is completely full - pump is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/15/2023 | 12:00 AM
04/26/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
09/29/2023 | Alternative | RoutineScheduled | 001-STS-91474 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 500 | Aqua Safe |  | Pump | Pressure | Mound | UV | 600.000000 | [] | [] | YES | [17 empty] | Sludge judge test revealed 1-2 inches of accumulation on the bottom of the septic tank. No pumping was needed. System and components are all workings as designed. UV Light is working. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 08:50 AM
07/25/2023 | Alternative | RoutineScheduled | 19-120-0161A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1750 | 1000 | 750 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Pungent | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/25/2023 | 12:00 AM
10/09/2023 | Alternative | RoutineScheduled | 05-142-0296 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/29/2023 | Alternative | RoutineScheduled Component Maintenance | 047-STS-24438 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection/ repair. Atu riser and riser base were leaking, removed both to reseal base and replaced riser with new one. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 07:39 AM
03/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/12/2023 | Alternative | Reportable Incident Component Maintenance | 175-03-0234 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced vents on mound. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
08/15/2023 | Alternative | RoutineScheduled | 027-STS-17670 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 4 - Blue Crystal tablets installed 14 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/15/2023 | 12:00 AM
01/13/2023 |  | Routine/Scheduled | 550-STS-6407 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/13/2023 | Jan 1 1900 1:25PM
01/17/2023 |  | RoutineScheduled | 177-STS-89593 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
02/08/2023 |  | Routine/Scheduled | S 800-13-0187 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream. Changed the filter in the aerator. Need to install an inlet tee in the septic tank (1 - tee and 1 - 4" coupling). The timer is set to 1.25 minutes every 3 hours. Installed 2 - 6" x 24" risers, 1 - flat ring, and 1 - lid. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/08/2023 | Jan 1 1900 1:30PM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance | 113-STS-25897 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
10/12/2023 | Alternative | RoutineScheduled | 06-197-021 | Wise | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | Aerator down. Left loaner aerator. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/12/2023 | 12:00 AM
11/16/2023 | Alternative | RoutineScheduled | 107-03-0044 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | 12:00 AM
02/20/2023 |  | RoutineScheduled | 175-14-0303 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | UV | 500.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation","Recirculation Pump"] | ["Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation","Recirculation Pump"] | NO | Musty | Clear | 7.200000 |  |  |  |  | 02/21/2023 | Sample Chamber | 3.000000 |  |  | 2.700000 | [5 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
07/12/2023 | Alternative | Follow-Up Component Maintenance | SP-05-120 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank and pump tank pumped out by others. Degraded peat was removed by hand and new peat was installed. Peat was purchased from Driller Services. Degraded peat was disposed at Spotsylvania Refuse. Resealed septic tank inlet riser and removed roots as best as possible. Installed septic tank outlet riser. Sealed pump tank wedge lid. Resealed pump tank outlet riser. Sealed downhill mid-seam in pump tank. Added A300 filter. Added root kill to all pods and drilled out drain holes. Checked laterals in each pod for blockages; repaired as needed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
12/05/2023 | Alternative | RoutineScheduled | 16-184-5001 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.500000 | 6.000000 |  | -1.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
12/12/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | UV |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | 7.600000 | 17.100000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/18/2023 | Dec 30 1899 8:36AM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/26/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Sand |  |  | Pressure | Trenches | Not Applicable |  | [] | [] | [18 empty] | slow drainage through sand filter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
10/09/2023 | Alternative | RoutineScheduled | 154-14-0156 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Norweco 960 |  | Gravity | Gravity | Trenches | Not Applicable | 150.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/10/2023 | 11:50 AM
08/29/2023 | Alternative | RoutineScheduled Component Maintenance | 033-14-0084-SR | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
01/04/2023 |  |  | 2015-143-0073 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Norweco | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out | Clean spin filter 11/11/22 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/27/2023 | 12:00 AM
06/30/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | Dec 30 1899 11:10AM
05/01/2023 | Alternative | Routine/Scheduled | 800-13-0098 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | Dec 30 1899 12:05PM
01/20/2023 |  | Reportable Incident | -STS-7110 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | COSS - Maintenance - GMP2018-02 Replaced distribution box with new 8 port concrete DBox. Spliced to existing conveyance line Spliced to existing header lines. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/23/2023 | Jan 1 1900 7:45AM
06/19/2023 |  | RoutineScheduled | 182-06-0471 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 1.000000 |  | FAST 0.5 |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation"] | NA | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Homeowner had tree company plant shallow saplings on the property. Tree company had planted some saplings on the end of the lines. They do not appear to be causing an issue at this time. The homeowner is contacting the tree company to move them off the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
12/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/11/2023 | Alternative | Follow-Up Component Maintenance | 175-06-0543 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired air relief valves. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
06/22/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-0"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Pureflo Peat turned and in good condition at this time/ Controls, pumps, floats and alarms functioning properly/ Counts Pump1-11247 ETM-125h 39m/ Pump2-11117 ETM-124h 38m/ Peak-71/ High-24/ No breakout or spongy areas on the pad area and dosing correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/10/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
01/27/2023 |  | RoutineScheduled |  | Page | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Air vac and valve box repaired Added solution to media | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
05/17/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | J&G Septic Service |  | James | Kleindl | 2.000000 | 3000 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Effluent Screens"] | YES | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/17/2023 | Dec 30 1899 5:00AM
01/12/2023 |  | RoutineScheduled | SWP-05-499 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | On site for annual inspection. Alarm light initially did not light when alarm float was lifted. Eventually traced the problem to a corroded hot wire connection to the back of the light assembly. Stripped hot wire and made new connection, light working. Neutral wire screw too badly corroded. In fact, there is a fair amount of corrosion throughout the control panel. Cycle counter, ETM, and contactor have already been replaced. If any more electrical problems, complete panel should be replaced and a better job done sealing up the conduit. Mounting post is rotten and needs replaced. Fourth and fifth pods (from the street) had a lot of standing water. Attempted to get them draining. Will need to return next week to remove enough peat to flush out the 1" drain ports at the bottom of the pods. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
09/14/2023 | Alternative | RoutineScheduled | 150-17-0090 | King William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 1.000000 | 1500 | Clearstream ATU |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | None | Clear | [14 empty] | Pumped Out | Clearstream trash compartment, treatment unit pumped due to accumulated solids, treatment unit refilled with fresh water. Rebuild Clearstream aerator, replaced broken trash compartment riser and lid. Removed and serviced pump. Clearstream pump, floats, controls, aerator functioning properly after service. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/15/2023 | 10:55 AM
12/13/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Advantex | Pump | Pressure | Drip | Not Applicable |  | [] | ["Control Operation","Distribution Pump Operation","Recirculation Pump","SludgeScum Accumulation","Level Sensor Operation"] | YES | [17 empty] | 0 scum, very little sludge, flushed filters, Alarms, floats, pumps working. Checked all 3 zones. pressure good, field dry. Very little use, d-324,38H13m R-53974, 721h,59m | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | 11:00 AM
06/30/2023 | Alternative | Routine/Scheduled | 159-04-300 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating - bulging noted. Biofilter - peatmoss on one side saturated - module has multiple fractures - owner attempting to limp through until public sewer available. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | 08:30 AM
11/01/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | EZ Treat Sandfilter |  | Pump |  |  |  |  | ["Control Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | ["Control Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | N/A | [17 empty] | Replaced pump in recirculation tank | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/01/2023 | Dec 30 1899 10:00AM
04/11/2023 |  | Routine/Scheduled | 04-120-0333A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/11/2023 | Jan 1 1900 11:37AM
08/23/2023 | Alternative | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Orenco Advantex | [6 empty] | SludgeScum Accumulation | SludgeScum Accumulation | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/13/2023 | 01:15 PM
12/01/2023 | Alternative |  | 17-100-0422 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/15/2024 | 12:00 AM
11/16/2023 | Alternative | RoutineScheduled Component Maintenance | 175-17-0082 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 10:33 AM
02/22/2023 |  | RoutineScheduled | 179-STS-88001 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Inlet riser on pump tank is damaged and lid (tuff tite). Customer wants price for replacement. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
08/09/2023 | Alternative | RoutineScheduled | 181-97-0336 (LEGACY ALT. SYSTEM) | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | Sand Filter | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The controls were operating as designed. The sand filter was inspected and in good operating condition. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | 01:25 PM
11/30/2023 | Alternative | RoutineScheduled | 061-19-165 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Microfast |  | Gravity | Gravity | Trenches | UV | 600.000000 | ["BlowerCompressorAerator Operation","Disinfection","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","SludgeScum Accumulation"] | NA | Septic | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/01/2023 | 02:00 PM
01/02/2023 |  |  | 00-197-A3 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/02/2023 |  | 4.190000 |  |  | 1.300000 |  |  | Will be sent separately |  | BOD: 4.19 TSS: 1.30 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/02/2023 | 12:00 AM
09/07/2023 | Alternative | RoutineScheduled Component Maintenance | 047-17-268 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Recirculation Pump" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Auxiliary Filter" ,"Attached Growth Medium"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the clarifying tank due to scum and sludge accumulation in the tank. It may be advisable to pump the septic tank at the same time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
05/12/2023 | Alternative | Reportable Incident | 093-15-0096 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to a smell in the house and the grey box humming. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The septic tank needs to be pumped, the pump tank needs to be pumped out (a lot of sludge), and pump the trash out of the Clearstream when doing so. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/12/2023 | Dec 30 1899 8:30AM
01/09/2023 |  | Follow-Up | 175-13-0167 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced ATU float | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
02/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Aerator control panel was replaced and the system appears to be functioning as designed at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
04/14/2023 |  |  | 2006-143-0095 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Ecoflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
01/31/2023 |  |  | 770-STS-42780 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 |  | Microfast |  | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | NA | Septic | Black | [14 empty] | Inspected | - recommend 1500gal Microfast tank be pumped/cleaned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2023 | 12:00 AM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend keeping vehicles away from drainfield area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/20/2023 |  | Routine/Scheduled | 03-163-0185 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump and effluent screen serviced. Treatment Module - media drapes & spray grid serviced. PUmp Tank - float sensors, pump and controls operating. DBox - at grade - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2023 | Jan 1 1900 8:45AM
05/24/2023 |  |  | 127-STS-31994 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 12:00 AM
12/20/2023 | Alternative | Routine/Scheduled | 07-160-0233 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 10:30 AM
01/09/2023 |  | Routine/Scheduled | 196-09-163 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 1500 | Advanced Septic |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 20.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 05:45 PM
02/01/2023 |  | RoutineScheduled | 179-10-0113-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend pumping the septic tank & Advantex RT tank at your next service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
08/28/2023 | Alternative | Follow-Up | 175-13-0332 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Service to replace faulty Blower only: Replaced Ecopod E-60 Blower ( R2103 Gast) Tested and working properly at this time. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
11/07/2023 | Alternative | RoutineScheduled | 05-113-194 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 8 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/07/2023 | 12:00 AM
03/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/19/2023 | Alternative | RoutineScheduled | 175-14-0303 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | UV | 500.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/21/2023 | 12:00 AM
06/16/2023 | Alternative | Routine/Scheduled | 05-142-0368 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes and spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | Dec 30 1899 9:00AM
02/01/2023 |  | RoutineScheduled | 179-STS-90108 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Initial inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
03/30/2023 |  | Routine/Scheduled | 2009-143-0134 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Microfast |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles"] | YES | [16 empty] | Inspected |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/30/2023 | 11:04 AM
02/13/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced control panel housing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
10/20/2023 | Alternative | RoutineScheduled | 015-STS-337717 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FASTY |  |  | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:00 AM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-87614 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
07/26/2023 | Alternative | RoutineScheduled | 18-100-0295 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 250 | Septic Tank | PuraFlo | Gravity | Pressure | Pad | UV | 300.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/18/2023 | 12:15 PM
04/26/2023 |  | Routine/Scheduled | {FIPSCode}-STS-4360 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | Jan 1 1900 8:25AM
11/09/2023 | Alternative | RoutineScheduled Component Maintenance | 179-17-0431-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
08/24/2023 | Alternative | RoutineScheduled Component Maintenance | 2002-93-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | Chlorination |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | 7.300000 | 14.200000 |  | 0.000000 | [9 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 09/15/2023 | 02:41 PM
05/25/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["None"] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/25/2023 | 12:00 AM
12/14/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | Dec 30 1899 1:35PM
03/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was off at time of inspection. It was turned on and appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/19/2023 |  | Routine/Scheduled | 2014-143-0140 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. The grade on the pipe in the Clearstream is not okay - needs to be addressed and/or fixed. Changed the diffuser in the Clearstream and changed the filter in the aerator. The septic tank needs additional risers on it to be properly inspected in the future. The timer is set to 4 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/19/2023 | 10:00 AM
04/27/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Lower line was cameraed and there were no signs of an issue. DSS adjusted dial flows and releveled the box. The field appears to be evenly distributed. Advise homeowner to monitor and notify if there are any changes | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/24/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Musty | Dark Brown | [5 empty] | 01/24/2023 |  | 58.000000 |  | 1600.000000 |  |  |  | Will be sent separately | Inspected | Blower line need repairing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/13/2023 | Jan 1 1900 8:47AM
06/12/2023 | Alternative | RoutineScheduled | 10-120-0231AR | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Other"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Other"] | [18 empty] | Installed new bacterial Catalyst in system. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
01/26/2023 |  | Routine/Scheduled | S 800-13-0190 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | Jan 1 1900 2:15PM
10/24/2023 | Alternative | RoutineScheduled | SD-05-435 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1250 | Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | None | Clear |  | 7.600000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 08:35 AM
10/04/2023 | Alternative |  | 14-100-0361 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/23/2023 | Alternative | RoutineScheduled | 2007-143-0033 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/01/2023 | Alternative | Routine/Scheduled | 234-16-118 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/01/2023 | Dec 30 1899 8:00AM
03/22/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection"] | ["BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | Jan 1 1900 7:20PM
03/09/2023 |  | RoutineScheduled | 175-01-0977 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
05/01/2023 | Alternative | Routine/Scheduled | 093-12-0053 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | Replaced aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | Dec 30 1899 11:25AM
02/16/2023 |  | RoutineScheduled | 087-STS-6448 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Carrington Pump & Irrigation | 1942001121 | John | Carrington |  |  | Norweco |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Level Sensor Operation","Distribution Pump Operation","Effluent Screens","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/16/2023 | 12:00 AM
10/11/2023 | Alternative | RoutineScheduled Component Maintenance | 154-08-0192 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | 175-17-0388 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["SludgeScum Accumulation"] |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | 12:58 PM
05/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
03/08/2023 | Alternative | Routine/Scheduled | AWES-9DELKV | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Multiflo FTB |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/08/2023 | Dec 30 1899 1:14PM
03/29/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-10"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-006129 ETM-0012863/ Pump2-006068 ETM-001272 On-1m 22s Off-2h Pumps 54.6gpm/ Puraflo Peat turned in all 8 modules and is in good condition/ Recommend cutting bush back away from the last Puraflo Module for better access and service. No breakout or spongy areas at the drainfield site and dosing correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/28/2023 | Alternative | RoutineScheduled | SD-12-315 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Distribution Pump Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Distribution Pump Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Septic tank needs pumped out, owners to make arrangements with local pumper. Gasket has separated from the septic inlet lid making it difficult to secure the lid correctly - recommend replace. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
03/28/2023 |  | RoutineScheduled | 101-06-0369 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Old Dominion Engineering | 1942001085 | Michael | Craun | [9 empty] | ["None"] | ["None"] |  | None | Clear | 3.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/07/2023 | 11:00 AM
08/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Alleghany-Roanoke | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 | 1500 | ATL |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["Dispersal System Operation","SludgeScum Accumulation"] | NA | Septic | [6 empty] | 08/15/2023 | Sample Tap | [6 empty] | Will be sent separately | Inspected | Montgomery County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | 12:00 AM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
11/27/2023 | Alternative | RoutineScheduled | 166-12-191 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 2.000000 | 1500/1000 | Clearstream |  | Gravity | Pressure | Drip | UV |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/01/2023 | 12:00 AM
07/21/2023 | Alternative | RoutineScheduled Component Maintenance | 175-17-0195 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
04/28/2023 |  | Initial Visit | VAG408228 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 2.000000 |  | Constructed Wetlands |  | Pump | Gravity | Discharge | Chlorination |  | ["Disinfection"] | ["Control Operation","Disinfection","Distribution Pump Operation"] |  | None | [17 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/07/2023 | 10:30 AM
10/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | 12:00 AM
11/28/2023 | Alternative | Reportable Incident | 810-STS-3854 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Owner called due to an alarm. On arrival the whole system was flooded. Spinfilter screen was stopped up and Clearstream filter was stopped up. The tank from the cottage is on demand dose - should be on a timer. (Cottage is occupied). Meet with the pumping company and pumped and cleaned the Clearstream tank and pump tank. Replaced the spinfilter screen. Cut the UV off and UV alarm and disconnected the pressure switch on the aerator due to the pumping of tanks. The septic tank needs a better filter due to having two homes on the system. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/28/2023 | Dec 30 1899 12:00PM
01/09/2023 |  | RoutineScheduled | 099-07-0210-ST | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation" ,"Effluent Screens"] | ["Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Outstanding proposal for replacing junction box. 1 pureflow module was ponding, augered and it drained pretty good. Will check next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 09:31 AM
07/31/2023 | Alternative | Reportable Incident | 151-07-0001 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | ["Control Operation","Distribution Pump Operation"] | ["Control Operation","Distribution Pump Operation","Level Sensor Operation"] | [18 empty] | Pump tank riser, conduit and control panel post damaged over the weekend by "lawn care" operations. Replaced control panel, new wiring, replaced float sensors, and replaced damaged riser access. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/01/2023 | 06:30 AM
11/02/2023 | Alternative | Routine/Scheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Orenco Advantex |  | Pump | Pressure | Drip |  | 300.000000 | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/08/2023 | 09:26 AM
04/18/2023 |  |  | 11-142-0183 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | 12:00 AM
03/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | UV |  | ["SludgeScum Accumulation","Dispersal System Operation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [17 empty] | Zone 1 solenoid is bad needs replaced. Clean out cap and plug needs replaced broken. Septic and atu need pumped and pressure washed a lot of solids on top of microfast unit | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/10/2023 | Dec 30 1899 9:40AM
12/15/2023 | Alternative | Routine/Scheduled | 136-08-0215 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component Normal Level 5" of sludge and 1" of solids Root intrusion inside of septic tank. Pulled and cleaned fitler Discharge/Pump Tank Condition of above Component Notes for above Component Normal Level Pump and floats are functioning properly however they are Aged Peat Moss Condition of above Component Notes for above Component Tipping bucket and dispersal trays are intact and functioning properly Minor ponding but Peat moss in great condition and raked put good Control Panel Condition of above Component Notes for above Component 120v into panel All audible and visual alarms are functioning properly however the audible alarm is unplugged Pump pulled 7amps Panel is Aged Distribution Box Condition of above Component Notes for above Component Plastic distribution boxlocated in front yard near tree and driveway at grade in good condition with 5 lines balanced and taking water All seals intact No visible cracks Drain Field Condition of above Component Notes for above Component No signs of surfacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 10:12 AM
11/11/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 1.000000 | 1000 | Puraflo (Anua) |  | Pump | Gravity | Trenches | Not Applicable | 100.000000 | ["Attached Growth Medium","Control Operation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | Fluffed and evened peat moss. installed a new Junction box and floats. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/22/2023 | 11:45 AM
04/26/2023 |  | Routine/Scheduled |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced - effluent screen is aged and showing extreme wear - recommend replacing. Pump basin - plastic - bulging present - fractured - recommend replacing. - float sensors, pump and controls operating. Biofilter - Fiberglass - deformity to shell noted. Mild fractures present - 12" standing water in the inspection port! - peatmoss raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/27/2023 | 06:30 AM
05/11/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
07/05/2023 | Alternative | Routine/Scheduled | 18-160-0166 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | 01:45 PM
01/30/2023 |  | RoutineScheduled | 175-15-0247 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank to Ecopod ATU | EZ-Treat Recirculation Tank to Pump Tank | Pump | Gravity | Discharge | UV |  | ["Disinfection","BlowerCompressorAerator Operation"] | ["Disinfection","BlowerCompressorAerator Operation"] | [18 empty] | Septic Tank-2"sludge 0"scum/ Ecopod-0"sludge 0"scum/ EZ-Treat Tank Recirculation Tank-2"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ On-3m 4s Off-29m/ No pump out needed at this time/ Blower air filter cleaned and blower functioning properly/ EZ-Treat Pump intake cleaned and spraying properly/ EZ-Treat Media in good condition/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump-006668 ETM-0032639. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/17/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-90141 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | ["Recirculation Pump" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NO | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
03/31/2023 | Alternative | RoutineScheduled | SD-10-247 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [8 empty] | 21248.000000 | [] | [] | [8 empty] | 03/15/2023 | Sample Tap | 2.000000 |  |  | 2.200000 | 13.640000 |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | 12:00 AM
11/03/2023 | Alternative | RoutineScheduled Component Maintenance | 061-18-166 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | YES | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. installed sim-tech filter. raked media. RECIRC HL-30. DISCHARGE: HL-18, PEAK-27. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
09/20/2023 | Alternative | RoutineScheduled Component Maintenance | 179-15-0190-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Roots inside d-box coming from line number 7, pulled roots out and added ROOT-X. Check next year and apply Root-x if nesesary. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
06/30/2023 | Alternative | Reportable Incident Component Maintenance | 179-18-0379-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to failed enable float in discharge tank. Replaced float, cleaned biotube filter and disc filter. Homeowner will get records and we will inspect the system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
05/15/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Drip |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Septic system, 1-2" Scum and 16-20" sludge in old Septic tank, Recirc znoe 7-8" sludge trace and discharge zone 7-10" sludge trace. Alarm Test Good - Floats test Good- low float on recirc maybe need to keep an eye, dimly lit when lifted may send a false signal. Maybe water in jbox. New wirenut did not fix the issue. - Recirc Pump time & count 591.4 Hours 43820 Cycles - Discharge pump time 104.6 hours 636 cycles. trended 368 days in history- 1 Alarms in history for1-5-2023 on advantex- same for alerts, Confirmed factory reccomended setting. Cleaned effluent filter in septic asystem is connected to montiroing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
07/05/2023 | Alternative | Routine/Scheduled | 07-135-3068 | Giles | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | 04:15 PM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/11/2023 | Alternative | Routine/Scheduled | 228-05-0229 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | UV |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | Replaced UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | Dec 30 1899 7:20AM
04/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance | SD-14-021 | Orange | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Effluent Screens"] | ["Effluent Screens" ,"Auxiliary Filter" ,"Attached Growth Medium"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | The peat in the Puraflo modules is no longer providing treatment. Before deciding whether to replace the peat or consider a different treatment system, we need to re-evaluate the dispersal area in drier weather. The dispersal area was very wet, but that may be due to recent rains. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 08/01/2023 | 06:26 AM
12/27/2023 | Alternative | RoutineScheduled | 06-183-254 | Russell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/27/2023 | 12:00 AM
02/28/2023 |  | Routine/Scheduled | 07-120-0773A | Colonial Heights | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. Dbox intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/01/2023 | Jan 1 1900 10:00AM
04/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/21/2023 | Alternative | RoutineScheduled Component Maintenance | 061-16-250 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Drip tank was barely in low level again (bottom float touching water, but not "on"). Cycled power off for 3 minutes. Increased standard rest time by 35 minutes in hopes of accumulating more water between cycles. Will reach out to panel manufacturer if low level alarms continue. In the past 6 days, the system pumped an average of 975.8 gals/day at 344.4 gals/cycle (avg.) for a total of 5,855 gallons. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
03/15/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
11/20/2023 | Alternative | Follow-Up Component Maintenance | 061-15-394 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Homeowner dug wrong spot, so we dug it up. DSI removed roots best as possible from tank and resealed top on end of tank. Replaced R.O. float. Installed proper float tree and adjusted floats to proper elevations. Re-plumbed airline properly. Moved air filter to inside blower box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
12/06/2023 | Alternative | RoutineScheduled | 133 06 0435 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Western Virginia Water Authority | 1942001145 | Michael | Doss |  |  |  |  | Gravity | Pressure | Drip | UV |  | [] | [] | NA | None | Clear | [5 empty] | 12/06/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/06/2024 | 11:45 AM
12/13/2023 | Alternative | Routine/Scheduled | 151-12-0158 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Customer Chesapeake Property Management Property Address 5563 Mary Ball Road, Lancaster, VA 22503 USA Technician Logan White Date Serviced 2023-12-13 Was customer present for service? Yes Type of System Alternative Type of AOSS System Clearstream to drip Septic Tank Condition of above Component Notes for above Component Normal level 2 in of sludge less than 1 in of solids Riser showing signs of leaking Discharge/Pump Tank Condition of above Component Notes for above Component Normal level Less than 1 in of suspended solids Tested floats and pump all working as should Cleaned spin filter All plumbing intact and pump moving water properly No signs of infiltration Aeration Condition of above Component Notes for above Component Normal level Less than 1 in of suspended solids Pulled and cleaned weir Pulled and cleaned diffuser Float is functional Riser showing signs of leaking Air Pump/Blower Condition of above Component Notes for above Component 120 volts coming Pulled and cleaned filter Air pressure sensor intact and functional Air pump currently turned off due to level in tank to low because of pumping last week Has met it's life expectancy Control Panel Condition of above Component Notes for above Component 120 volts coming in All visual and audible alarms functional Discharge pump pulled 7.2 amps All components working as should however panel has met its life expectancy Drip Field Condition of above Component Notes for above Component No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | 11:28 AM
03/15/2023 |  | Routine/Scheduled | {FIPSCode}-STS-5149 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | Jan 1 1900 3:00PM
11/14/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | Dec 30 1899 9:55AM
05/12/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-132 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
01/16/2023 |  | Routine/Scheduled | 550-STS-6733 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 |  |  |  | 01/24/2023 |  | 40.000000 |  | 6900.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 10:15AM
06/15/2023 | Alternative | Reportable Incident Component Maintenance | SWP-01-501 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in high level alarm due to failed timer float. Replaced timer float. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
09/21/2023 | Alternative | Routine/Scheduled | 128-04-183 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal level 1in of sludge and solids Pulled and cleaned filter No signs of infiltration -Discharge/Pump Tank: Normal level Pulled and tested all floats functioning properly Plumbing intact Pump properly moving water No signs of infiltration -Peat Moss: Tipping bucket and dispersal trays intact Examined and raked peat moss in good condition | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/06/2023 | 03:20 PM
05/19/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/22/2023 | 11:15 AM
02/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
03/22/2023 | Alternative | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [17 empty] | Service call only: Replaced faulty Jet UV-Light bulb, sleeve and cord. Light now functioning properly. Pump counts-9382 ETM-921h 58m/ Peak-31 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
08/09/2023 | Alternative | RoutineScheduled Component Maintenance | 177-18-0231-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
11/17/2023 | Alternative | RoutineScheduled Component Maintenance | 099-07-0123-SWT | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The peat has settled below the piping in all five modules. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
07/10/2023 | Alternative | Routine/Scheduled | 157-03-044 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Basin - minor bulging present - float sensors, pump & controls operating. Biofilter - Peatmoss in good condition - raked /turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | 07:00 AM
09/25/2023 | Alternative | Routine/Scheduled | 166-13-148 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm call 9/25/23: -Phyllis took me into the master bath when I arrived and could smell the sewer smell they were talking about. I smelt the sink, vent, math tub and toilet. The only thing they smelt off was around the base of the toilet, everything else was fine. The system was in Alarm and discharge was in high level. Found risers to be leaking and it had rained heavily over the weekend putting the system in high level. I pumped the tank out of alarm. Informed Phyllis that we will be out Thursday when it is supposed to rain to see if the risers are actively leaking and to replace the wax ring in the master bath - Will have a follow up visit on Oct 16th | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/11/2023 | 10:43 AM
09/27/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/27/2023 | Dec 30 1899 10:55AM
05/23/2023 | Alternative | Routine/Scheduled | 136-03-0334 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Aeration tank - normal level - mixing present - compressor serviced. Pump tank - float sensors, pump and controls operating. DBox - deep install - not serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 09:00 AM
12/11/2023 | Alternative | RoutineScheduled | S-12-111-0081 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 2.000000 | 4500 | SEPTIC TANK ONLY | ECOPOD | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | THE SYSTEM DID NOT NEED TO BE PUMPED. THE BLOWER FILTER WAS PULLED AND CLEANED. THE CONTROLS WERE OPERATING AS DESIGNED. THERE WERE NO VISIBLE LEAKS IN THE LEECH FIELD. THE LIDS WERE SECURED. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | Dec 30 1899 12:55PM
06/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/12/2023 | 01:13 PM
07/05/2023 | Alternative | RoutineScheduled Component Maintenance | 113-STS-25897 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
06/28/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/28/2023 | Dec 30 1899 9:10AM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/17/2023 |  | RoutineScheduled | 177-06-0348-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump" ,"SludgeScum Accumulation"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Pungent | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the Advantex Tank due to sludge accumulation int he tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
06/06/2023 |  | RoutineScheduled | 153-STS-19052 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
02/20/2023 |  | RoutineScheduled | 179-16-0311-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
04/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air filter was cleaned. The pump tank needs pumped out. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
08/07/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Septic pumped out 08/11/2023 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | 12:00 AM
11/07/2023 | Alternative | Initial Visit | 165-STS-339630 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 RT |  |  | Pressure | Drip | Not Applicable |  | [] | [] | [18 empty] | Start up. Homeowner does not have address number at this time | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/07/2023 | 12:00 AM
10/30/2023 | Alternative | RoutineScheduled | 175-15-0438 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-6"sludge 0"scum/ Microfast ATU Tank-10"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-34625 ETM-3763 hrs/ High level-22/ Hand-25/ Override-30/ On-6m 2s Off-1h 53m/ Watermeter-0,237,020/ Cleaned the hydraulic unit spin filter/ No breakout or spongy areas on the Delta Geoflow Drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/01/2023 |  | Routine/Scheduled | 228-04-1100 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 2.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | Jan 1 1900 9:00AM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/30/2023 |  |  | 07-113-071 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/30/2023 | [7 empty] | Will be sent separately |  | BOD: BDL TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | 12:00 AM
10/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Please do not flush hygiene products | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Aerator motor broke PVC fittings inside the blower housing. ATU was not receiving aeration. Homeowner has contacted someone for repair. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/04/2023 | 06:02 AM
02/15/2023 |  | RoutineScheduled | 175-06-0075 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Auxiliary Filter"] | ["Effluent Screens" ,"Recirculation Pump" ,"Auxiliary Filter"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
11/11/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20 |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 14" of accumulated solids in septic tank. 2" of solids in discharge pump tank. Cleaned recirculation pump solids basket filter. Flushed treatment unit spray manifold. Sprayed solids off of the treatment unit "sheets". Tested floats, pumps and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 07:03 PM
01/18/2023 |  | RoutineScheduled |  | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Level Sensor Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | replaced bottom float and top float and new float tree | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
10/06/2023 | Alternative | Pump-Out Only | 06-160-0367 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner |  |  | WHITEWATER | [6 empty] | [] | [] | [17 empty] | Pumped Out | Pumping & Cleaning Whitewater Pretreatment Tank (1000 gallons) JOB SCOPE: Pumped/cleaned septic tank; everything appears to be functioning at this time. This can in no way be construed as a guarantee that septic system will continue to function in the future. REFER TO ANY REPORTS MADE BY ADVANCED ENVIRONMENTAL FOR MORE INFORMATION. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | 12:00 AM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping Microfast | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/12/2023 | Alternative | Routine/Scheduled | 17-142-0438 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Annual Maintenance: -Septic Tank: Water level high upon arrival due to a clogged effluent screen. Flushed and cleaned effluent screen and water level returned to normal. Not due for pump out. -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Recirculation at Rest Voltage: 126.7 Recirculation Amperage: 10.5 -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Discharge at Rest Voltage: 126.0 Discharge Amperage: 11.3 -Media Sheets: Cleaned media sheets. Confirmed spray pattern is good - Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Control Voltage: 126.1 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | Dec 30 1899 2:13PM
12/19/2023 | Alternative |  | 101-17-0060 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Tara / Lars | Harrington / Tiffany | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/13/2023 | Alternative | RoutineScheduled | 13-197-103 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [8 empty] | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 4 - Blue Crystal tablets installed 8 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/13/2023 | 12:00 AM
12/18/2023 | Alternative | RoutineScheduled Component Maintenance | 182-01-0378 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 12/18/2023 |  | 2.000000 | [5 empty] | Will be sent separately | Inspected | maybe toilet leak high level replace spin filter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
04/12/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The sheets are badly bridged will need to be cleaned. The advantex lid is broken and will need replaced. Also needs new hinges. The pump tank electric box lid is broken and ground water can get in. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
11/02/2023 | Alternative | RoutineScheduled Component Maintenance | 177-07-0255-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | The alarm buzzer has a low-pitched constant alarm. The peat in the Puraflo modules is nearing the end of its useful life. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
05/22/2023 | Alternative | RoutineScheduled | 171-15-0211 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | [17 empty] | Inspected | Sludge level-1+" scum layer on top-12+" sludge on bottom in Septic tank - Recirc zone of tank 12+" sludge, Discharge zone of tank 6-8" sludge. All 6 float swtiches test operational- Sprayed off Media sheets- Clear Effluent on top, Cleaned Effluent filter. Recirculation pump operational - good spray pattern-Alarm operational. RTU134250 - System has active online 24hr monitoring- alarm 8-2-22 and 1-1-23. recirc pump run time 1316.6 hours and 21,989 cycles, discharge pump run time 146.5 hours and 3971 cycles, 2118 days trended | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
05/12/2023 | Alternative | RoutineScheduled | C-13-111-0110 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Delta Environmental DF60 |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Routine Inspection visit- Septic tank - No Access available to tank- Sludge levels- owner said system pumped 2 years ago by "Sinks Septic" Whitewater Treatment tank has bad white scum smells and looks anoxic. Reccomend to pump both tanks asap. sludge level 24-30 inches, needs pumping. Do not use antibiotic soaps, cleaner and most buckets. , | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | Jan 1 1900 9:30AM
01/03/2023 | Alternative | RoutineScheduled | SD-06-308 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Needs UV Bulb. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 11:08 AM
01/06/2023 |  | Routine/Scheduled | 800-07-0078 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/06/2023 | Jan 1 1900 12:02PM
02/20/2023 | Alternative | RoutineScheduled | 047-STS-21307 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Water quality was a little cloudy, gave customer copy of Do's and don'ts. Blower 1.19 amps. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Clearstream | none | Pump | Gravity |  | UV |  |  |  | NA | Musty | Clear | 6.900000 | 12.900000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 11/15/2023 | Dec 30 1899 2:02PM
05/08/2023 |  | RoutineScheduled | 177-17-0206-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
09/19/2023 | Alternative | RoutineScheduled Component Maintenance | 177-06-0385-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Multiflo FTB | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The alarm light in the control panel is not working. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
06/01/2023 | Alternative |  | 09-192-239 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 06/01/2023 |  | 2.780000 |  |  | 1.500000 |  |  | Will be sent separately |  | BOD: 2.78 TSS: 1.50 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/01/2023 | 12:00 AM
02/09/2023 |  | RoutineScheduled | 153-STS-20266 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Prince William | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 1.000000 | 1000 |  |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation","Other"] | ["Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation","Dispersal System Operation"] | NA | [16 empty] | Pumped Out | Sale inspection of a conventional gravity septic system. The septic tank inlet lid was dug up it was about 13" under the ground. The effluent was at working level. The T's are pvc. The tank was pumped out and inspected for any cracks or leaks and none were seen. The top 12" of the concrete tank has a lot of stone showing. It didn't appear to be leaking. And it was not soft when poked with the probe. The sewer line was camera snaked and found a belly under the retaining wall. Their is standing water there. The conveyance line was camera snaked and found to have a belly about 3 feet before the d-box with standing water. The 14 port concrete d-box was dug up it was 8" under the ground. The d-box is in bad condition and no levelers. All 10 corragated header lines were camera snaked and found line #5 crushed 10 feet out and line #10 6 feet out was unable to get camera threw the roots. Line #1 and #2 have some standing water in the lines. It appears that those two lines were getting most of the effluent. The rest of the drain field lines were dry. At this time the septic system is not in working condition. The belly in the sewer line and conveyance line need fixed. The d-box needs replaced with speed levelers. And line 5 and 10 need issues resolved. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 02/11/2023 | 01:50 PM
09/18/2023 | Alternative | RoutineScheduled | C-13-111-0051 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [7 empty] | 09/18/2023 | Sample Chamber | 3.800000 |  |  | 3.100000 |  |  | Attached to this report |  | The system did not need to be pumped. The blower filter was pulled and cleaned. The controls were operating as designed. The BOD and TSS were within the permitted limits. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | Dec 30 1899 4:40PM
03/22/2023 |  |  | 085-STS-32335 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Norweco | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [18 empty] | Recommend pumping the septic tank in the next few months | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
02/03/2023 | Alternative | RoutineScheduled | 151-05-509 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/07/2023 | 12:00 AM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
05/06/2023 | Alternative | Follow-Up | SD-12-174 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001236 | Stuart | Lynn | 2.000000 | 8000 | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Attached Growth Medium"] | ["Dispersal System Operation"] | NA | Sulphitic | Cloudy | 7.100000 | 4.500000 | [11 empty] | Will be sent separately | Inspected | 4900 6213 Dumfries Rd Commercial Commercial mrlynn - Makenzie Lynn - 5/2/2023 5:21:46 PM - check operations and plant levels test drip zones, switched off 5 & 6 scritchfield 4900 6213 Dumfries Rd Commercial Pump as Directed - 4/28/2023 3:51:26 PM - Pump as directed per mrlynn fperez 4/28/2023 4,000 from septic tank 1 4900 6213 Dumfries Rd Commercial Pump as Directed scarder - Shayne Carder - May 04, 4000 gallons pumped final pump chamber 4900 6213 Dumfries Rd Backhoe Backhoe mcox - Michael Cox - 5/9/2023 7:12:48 AM - Backhoe with Operator to assist with soil work with M&M soils 5/9/2023 Glenn McLenney & Curtis Moore on site evaluating reserve areas. SML onsite to mark property corners jblanco 5/10 & 11 VDH on site for level II review /2023 remove brush and limbs complete mowing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | 12:05 PM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
05/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Trash tank level was high due to filter being clogged. Cleaned filter and level returned to normal. Recommend pumping. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
02/07/2023 | Alternative | Reportable Incident | 073-STS-101890 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 300.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | COSS - Maintenance - GMP2018-02 - VDH HDID 136-22-0350 Pumped existing septic tank empty - crushed and removed. Installed new 1000 gallon concrete mid seam septic tank in same location. Installed access risers to grade. Installed new sewer line and inlet baffle. Installed new conveyance line and outlet baffle. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/09/2023 | 06:45 AM
05/18/2023 |  | Follow-Up | 153-STS-20393 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Recirculation Pump"] | ["Recirculation Pump"] | [18 empty] | Service call only: High water alarm, found the EZ-Treat Recirculation Pump STEP-30 was faulty and requires replacement. Returned on 5/19/2023 and replaced the pump, tested and working correctly. Counts: Pump-0000126 ETM-0000607 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
12/08/2023 | Alternative | Routine/Scheduled | 800-STS-14137 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 1 minute every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/08/2023 | Dec 30 1899 3:30PM
04/20/2023 |  | RoutineScheduled | 08-113-080 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 2 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/20/2023 | 12:00 AM
03/23/2023 |  |  | 087-STS-6278 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 1.000000 | 1250 | 1250 |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens"] | YES | Musty | Clear | 7.000000 |  | 6.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/23/2023 | 10:45 AM
04/20/2023 |  | Follow-Up | 179-08-0194-SWT | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | Puraflo | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Re-plumbed piping from Puraflo pods to distribution box with proper fall. Added root kill. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
11/11/2023 | Alternative | RoutineScheduled | 2126-09-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Ouraflo |  | Pump | Gravity | Discharge | UV | 250.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | 7.700000 |  |  |  |  | 11/13/2023 | Sample Chamber | 2.000000 |  |  | 26.800000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/01/2023 | 12:00 AM
09/09/2023 | Alternative | RoutineScheduled | 175-05-0983 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1942001489 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 500.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/11/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | DeHaven's Backhoe Service Inc. | 1942001541 | Wayne | Edmonson | 1.000000 | 1500 | Advantex |  | Pump | Pressure | Drip | Not Applicable | 225.000000 | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 10:00 PM
07/26/2023 | Alternative | RoutineScheduled | 00-120-0424A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Onsite Septic Service | 1942001039 | Corey | Braxton | 7.000000 |  | Puraflo |  | Gravity | Gravity | Pad |  |  | [] | ["Control Operation","Attached Growth Medium","Distribution Pump Operation","Level Sensor Operation"] |  | Musty | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
06/23/2023 | Alternative | RoutineScheduled | 075-STS-34568 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | All In Septic Services | 1942001442 | Dennis | Mitchell | 3.000000 | 3000 | Fuji |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Effluent Screens","Other"] | YES | Musty | Clear | [14 empty] | Inspected | Sludge/Scum Accumulation - Septic 6", ATU 0", Pump Station 0" Fuji System Flushed per Factory Spec Distance between "off" and "on" float moved from 3" to 6", 15 low water alarms since put in use (1yr) | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | Dec 30 1899 10:00AM
04/12/2023 |  | RoutineScheduled | 175-02-0631 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 04:23 AM
01/06/2023 | Alternative | Reportable Incident | 157-16-0027 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Dispersal System Operation","Distribution Pump Operation"] | ["Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Repaired damaged / fractured forcemain. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/09/2023 | 09:30 AM
12/04/2023 | Alternative | RoutineScheduled Component Maintenance | {FIPSCode}-STS-13220 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Gravity | Gravity |  | UV |  | ["Disinfection" ,"BlowerCompressorAerator Operation"] | ["Disinfection" ,"BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | 8.100000 | 18.200000 | [11 empty] | Will be sent separately | Inspected | No Discharge Sign | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 12/18/2023 | 08:36 AM
08/11/2023 | Alternative | RoutineScheduled | 08-113-005 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/11/2023 | 12:00 AM
04/20/2023 | Alternative | RoutineScheduled | 115-08-0094 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 2000 | Septic Tank | EcoPod | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | NA | [16 empty] | Inspected | Called due to an alarm- found the Fbreaker had tripped for the system and blower and pump not working. After trouble shooting found the blower was locked up and back end blown off with Dark marks around the base, About the same time a bad lightning storm came through and owner says its related. We disconnected the blower and got the pump to work normally until we returned and replaced the blower motor, System is not working properly with new blower, We also replumbed the header supply line as old line cracked.Septic tank 20 inch sludge, treatment tank 12 inch sludge and pump tank has 12 inches sludge. May consider to have septic pumped out next year . If smells become and issue may want to pump both septic and treatment tank to restart flora incase cleaners and chemical and antibiotic soaps kills the good bacteria. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
10/16/2023 | Alternative | RoutineScheduled | 13-142-0041 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:00 AM
01/05/2023 |  | RoutineScheduled | 196-07-035 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | Installed new regenerative blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
05/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
02/08/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | A new septic system was installed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance | 182-10-0075 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
05/15/2023 | Alternative | Initial Visit | 073-STS-96272 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 152.000000 | [7 empty] | Owner called due to a smell coming out of the septic. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Looks to be paint in the tanks - needs to be pumped out and cleaned. Inlet tee on the Clearstream was backgrading and the H20 in the Clearstream and pump tank were milky. The timer is set to 3 minutes 28 seconds on and 2 hours off. Took BOD sample. NOTE : BOD sample was high - system should function properly after service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | 12:00 PM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/18/2023 |  | Routine/Scheduled | 2013-143-0131 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/18/2023 | 11:01 AM
02/21/2023 |  | RoutineScheduled | 2002-93-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | Chlorination |  |  |  | NA | Musty | Clear | 8.100000 | 7.900000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 03/13/2023 | 11:23 AM
04/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/20/2023 | Dec 30 1899 5:20PM
05/09/2023 | Alternative | Routine/Scheduled | 19-126-049 | Dinwiddie | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/09/2023 | Dec 30 1899 3:57PM
01/05/2023 |  | RoutineScheduled | 175-18-0404 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Gravity | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 02:21 PM
08/03/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-90250 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | NA | Musty | Dark Brown | [13 empty] | Will be sent separately | Inspected | Routine inspection. Media has filamentus bacteria but is not clogged up, water clear but has a tea color. Customer said his wife took antibiotics not long ago. Gave him a copy of Do's and don'ts. Blower 3.09 amps. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/23/2023 | Alternative | Routine/Scheduled |  | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 2000 | Clearstream | Clearstream | Pump | Gravity | Trenches | Not Applicable | 2000.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level Secondary septic tank - normal level - effluent screen serviced. Flow Equal Tank - float sensors, pump and controls operating. Aeration tank (2) - normal level - mixing present - compressors serviced. Pump Tank - float sensors, pump and controls operating. LPD Field - walkover - no surfacing noted. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | 09:30 AM
01/23/2023 |  | Routine/Scheduled | {FIPSCode}-STS-3405 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2023 | Jan 1 1900 2:35PM
07/31/2023 | Alternative | RoutineScheduled Component Maintenance | 179-12-0113-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["Effluent Screens" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
03/30/2023 | Alternative | Follow-Up | SD-06-77 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank pumped out by others prior to peat replacement. Degraded peat was removed by hand (shovels/pitch forks) and new peat was installed. Peat was purchased from Wrights Ready Mix. Degraded peat was disposed at Spotsylvania Refuse. Replaced Ecoflo lid with used lid. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
07/14/2023 | Alternative | RoutineScheduled Component Maintenance | 099-17-0056 SPSA | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend replacing two EZ Set riser lids on the Septic Tank and digging by hand to remove roots that have grown into the distribution box lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
01/05/2023 |  | Routine/Scheduled | 228-18-0020 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/05/2023 | Jan 1 1900 1:05PM
04/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/15/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-93201 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
08/10/2023 | Alternative | Initial Visit | 800-STS-14678 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 5.000000 |  | 9.000000 | [5 empty] | Owner called due to a red light on. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. The Clearstream tank needs to be pumped out. The timer is set to 2.3 minutes every 3 hours. Took initial BOD and Fecal samples. The inlet tee from the house on the left was stopped up - full of grease. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | Dec 30 1899 10:30AM
11/30/2023 | Alternative |  | 18-100-0472 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 12:00 AM
04/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/11/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
04/14/2023 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesapeake | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 2000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Primary septic tank - normal level Secondary septic tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | Jan 1 1900 10:30AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance | 175-04-0499 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
07/25/2023 | Alternative | RoutineScheduled Component Maintenance | 177-09-0102-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Semi-Annual Inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
05/12/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Puraflo |  |  |  | Trenches |  |  | ["Attached Growth Medium","Septic Tank Baffles","Level Sensor Operation"] | ["Attached Growth Medium","Septic Tank Baffles","Level Sensor Operation"] | [18 empty] | replaced float | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/12/2023 | 12:00 AM
05/12/2023 | Alternative | RoutineScheduled | 132-06-0329 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
02/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Pad | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 02/14/2023 | Sample Chamber | 19.000000 | [5 empty] | Attached to this report |  | Septic tank-10"sludge 8"scum/ .75 Microfast ATU-16"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ Septic-Microfast Tank requires pump out due to sludge levels/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms functioning correctly/ Counts: Pump1-768 ETM-95h 36m/ Pump2-765 ETM-94h 52m/ On-7m 37s Off-11h 52m/ Peak-11/ High-11/ No breakout or spongy areas on the LPD Pad area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["Disinfection","BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | [17 empty] | Septic Tank-14"sludge 8"scum/ Microfast-18"sludge/ Pump Tank-2"sludge/ Pump out required on the Septic Microfast Tank due to sludge levels/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ UV-Light bulb and sleeve were replaced and functioning properly at this time/ Counts: Pump-2440 ETM-519h 52m/ Peak cnts-13 ETM-0h 41m/ High cnts-22/ Watermeter-166,279.71/ No breakout or spongy areas on the drip field and dosing properly | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
01/23/2023 |  | Routine/Scheduled | 07-163-0175 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Delta Environmental Products, DF Series |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - normal level - no riser access. Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - plastic - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 9:00AM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/07/2023 | Alternative | Pump-Out Only Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank Pumped | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 2.000000 | [8 empty] | [] | [] | NA | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/08/2023 | 12:00 AM
04/25/2023 |  | Pump-Out Only |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Cajun Aire ATU |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Pumped out primary septic tank and processing tank - hosed down and serviced. Refilled with fresh water for system restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | 01:00 PM
08/05/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-11126 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination | 500.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation","Recirculation Pump"] | NA | Musty | Clear | 7.200000 |  |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
02/28/2023 |  | RoutineScheduled | C102-06-0086 | Alleghany | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | Septic Tank only | AdvantexAX20 | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The recirculating pump was pulled and sprayed off. The textile sheets were sprayed off. The laterals were rodded and cleaned. The controls were operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | Jan 1 1900 9:20AM
03/28/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower connection was repaired. System should return to normal operation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/19/2023 | Alternative | RoutineScheduled | 08-142-0269 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 |  | EcoFlo |  | Pump | Pressure | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | 12:00 AM
04/03/2023 |  | RoutineScheduled | 04-120-0470A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 3250 | 1000 | 1000 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens","Recirculation Pump"] | YES | None | Clear | 8.000000 |  | 6.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | Jan 1 1900 11:30AM
03/15/2023 | Alternative | Routine/Scheduled | 05-163-0040 | New Kent | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1250 | Ecoflo |  | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | Effluent filter cleaned. Pad is failing. Need a site and soil study performed to determine a repair. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/15/2023 | Dec 30 1899 2:59PM
06/21/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | ["None"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | 12:00 AM
03/20/2023 |  | RoutineScheduled | 132-08-0159 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 500.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 12:00 AM
06/23/2023 | Alternative | RoutineScheduled | 181-16-0052 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | MicroFast | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NO | [17 empty] | The system did not need to be pumped. The effluent filter, blower filter, and spin filter were all pulled and cleaned. The treatment unit was operating as designed. The controls were operating as designed. The drip field had return effluent coming back to the pump tank, so the drip field was operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | 08:35 PM
02/15/2023 |  | RoutineScheduled | 2018-143-0158 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Norweco Singulair |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","Control Operation","Auxiliary Filter","BlowerCompressorAerator Operation","Effluent Screens","Dispersal System Operation","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/15/2023 | 12:00 AM
08/09/2023 | Alternative | RoutineScheduled | 06-113-249 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/09/2023 | 12:00 AM
05/25/2023 | Alternative | Reportable Incident | 093-06-0223 | Southampton | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/25/2023 | Dec 30 1899 9:30AM
11/14/2023 | Alternative | RoutineScheduled Component Maintenance | 099-09-0037-SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
05/16/2023 |  | Follow-Up | 124-STS-2379 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Hooked up the pressure switch on the aerator and hooked up the UV. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/16/2023 | Jan 1 1900 12:00PM
10/06/2023 | Alternative | Follow-Up Component Maintenance | SWP-01-271 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced distribution with above grade ?monster? distribution box and deleted sample box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
11/03/2023 | Alternative | Routine/Scheduled | 07-142-0330 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Outlet tee appears to be intact. Not due for pump out. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly -Aeration: Water level normal. Noted root infiltration along top seam of aeration tank. -Air Pump/Blower: Checked and confirmed aerator is functioning properly. Flushed and cleaned aerator air intake filter -Control Panel: Checked and confirmed components within control panels are functioning properly. Checked and confirmed audible alarms are functioning properly. Checked and confirmed visual alarms are functioning properly. -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact. -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | Dec 30 1899 8:57AM
07/21/2023 | Alternative | RoutineScheduled | 175-05-0148 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["SludgeScum Accumulation","Level Sensor Operation","Septic Tank Baffles","Effluent Screens","Distribution Pump Operation","Dispersal System Operation","Control Operation","Attached Growth Medium"] | YES | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/28/2023 | 10:45 AM
12/27/2023 | Alternative | RoutineScheduled | 107-16-0235 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
05/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/16/2023 | Alternative |  | 132-03-0157 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Roger/Deirdre | Anderson/Curran | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/18/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | [5 empty] | 04/18/2023 |  | 15.000000 |  | 220.000000 |  |  |  | Will be sent separately | Inspected | Repaired UV cord & replaced bulb while on site. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | Jan 1 1900 12:48PM
05/02/2023 |  | Routine/Scheduled | 17-120-0496A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/02/2023 | Jan 1 1900 11:37AM
02/21/2023 |  | RoutineScheduled | 179-STS-90297 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We were unable to inspect the control panel because it was locked. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
09/07/2023 | Alternative | Routine/Scheduled | 196-06-144 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | 06:45 PM
06/14/2023 | Alternative | Reportable Incident | 093-11-0089 | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/15/2023 | Dec 30 1899 11:00AM
02/01/2023 | Alternative | Reportable Incident | 166-10-075 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | High water alarm. Replaced clogged spin filter screens. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
08/07/2023 | Alternative | Initial Visit |  | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Aqua Klear |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Visit Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - concrete - intact - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | Dec 30 1899 7:00AM
10/12/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Microfast |  | Pump | Pressure | Drip |  | 150.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 11:23 AM
01/09/2023 |  | Reportable Incident | 03-163-0261 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Distribution Pump Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Discharge pump failure - pumped discharge tank empty - pumped processing tank/aeration tank empty and serviced aspirator while on property. Replaced discharge pump and plumbing - refilled processing tank with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | Jan 1 1900 11:30AM
04/24/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Three Rivers | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | NA | [7 empty] | 04/24/2023 | Sample Chamber | 11.000000 | [5 empty] | Attached to this report |  | Septic Tank-4"sludge 3"scum/ Microfast-2"sludge / Pump Tank-0"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Faulty off float replaced during inspection/ Controls, pumps, floats and alarms now functioning properly/ Counts: Pump1-175 ETM-10h 41m/ Pump2-171 ETM-9h 58m/ No breakout or spongy areas on the drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
08/15/2023 | Alternative | Initial Visit | 101-STS-92795 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Virginia Septic Solutions LLC | 1942001500 | Justin | Barker | 1.000000 | 1000 | Clearstream 600n |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["Disinfection","BlowerCompressorAerator Operation"] | NA | None | Clear | [15 empty] | Replaced aerator and uv lamp. Did not locate drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 12:00 AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/31/2023 |  | RoutineScheduled | 179-15-0201-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Blower 2.74 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
10/19/2023 | Alternative | Routine/Scheduled | C-11-111-0042 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/19/2023 | Dec 30 1899 2:00PM
10/27/2023 | Alternative | RoutineScheduled | 085-STS-35899 | Hanover | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chickahominy | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2000 | Puraflow 3 Pods |  | Pump | Gravity | Mound | Not Applicable |  | ["Attached Growth Medium"] | ["Auxiliary Filter","Level Sensor Operation"] | NA | Musty | Clear | [14 empty] | Inspected | Effluent Filter Cleaned Sludge/Scum Accumulation - Septic 6", Pump Station <2" Faulty float controls in pump station, float not turning pump off until timer de activates Peat Media is Heavily Saturated with Ponding - Effluent Pouring out of the Lids | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/27/2023 | Dec 30 1899 2:00PM
09/11/2023 | Alternative | RoutineScheduled | 06-125-086 | Dickenson | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Dispersal System Operation","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | Installed loaner aerator. Aerator Exchanged | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/11/2023 | 12:00 AM
05/04/2023 |  | RoutineScheduled | 145-02-0106 | Highland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | Peat Moss | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The trays and tipping tray were both pulled and cleaned. The peat moss was raked. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/03/2023 | 11:55 AM
07/12/2023 | Alternative | Routine/Scheduled | 02-163-0437 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. LPP - no indications of surfacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/13/2023 | Dec 30 1899 7:00AM
04/04/2023 |  | RoutineScheduled | 185-STS-17544 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/04/2023 | 12:00 AM
04/06/2023 | Alternative | RoutineScheduled | 023-STS-42917 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Western Virginia Water Authority | 1942001145 | Michael | Doss |  |  |  |  | Gravity | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | NA | None | Clear | [5 empty] | 04/06/2023 | Pump Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/11/2023 | Jan 1 1900 12:45PM
11/13/2023 | Alternative | RoutineScheduled Component Maintenance | 165-STS-333279 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
06/26/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-63831 | Westmoreland | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Elite Onsite | 1942001726 | Drew | Saunders | 2.000000 | 1500 | 1000 | 500 | Pump | Gravity | Pad | Not Applicable | 350.000000 | ["Attached Growth Medium","Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/30/2023 | 02:00 PM
10/13/2023 | Alternative | Routine/Scheduled | 166-18-177 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal level 12 in of sludge less than 1 in of solids Pulled and cleaned rsv Disassembled and sprayed rsv until water ran clear May need pump and refill next year -Recirculation Tank: Normal level 4 in of suspended solids Tested floats and pump all working as should Pulled brushed and sprayed biotube filter Pulled and cleaned pump Filter housing intact filter properly working Plumbing intact pump properly moving water No signs of infiltration -Discharge/Pump Tank: Normal level Less than 1 in of suspended solids Tested floats and pump all working as should Pulled and cleaned pump Splice box and plumbing are intact Pump properly moving water No signs of infiltration -Media Sheets: Brushed and flushed laterals until water ran clear Sprayed media sheets Sheet chamber intact no cracks or deterioration -Control Panel: 120 voltage coming in All visual and audible alarms functioning properly Recirc pump pulled 12.10 amps Discharge pump pulled 12 Amps Panel is intact all components properly working -Drain Field Headworx box: Pulled and cleaned spin filter till daylight was visible Drainfield showing no signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/27/2023 | 03:46 PM
05/31/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/23/2023 | Alternative | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Repaired manifold in EZ Treat due to being frozen. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/02/2023 | Dec 30 1899 11:08AM
05/16/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Septic zone 1-2"in Scum & 16" Sludge, recirculation zone 12 in., Clear Effluent on top, discharge basin 10" in fine sludge, media tank was blinded with slime and roots and full to top overflowing when we ran in test mode. Eventually we cleared the blockage, it appears to flow again, we see roots are growing into the tank lid and likely fitting causing slow flow. Also the effluent may have a die off of the good bacteria due to cleaning chemicals and antibiotic soap and/or cleaners. It smells dead, is Slime coted and needs and extra cleaning on a return trip and likely should be a pump out, to restart bacteria and reduce using any soaps or chemicals which kill bacteria Ran system in test mode, Alarm opperational, All Floats opperational. Adjust the run time numbers to handle the flow for when high use. Recirc pump run time 247.9 hours and 48,171 cycles, Discharge pump run time 92 hous asnd 1697 cycles 634 days trended. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance | SP-05-102 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 2.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
06/21/2023 | Alternative | RoutineScheduled | VAG401889 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Multiflo |  |  |  | Discharge | Chlorination |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | [18 empty] | No discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/21/2023 | 12:00 AM
11/17/2023 | Alternative |  | 047-19-068 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 12:00 AM
03/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping Microfast due to recent back up. There appears to be broken tubing underground. Lower zone appears to show signs of surfacing effluent. homeowner has contacted someone for repair. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
08/29/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-1490 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/29/2023 | Dec 30 1899 11:50AM
04/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/19/2023 | Alternative | Routine/Scheduled | 087-STS-6682 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Annua Maintenance: -Septic Tank: Water level normal. Flushed and cleaned effluent screen. Not due for pump out. -Discharge/Pump Tank: Water level. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. Noted signs of potential groundwater infiltration around base of riser -Peat Moss Coconut husk: Coconut husk is in good condition -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Drain Field: Found no signs of surfacing around dispersal area | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 01:24 PM
09/06/2023 | Alternative | Routine/Scheduled | 07-160-0129 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | 04:00 PM
10/19/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0334-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Roots in 1 pod, removed. Small crack on D-box, sealed with ADH200. 6 trees marked to be removed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
01/09/2023 |  | RoutineScheduled | 099-STS-90063 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment is crystal clear. Alot of toilet paper is starting to build up in septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 09:31 AM
04/04/2023 |  | RoutineScheduled | 175-14-0482 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
05/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | atu needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
10/17/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None |  | 7.600000 |  |  |  |  | 10/17/2023 |  | 2.000000 |  |  | 1.000000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/07/2023 | 02:30 PM
06/22/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | NA | [7 empty] | 06/22/2023 | Sample Chamber | 13.000000 | [5 empty] | Attached to this report |  | Septic Tank-3"sludge 4"scum/ Microfast-0"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Replaced faulty off float during inspection/ Controls, pumps, floats and alarms now functioning properly/ Counts: Pump1-176 ETM-6h 20m/ Pump2-173 ETM-6h 19m/ Peak-6/ High-9/ No breakout or spongy areas on the drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/28/2023 |  | Routine/Scheduled | 550-STS-5879 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | Replaced aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | Jan 1 1900 12:55PM
06/29/2023 | Alternative | Routine/Scheduled | TELS-ATRSLQ | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/29/2023 | Dec 30 1899 12:40PM
11/03/2023 | Alternative | Routine/Scheduled |  | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/03/2023 | 09:00 AM
05/26/2023 | Alternative | RoutineScheduled | 061-STS-23341 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 | 1500 gallon-Septic W/Fast and 1250 Pump | Septic | MicroFast | Pump | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [17 empty] | 5' Liquid depth with 0 scum and 6-8" of sludge, Fast side clean, media clean. pump tank clean. Alarms working, floats working, pump working. Drainfield is dry. Pump event 129, 6.19 hrs. Very little use. BOD sample failed. Media is clean with 2 people using the system according to MicroFast and other contractors. The system is operational, but the media does not have enough bacteria on it to fully treat the effluent yet. Will re-test at the next inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | 10:00 AM
09/07/2023 | Alternative | Routine/Scheduled | 04-174-0112 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Puraflo |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/07/2023 | Dec 30 1899 12:47PM
05/01/2023 |  | Initial Visit | 182-09-0196 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Gravity | Trenches |  |  | ["Attached Growth Medium","SludgeScum Accumulation","Septic Tank Baffles"] | ["Dispersal System Operation","SludgeScum Accumulation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/16/2023 | 12:00 AM
05/24/2023 | Alternative | Follow-Up | 061-STS-24974 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Attached Growth Medium","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | YES | [7 empty] | 05/24/2023 | Pump Chamber | 7.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | 08:30 AM
08/01/2023 | Alternative | Routine/Scheduled | 800-STS-14327 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 2 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/01/2023 | Dec 30 1899 8:20AM
08/31/2023 | Alternative | RoutineScheduled | 09-100-0396 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | BIO-COIR |  | Pump | Gravity | Mound | Not Applicable | 600.000000 | [] | [] | YES | [17 empty] | SLUDGE JUDGE 4" FROM BOTTOM EVERYTHING WORKING AS IT SHOULD ALARMS WORK NOZZLES CLEANED | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/01/2023 | 12:55 PM
05/17/2023 |  | RoutineScheduled |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Prince William | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 2.000000 | 3000 | Micro-fast | N/a | Pump | Pressure | Drip | Not Applicable | 200.000000 | ["Effluent Screens","Dispersal System Operation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | The entire system is in operation with the health department plans and regs. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 12:00 PM
10/05/2023 | Alternative | RoutineScheduled | 09-184-5004 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 15 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/05/2023 | 12:00 AM
05/25/2023 | Alternative | Routine/Scheduled | 08-160-0240 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable | 68.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/25/2023 | 04:00 PM
02/27/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [8 empty] | 762.000000 | [] | [] | [8 empty] | 02/14/2023 | Sample Tap | 7.000000 |  |  | 7.170000 | 77.600000 |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
03/28/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced contactor in control panel & 3 floats. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
10/19/2023 | Alternative | RoutineScheduled | C11-180-0122 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex AX20RT |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. New homeowner. 14" of accumulated solids in septic tank. Cleaned septic tank solids filter. 10" of solids in recirculation portion of treatment unit. 0" in discharge portion of treatment unit. Replaced passive charcoal vent filter due to slimy biomass in treatment unit. This will improve passive oxygen transfer to biomass and improve treatment quality. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 12:00 AM
03/14/2023 | Alternative | RoutineScheduled | SD-04-13 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | Annual inspection. Peat is believed to be original and about 17 years old. Peat is compacted and ponding in places. Recommend replacement to ensure proper treatment. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
05/11/2023 | Alternative | Routine/Scheduled | 157-98- | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. BioFilter - 4 modules - Peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/25/2023 | 11:00 AM
06/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 4.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Audible alarm for DF pump was not functioning. It was replaced at time of inspection. 3 Spray heads on the EZ treat unit were clogged. Lines were flushed and nozzles were replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/21/2023 | Alternative | Reportable Incident | 119-STS-101922 | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | COSS - Repair Install - VDH HDID 159-23-0010 - GMP2018-02 Pumped existing septic tank empty - abandoned in place - filled with flowable fill material. Installed new 1000 gallon concrete septic tank in area indicated. Replaced sewer line with new 4" PVC Replaced Conveyance line with new 4" PVC Installed 8 port concrete distribution box. Installed 4 absorption laterals as permitted. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/22/2023 | 10:30 AM
08/17/2023 | Alternative | RoutineScheduled |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco | Norweco | Gravity | Pressure | Mound | UV | 450.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/18/2023 | 12:00 AM
02/23/2023 |  | RoutineScheduled | 177-06-0360-SR | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | Musty | Clear |  | 7.230000 |  |  |  | 02/23/2023 | Sample Chamber | 15.000000 |  | 1.000000 | 3.200000 |  |  | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
07/14/2023 | Alternative | RoutineScheduled Component Maintenance | SP-03-40 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
09/22/2023 | Alternative | RoutineScheduled Component Maintenance | VAG408261 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Chlorination |  | ["Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed OEM Blower panel | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
03/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
04/26/2023 |  | RoutineScheduled | SWP-04-88 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Media starting to show its age, probably 2 more years. Evaluate next visit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
03/07/2023 |  | RoutineScheduled | 10-197-057 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 3 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/07/2023 | 12:00 AM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/19/2023 | Alternative | RoutineScheduled | 16-100-0101 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 2.000000 | 500 | AQUA SAFE |  | Pump |  | Mound | UV | 900.000000 | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | NA | [16 empty] | Pumped Out | SLUDGE JUDGE OF SEPTIC TANK REVEALED 4-5" FROM THE BOTTOM AND 8-9" FROM THE TOP-PUMPED SEPTIC EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 12:00 AM
12/09/2023 | Alternative | Initial Visit | 031-STS-26608 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Septic Tank | Norweco Singulair Green | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | Initial/Annual inspection. Septic tank is 3/4 full. No water in aeration portion or clarifier/discharge portion. No water in discharge pump chamber. Aerator is operational and running. Inspected system for proper installation. All aspects seem to be operating as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 07:03 PM
01/09/2023 |  | Reportable Incident | -STS-92146 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system blower alarm going off due to a tripped breaker at the panel. Reset breaker and blower started up again. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
10/23/2023 | Alternative | Routine/Scheduled | 041-STS-258000 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Changed the diffuser in the Clearstream and changed the filter in the aerator. The Clearstream tank needs to be pumped as well as the septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/23/2023 | Dec 30 1899 11:30AM
12/06/2023 | Alternative | Pump-Out Only | 175-03-0022 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 | 500 | 1000 |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [16 empty] | Pumped Out | st/atu tank pumped out | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/08/2023 | 01:00 PM
12/19/2023 | Alternative |  | 101-13-0422 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Shirley | Rennick | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/28/2023 | Alternative |  | 181-07-0146 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The blower filter was cleaned. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/09/2023 | 12:00 PM
01/30/2023 |  |  | 175-04-0477 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | McKim Septic & Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | ["Other"] | [8 empty] | 01/30/2023 | Sample Tap | 58.000000 |  |  | 164.000000 |  |  | Will be sent separately |  |  | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/28/2023 | 03:50 PM
12/21/2023 | Alternative | RoutineScheduled | 175-15-0409 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-4"sludge 3"scum/ Microfast ATU-4"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-1198 ETM-115h 24m / On-5m 51s Off- 11h 54m/ High cnts-16/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/16/2023 | Alternative | Reportable Incident | 154-09-0232 | Louisa | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 1750 | Aquasafe |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | Musty | Cloudy | [14 empty] | Pumped Out | Septic and Treatment Tank Pumped Aerator Rebuilt | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/16/2023 | 09:30 AM
09/25/2023 | Alternative | RoutineScheduled | 159-16-023 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/23/2023 | Alternative | RoutineScheduled | 147-STS-22700 | Prince Edward | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Septic | Purasys | Pump | Gravity | Pad | Not Applicable | 350.000000 | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | NA | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/23/2023 | Dec 30 1899 3:30PM
07/25/2023 | Alternative | RoutineScheduled Component Maintenance | 182-18-0280 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
01/05/2023 |  |  | 023-STS-42917 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Western Virginia Water Authority | 1942001145 | Michael | Doss | [9 empty] | ["None"] | ["None"] | NA | None | Clear | [5 empty] | 01/05/2023 | Pump Chamber | [6 empty] | Attached to this report |  | I am still adding bugs to the system to get the treatment needed, I have to add micro bugs to the system on Fridays to carry it over the weekend when it is not being feed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2023 | Jan 1 1900 8:30AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/22/2023 | Alternative |  | 154-06-0742 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Michael & Dona | Breen | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/03/2023 |  | RoutineScheduled | 177-STS-90247 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | 12:00 AM
10/04/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/04/2023 | Dec 30 1899 11:10AM
10/18/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | 12:00 AM
04/21/2023 |  | Routine/Scheduled |  | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Primary septic tank - normal level - Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - replaced float sensors, pump and controls operating. Drip - serviced headworks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/24/2023 | 09:00 AM
11/07/2023 | Alternative | RoutineScheduled Component Maintenance | 179-14-0008-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Septic | Cloudy | [5 empty] | 11/07/2023 |  | 61.000000 |  | 1600.000000 |  |  |  | Will be sent separately | Inspected | Routine inspection. Replaced UV bulb. System been in alarm for few weeks due to dead blower, replaced blower. Took samples which are most likely going to fail but since blower and UV bulb were replaced system should go back to normal in few days. Supply 25psi. Return 30psi. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 182-05-0289 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
04/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | An inspection of a conventional pump septic system. The state requires that the septic tank be pumped out every 5 years and filed with the state and county. The septic control panel is an interior Waterguard demand dose. The septic tank inlet lid was dug up it was 12" under the ground. Tank was at working level. Both inlet and outlet T's are pvc. Tank was pumped out and a visual inspection of the tank was done. The sewer line was camera snaked and was clear. The Pump tank, pump, floats, force main, risers and electric box were inspected. The 6-port concrete d-box was dug up it was 12" under the ground. All 4 header lines were camera snaked and were clear. The drain field was probed and dry. There are small trees on the end of the drain field area that we would recommend removing so to avoid an issue later with root intrusion At time of inspection the septic system was in working condition. This inspection does not guarantee the life of the septic components. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/09/2023 | Alternative | Routine/Scheduled | 157-04-281 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Primary septic tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - plastic - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 12:30 PM
03/27/2023 |  | RoutineScheduled | 06-184-5001 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/27/2023 | 12:00 AM
12/12/2023 | Alternative | RoutineScheduled |  | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters, checked sludge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Effluent filter was clogged and caused the level to be high. Inlet side had a significant amount of grease. Recommend pumping | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/10/2023 |  | RoutineScheduled | {FIPSCode}-STS-75726 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
04/25/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Multiflo |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Septic Tank 2-4" scum and 20" sludge, Treatment tank 2" scum on deck and 6-12" sludge, pump tabk had 10-12" fine sludge-May Want to Pump system this year. Good aeration on multiflow, alarm good, cleaned drip filterm found pump had lost presuure to the Pressure Bell and was reading zero, Pulled out cleaned removed water and reset, Now reading 0.6 after pumping down. pump good alarm good, silence good. May want to pump septic tank and deck of scum layer on multiflo same time- | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
03/30/2023 |  | RoutineScheduled | 07-197-A2 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Effluent Screens","Control Operation","Auxiliary Filter","Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection"] | YES | Musty | Clear | [15 empty] | 4 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/30/2023 | 12:00 AM
09/06/2023 | Alternative | Routine/Scheduled | 04-160-0213 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Ecoflo |  | Pump | Pressure | Drip | Not Applicable |  | None | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | 10:00 AM
11/22/2023 | Alternative | RoutineScheduled Component Maintenance | 177-07-0106-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | Roots are growing in at the base of the riser on the septic tank. If you get alarms during periods of heavy rain, this riser should be excavated and resealed. There are thick roots in the Puraflo modules. This may make it difficult to service the peat in the future. There also appears to be shrubs and trees on the drainfield that should be removed. The walkway may be on the drainfield as well. We are sending you copy of the as-built drawing for your system to help locate shrubs and trees on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
02/03/2023 |  | RoutineScheduled | 2015-143-0147 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Elite Onsite | 1942001726 | Drew | Saunders | 2.000000 | 2000 | 1000 | 1000 | Pump | Pressure |  | Not Applicable | 450.000000 | ["None"] | ["None"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | 07:00 PM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/20/2023 | Alternative | Pump-Out Only | 136-15-0010 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [16 empty] | Pumped Out | Pump Out: The recirc tank has 16" of sludge. Pumping of 1500gal. Refill of 1500gal. * pumped and cleaned system * refilled with clean water | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/06/2023 | 01:09 PM
10/02/2023 | Alternative | RoutineScheduled | 159-05-114 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | sludge checked, cleaned filter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/27/2023 |  | RoutineScheduled | 16-184-5001 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation","BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/27/2023 | 12:00 AM
05/15/2023 | Alternative | RoutineScheduled | 115-05-0351 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Septic Tank | Ecoflo | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | YES | Musty | [15 empty] | Inspected | Sludge level-under1" Scum & 10" Sludge in Septic tank. Water level 1 ft low in septic tank- home has little water useage. Pump Chamber -sludge. Effluent screen was clean and dry above water level. Alarm functional and pump is operational, Peat was moist and the tipping tray dry. System has not had much useage, No ponding in peat moss. Pump tank union leaking @ quick slip lock union in pump tank due to age, best to repair when and if the pumps fails. Owner should fine a company to seal the mid seam septic tank water level appears at midseam. system is operational | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
07/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | EcoVirginia LLC | 1942001235 | William | Poindexter | 3.000000 |  | Septic | Delta ATU | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | 12:00 AM
12/06/2023 | Alternative | RoutineScheduled | 87-67 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure |  | Not Applicable | 600.000000 | ["None"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 12:00 AM
07/26/2023 | Alternative | Reportable Incident | C800-14-0073 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | Control Operation | Control Operation | N/A | [17 empty] | Replaced timer | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/26/2023 | Dec 30 1899 4:00PM
09/20/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation"] | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Replaced blue float while on site. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/16/2023 | Dec 30 1899 12:58PM
03/23/2023 |  | RoutineScheduled | 154-05-0991 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Randy's Complete Water & Wastewater Services | 1942001335 | Randy | Gray | 1.000000 | 1000 | Puroflo |  | Pump | Pressure | Discharge | Not Applicable | 100.000000 | ["None"] | ["None"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | 12:00 AM
10/27/2023 | Alternative | RoutineScheduled | 182-00-0596 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["SludgeScum Accumulation","Auxiliary Filter"] | ["Auxiliary Filter","SludgeScum Accumulation"] | [18 empty] | pumping scheduled for septic/FAST | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/27/2023 | 12:00 AM
02/16/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
10/24/2023 | Alternative | RoutineScheduled Component Maintenance | 182-05-0263 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 10/24/2023 |  | 3.000000 | [5 empty] | Will be sent separately | Inspected | All tanks pumped Lab sample normal | This AOSS should now return to normal function after having provided the above state routine maintenance | 11/22/2023 | 09:18 AM
06/20/2023 | Alternative | RoutineScheduled | 2017-143-0196 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Norweco Singulair |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Auxiliary Filter"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 12:00 AM
04/26/2023 |  | RoutineScheduled | 03-192-032c | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/26/2023 | 12:00 AM
09/28/2023 | Alternative | RoutineScheduled | 11-100-0335 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | BIOCOIR |  | Pump | Gravity | Pad | Not Applicable | 600.000000 | [] | [] | YES | [16 empty] | Pumped Out | PUMPED SEPTIC TANK-EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 12:05 PM
07/21/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-5684 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced - recommend pumpout and refill. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact - | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | Dec 30 1899 9:45AM
09/14/2023 | Alternative | RoutineScheduled | 132-07-0049 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/22/2023 | 12:00 AM
10/04/2023 | Alternative | RoutineScheduled | 2017-143-0169 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/26/2023 | Alternative | RoutineScheduled Component Maintenance | 107-06-0802 | Augusta | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Media is pooling and needs replaced Visual alarm needs replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 08/23/2023 | 06:57 AM
05/05/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Septic tank 2-3" scum and 6-10 in sludge Recirc zone of treatment tank was covered in slime growth, and had 4-5 inches of slude. The discharge zone had 5-6" of fine sludge. Cleaned effluent filter in spetic tank. (clogged) Alarm and both pumps are operational. Float switches all test operational. Sprayed off media and cleaned off the slime layer. Medai cleaned up fine. some smell keep all antibiotic soap and chemicals out of the system. recirc pump run time 957 hours and 71,146 cycles and discharge pump run time 170 hours and 1904 cycles with 560 days trended in history. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
01/24/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Level Sensor Operation"] | ["Level Sensor Operation"] | [18 empty] | Alarm Service Call Only: Alarm due to faulty alarm float and was replaced. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
02/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Salem | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Brittany | Conner | 2.000000 | 2500 | Whitewater |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | Septic | Cloudy | [14 empty] | Inspected | - recommend both tanks be pumped and cleaned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | 12:00 AM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump chamber lid should be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/17/2023 | Alternative | Routine/Scheduled | 151-13-0170 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/17/2023 | 06:43 PM
05/24/2023 |  | RoutineScheduled | 175-14-0316 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Removed roots from top d-box that were starting to block flow to one of the lines. Root mass pulled out easily because sch 40 pipe was used (instead of corrugated pipe) for the headers. Advised owner to trim back trees and brush another 5 feet. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
11/22/2023 | Alternative | Reportable Incident | 15-142-0139 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Arrived on site opened advatex rt system and found sheets had build up on top and between sheets. Recirc floats are aged Discharge floats are aged. Made recommendations sent by email 12/08: ******REPAIRS TO BE MADE ONSITE***** -Advantex Treatment Unit Engineered Textile Media Filter Cleaning - includes use of a specialized wanding tool -Installation of 3 Floats -Installation of 3 Floats | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/06/2023 | Dec 30 1899 9:06AM
08/03/2023 | Alternative | RoutineScheduled | 107-02-0800 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Sand |  |  | Gravity | Trenches | Not Applicable |  | ["None"] | [] | [18 empty] | riser on siphon tank busted. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/03/2023 | 12:00 AM
08/25/2023 |  | Initial Visit |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Seals Septic Service | [5 empty] | E-Z Treat | [6 empty] | ["Attached Growth Medium","Septic Tank Baffles","Control Operation","Dispersal System Operation"] | ["Attached Growth Medium","Septic Tank Baffles","Control Operation","Distribution Pump Operation"] | [18 empty] | Cleaned emitters. Adjusted floats. Follow up scheduled for CP work | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/25/2022 | 12:00 AM
12/21/2023 | Alternative | RoutineScheduled Component Maintenance | 061-STS-21237 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Auxiliary Filter" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. High level alarm and peak floats in drip tank stuck on during testing. Splice box in drip tank was nearly full of water. Removing the water got the high level and peak floats working again. Three of the EZ Treat nozzles were completely stopped up. Removing & cleaning the nozzles restored the flow. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 07:39 AM
04/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The system appears to be functioning as designed at this time. The field is slightly overgrown and difficult to tell that is going on. No surfacing effluent was observed. There appears to possibly have been vehicles driven on or near the drainfield. This is strongly discouraged. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/22/2023 |  | Routine/Scheduled | {FIPSCode}-STS-4733 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | Jan 1 1900 2:30PM
02/08/2023 | Alternative |  | 154-13-0155 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Virginia Soils Inc, dba VSI Supply / AG Onsite | 1942001291 | Archie | Arnold | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/15/2023 | 12:00 AM
08/28/2023 | Alternative | RoutineScheduled Component Maintenance | 175-06-0167 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
08/02/2023 | Alternative | RoutineScheduled | 2017-143-0214 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/04/2023 | 12:00 AM
10/16/2023 | Alternative | RoutineScheduled Component Maintenance | 179-13-0285-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
03/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air line had broken. DSS moved the blower and replaced the air line. System appears to be functioning as designed at this time | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
09/06/2023 | Alternative | RoutineScheduled Component Maintenance | 177-11-0121-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Outstanding proposal for pumping out recirc tank. Enabler float for discharge was not making good contact, cut wire and spliced it plus Put in new wire nut. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
10/20/2023 | Alternative | RoutineScheduled | 18-118-0033 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Clearstream |  | Pump | Pressure | Drip |  |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:00 AM
10/17/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | Dec 30 1899 5:30PM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/09/2023 | Alternative | Routine/Scheduled | 88-120-0088AR | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Inspected |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/09/2023 | Dec 30 1899 5:14PM
01/16/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Control Operation"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
01/10/2023 |  | RoutineScheduled | 09-197-A2 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Multiflo |  | Gravity | Gravity | Discharge | UV | 200.000000 | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/10/2023 | 12:00 AM
12/28/2023 | Alternative | RoutineScheduled | VAG408078 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Gravity | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | no discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/09/2024 | 12:00 AM
02/21/2023 |  | Routine/Scheduled | 05-120-0362A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Puraflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/21/2023 | Jan 1 1900 2:05PM
04/10/2023 | Alternative |  | 14-100-0361 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/14/2023 |  | RoutineScheduled | 179-14-0239-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
09/19/2023 | Alternative | RoutineScheduled | 12-177-1097 | Pulaski | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - New River | King's Alternative Septic | 1942001094 | David | King | 2.000000 | 1000 | Eco Pure |  | Pump | Gravity | Trenches | UV |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | Cleaned effluent screens, system is working correctly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/19/2023 | 12:00 AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/14/2023 | Alternative | Routine/Scheduled | 2005-126-066 | Dinwiddie | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Biomicrobics MicroFAST |  | Gravity | Gravity | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [7 empty] | 06/14/2023 | Sample Chamber | 11.000000 |  | 1.000000 | 150.000000 |  |  | Attached to this report |  |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/14/2023 | Dec 30 1899 2:52PM
10/23/2023 | Alternative |  | 13-197-A2 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.500000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
06/26/2023 | Alternative | Follow-Up Component Maintenance | 179-15-0015-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to follow up from yearly inspection. All tanks were in high level due to mother board failure not running the system properly. Got all tanks back to proper levels. Installed new mother board and set all settings on the board. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
08/11/2023 | Alternative | RoutineScheduled | 171-15-0211 | Pittsylvania | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | After testing determined the float swithces were good but the timer dosing feature was not functioning properly i replaced the timer in the control panel, afterwards i still had an issue with proper operation. Called manufacturer and after more troubleshooting determined the system was wired up incorrectly from installation and it worked only at the overide level like a demand dose pump with a narrow pump angle. so cycles a lot but on/off for short intervals and unable to keep up during heavy rains due to infiltration.. We fixed this wiring issue and the unit should now pump properly as a time dosing feature. we may yet bring the timer dosing back to the original setting since it was increased over the poast 2 years due to the issue. .Possibly we still have some infiltration to deal with and reduce.. Owner may may a dry ditch to funnel run off away from the tank area. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/30/2023 | 09:30 AM
06/15/2023 | Alternative | Routine/Scheduled | 17-172-0336A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 2.000000 | [7 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The timer is set to 10 minutes every 2 hours. Took 5 year sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/15/2023 | Dec 30 1899 8:30AM
07/27/2023 | Alternative |  | 195-STS-26571 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/27/2023 |  | 2.650000 |  |  | 7.070000 |  |  | Will be sent separately |  | BOD: 2.65 TSS: 7.07 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | 12:00 AM
01/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
01/20/2023 |  | Routine/Scheduled | 2015-143-0103 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Multiflo ATU |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/20/2023 | 03:57 PM
08/10/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  | Puraflo Trench |  | Pump | Pressure | Discharge | Not Applicable | 600.000000 | ["None"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/26/2023 | 12:00 AM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Uncovered distribution box due to what appeared to be nitrification around the box area. The box and surge box are functioning as designed. Recommend re-parging them to protect from future issues. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/01/2023 | Alternative | RoutineScheduled | SD-85-73 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Cloverleaf Environmental Consulting, Inc | 1942001135 | Robert | Charnley |  |  | Septic Tank |  | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/02/2023 | Alternative | RoutineScheduled | SD-07-53 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1200 | septic | Puraflo | Gravity | Pressure | Trenches |  |  | [] | [] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 07:50 AM