## Batch Export
Visit Date | System Type | Visit Purpose | Application ID | Physical County | Certify Statement | Record Reviewed | Source System Database | Company Name | License Number | First Name | Last Name | Number of Tanks | Tank Capacity | Treatment Unit 1 | Treatment Unit 2 | Conveyance | Distribution | Dispersal | Disinfection | Actual/Estimated Flow (gpd) | Maintenance Needed | Maintenance Provided | Effluent Screen Cleaned | Odor | Turbidity/Color | pH | DO in Aeration Tank (mg/L) | Settleable Solids (%) | TRC After Contact Tank (mg/L) | Other Test | Date Collected | Collection Point | 5-Day Biochemical Oxygen Demand (mg/L) | TRC (ppm) | Fecal Coliform (CFU/100 mL) | Total Suspended Solids (mg/L) | Total Nitrogen (mg/L) | Total Phosphorus (mg/L) | Laboratory Results are | Outcome of Visit | Comments | I hereby certify | Date | Time
12/21/2023 | Alternative | Routine/Scheduled | 199-16-0003 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Trash Tank Condition of above Component Notes for above Component Water level normal. Inlet tee appears to be intact. Outlet tee appears to be intact. Not due for pump out Aeration Condition of above Component Notes for above Component Water level above normal. Flushed and cleaned effluent screen assembly. Not due for pump out. Air Pump/Blower Condition of above Component Notes for above Component Checked and confirmed aerator is functioning properly. Cleaned aerator shaft Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Distribution Box Condition of above Component Notes for above Component Water level normal. Structural integrity of distribution box appears to be intact Drain Field Condition of above Component Notes for above Component Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | Dec 30 1899 8:55AM
04/04/2023 |  | RoutineScheduled | 17-192-155 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 3 Chlorine 11 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/04/2023 | 12:00 AM
04/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/19/2023 | Alternative | Pump-Out Only | 19-160-0036 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/11/2023 | Alternative |  | 132-19-0009 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Tiffany | Good | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/10/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Tank pumped by another company Valve box lid replaced Effluent line clogged - cleaned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
06/14/2023 |  | Initial Visit | 067-STS-39542 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20 RT |  | Gravity | Gravity | Trenches |  |  | ["Control Operation","Recirculation Pump"] | ["Control Operation","Recirculation Pump"] | NA | [17 empty] | Initial startup visit. Verified correct wiring. Set recirculation pump timers and override timers. Set recirculation pump flow rate. Tested floats, pump and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 07:03 PM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance | SD-96-512 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Annual inspection. Both tanks were replaced by another contractor last month. All 4 floats were replaced and a new A300 effluent filter installed. Tanks were moved down the hill so that they now have only 18" of cover. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/29/2023 | Alternative | Routine/Scheduled | 199-05-0033 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Found at normal level, 5in of sludge and less than 1in of solids. Pulled and cleaned filter. -Discharge/Pump Tank: Found at normal level, tested floats and pump. All workimg as they should. Found multiple cracks in bottom of pump chamber. -Peat Moss: Tipping bucket and trays are in working order. Raked out peat on both sides. Some roots and some compaction and ponding. Drain Field: No signs of surfacing in drainfield area. Central support no water. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | Dec 30 1899 3:27PM
03/29/2023 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | 12:05 PM
12/20/2023 | Alternative | Reportable Incident Component Maintenance | SD-07-205 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | High level alarm for both tanks. Spin filter was very dirty and reduced the flow rate to the field. Switched out for clean filter and opened ball valve a bit more so supply gauge was reading between 22 and 24 psi. Recommend adding a pressure gauge on return line in the headworks. This time, the float tree pulled out of its socket in the discharge pump tank. Redundant off float was found to be stuck on and was replaced. Also had to replace the RO resistor. Infiltration in recirc tank contributed to the system getting into alarm and staying in alarm status for a week. Recirc tank should be pumped out for sludge accumulation and to speed up recovery. Concrete lid for pump tank is broken, needs replaced. Will send another repair proposal. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 07:39 AM
06/15/2023 | Alternative | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/03/2023 | 10:30 AM
04/05/2023 |  | RoutineScheduled | 179-11-0009-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation","Effluent Screens"] | ["SludgeScum Accumulation","Effluent Screens","Attached Growth Medium"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/12/2023 | 04:55 PM
07/14/2023 | Alternative | Initial Visit | SD-83-095 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1200 | septic | ISF | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | NA | Musty | Cloudy | [15 empty] | No discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/17/2023 | 07:45 AM
11/09/2023 | Alternative | RoutineScheduled Component Maintenance | 175-05-0628 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 10:33 AM
07/25/2023 | Alternative | Initial Visit | S16-111-0004 | Botetourt | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | Delta Whitewater | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","SludgeScum Accumulation","Auxiliary Filter"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","SludgeScum Accumulation","Auxiliary Filter"] | YES | [17 empty] | The owner had the system pumped before she had called me. The main breaker at the disconnect had failed, causing the system to back up. The spin filter and effluent screen were both cleaned. The blower had failed so I replaced it with a new blower. The controls were operating as designed, after the main breaker was replaced. There were no visible leaks in the leech field. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/28/2023 | Jan 1 1900 1:05PM
08/23/2023 | Alternative | RoutineScheduled | 179-13-0271-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 0-1 0-1 | 0-0 | Pump | Pressure | Drip | UV |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] |  | None | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/23/2023 | 10:00 AM
04/04/2023 |  | Routine/Scheduled | 2007-143-0059 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump and effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/05/2023 | 09:15 AM
01/09/2023 |  |  | 2003-143-0247 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex | [6 empty] | ["Control Operation"] | ["Control Operation"] | [18 empty] | Replaced Advantex control panel and added two floats to the system. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/03/2023 | 12:00 AM
06/13/2023 |  |  | 179-STS-89581 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
07/11/2023 | Alternative | RoutineScheduled | 171-08-0136 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1000 | Puraflow |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Auxiliary Filter","Control Operation","Other"] | ["Auxiliary Filter","Control Operation","Other"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | 01:00 PM
03/20/2023 |  | RoutineScheduled | 175-00-0850 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank to Puraflo Modules | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-4"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Controls, pump, floats and alarms functioning properly/ Puraflo Peat turned in all 4 modules and the peat is in good condition/ Counts: Pump-027390 ETM-0036623/ No breakout or spongy areas on the Pad Area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/15/2023 | Alternative | Routine/Scheduled |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 250.000000 | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | Dec 30 1899 3:00PM
09/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | King William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Three Rivers | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out | Repaired pump line and broken dripfield line | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
10/27/2023 | Alternative | Reportable Incident | 157-15-0065 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Arrived on site, found discharge tank at normal level. Treatment tank and septic tank were flooded into the riser. Uv had no water running through it. Pulled uv and water began to flow. Uv was clogged pulled and cleaned uv and uv housing. Water level returned to normal. Verified pump, transducer and panel operating as they should | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | 08:37 AM
08/09/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation","Attached Growth Medium"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-12"sludge 4"scum/ Microfast-16"sludge/ Pump Tank-2"sludge/ Pump out required on the Septic-Microfast Tank/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-2305 ETM-70h 58m/ Pump2-2315 ETM-70h 20m/ Peak-65/ High-23/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/09/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"BlowerCompressorAerator Operation"] | ["Disinfection" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [5 empty] | 05/09/2023 |  | 7.000000 |  | 920.000000 |  |  |  | Will be sent separately | Inspected | Replaced UV Bulb while site. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
05/08/2023 | Alternative | Routine/Scheduled | 136-90-0350 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service - STE-Drip-Mound Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Drip Field - Automatic Headworks serviced - disk filters serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 10:30 AM
07/06/2023 | Alternative | RoutineScheduled | 07-158-184 | Mecklenburg | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Southside | Matthews Sanitation Services Llc | 1942001226 | Brian | Matthews |  | 1000 |  |  | Pump |  | Discharge | Chlorination |  | [] | [] | [19 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
01/06/2023 |  | Follow-Up | SWP-05-94 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 2.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | First septic tank and pump tank pumped out by others 2 days prior. Degraded peat was removed by hand with pitch forks and new peat was installed. Peat was purchased from Driller Services, degraded peat was disposed at Spotsylvania Refuse. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 09:31 AM
11/03/2023 | Alternative | RoutineScheduled | 107-96-0320 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | Sand Filter | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The sand filter was in good operating condition. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/27/2023 | 09:40 PM
03/30/2023 |  | Routine/Scheduled | 01-120-0522A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes and spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | Jan 1 1900 6:45AM
09/01/2023 | Alternative | Routine/Scheduled | 550-STS-6590 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/01/2023 | Dec 30 1899 1:00PM
08/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
08/25/2023 | Alternative | Reportable Incident | 157-10-0104 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. The timer is set to 4 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/25/2023 | 03:30 PM
05/02/2023 |  | Routine/Scheduled | 234-12-32 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | Jan 1 1900 1:40PM
10/09/2023 | Alternative | RoutineScheduled | 177-STS-89799 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [8 empty] | 10/09/2023 | [10 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
03/06/2023 |  | RoutineScheduled | 175-13-0135 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Sample box has settled & needs replacing . UV bulb & chord needs replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/31/2023 | 12:26 PM
12/01/2023 | Alternative | RoutineScheduled Component Maintenance | S102-19-0003 | Alleghany | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Alleghany-Roanoke | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | Dec 30 1899 10:39AM
03/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Found filter broken. Replaced A300 filter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
02/22/2023 |  | Routine/Scheduled | {FIPSCode}-STS-1490 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | Jan 1 1900 11:45AM
09/25/2023 | Alternative | RoutineScheduled | 175-03-0838 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | McKim Septic and Pumping | 1942001330 | Michelle | McKim |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Auxiliary Filter","Control Operation","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [17 empty] | Air blower was not working and the atu tank needs pumped out | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/29/2023 | 04:50 PM
05/12/2023 | Alternative | RoutineScheduled | S-04-111-0128 | Botetourt | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Delta white water |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | NA | [16 empty] | Inspected | Septic tank 1" scum and 8" sludge, treatment tank minimal scum layer on top and trace sludge with aertion running. Clear effluent, Pump tank has 5-6" sludge trace, Sprayed for Black widow spiders. many present. Flushed return line and flushed spin filter, 2544.86 hours and 16,402 cycles. System is functioning much improved over previous owner and the new owner is addressing the final wet spots in lower drip area due to the shadly location and lay. They May add fine gravel to the area or possibly replace some tubbing, We have not located any leaks. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/30/2023 | Jan 1 1900 9:30AM
04/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/04/2023 | Alternative |  | SWP-05-193 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
05/26/2023 | Alternative | Reportable Incident Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced Puraflo peat in 8 modules. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
11/28/2023 | Alternative | RoutineScheduled Component Maintenance | 175-15-0447 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 09:34 AM
10/02/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | Western Virginia Water Authority | 1942001145 | Michael | Doss |  |  |  |  | Gravity | Pressure | Drip | UV |  | ["None"] | ["None"] | YES | None | Clear | [5 empty] | 10/02/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | 07:00 AM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
05/11/2023 |  | RoutineScheduled | SWP-05-813 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
10/05/2023 | Alternative | RoutineScheduled Component Maintenance | SD-03-163 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Peat moss is showing its age and will need to be replaced next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
10/05/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-87861 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 4.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Bad enabler float in grinder pump tank, replaced. System has more grease than usual waiting for customer to call us back to discuss. PEAK-210302. HL-93773. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
04/18/2023 |  | RoutineScheduled | SWP-04-399 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation"] | ["Attached Growth Medium" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
07/05/2023 | Alternative | RoutineScheduled Component Maintenance | 113-STS-25897 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | ["BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
06/22/2023 | Alternative | Initial Visit | 800-STS-14497 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 148.000000 | [7 empty] | Owner called due to the red light being on for a week. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. It was raining at the time of service and could not check out the drainfield or mound. The timer was set at 1 minute every 2 hours changed it to 2 minutes every 2 hours. Took BOD sample. NOTE - BOD sample was high - system should function properly after service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | Dec 30 1899 11:30AM
02/08/2023 | Alternative | Routine/Scheduled | S 800-15-0126 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Ecoflo | [6 empty] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Replaced peat moss | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/08/2023 | Dec 30 1899 9:00AM
06/01/2023 | Alternative | RoutineScheduled | SD-05-72 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 65.250000 | ["Effluent Screens","SludgeScum Accumulation","Attached Growth Medium"] | ["Effluent Screens","SludgeScum Accumulation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/02/2023 | 07:45 AM
06/02/2023 |  |  | SP-05-54 | Caroline | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/23/2023 | 12:00 AM
08/04/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 2.000000 | 1000 | anua (puraflo) |  | Pump | Pressure | Trenches | Not Applicable | 100.000000 | ["Effluent Screens","Control Operation"] | ["Control Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | [15 empty] | The system is operational and in compliance with the health department regulations and approved plans. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/04/2023 | 06:00 PM
08/24/2023 | Alternative | Reportable Incident | 810-STS-3773 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/24/2023 | Dec 30 1899 9:00AM
08/21/2023 | Alternative | Routine/Scheduled | 19-137-0119 | Goochland | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream. Changed the filter in the aerator and changed the mesh screen in the spinfilter. There is visible wetness on the drainfield - bleeding out - wet spot - needs to be addressed and/or fixed. The box with the K-Rain valve has water in it. Replaced the riser on the pump tank (6" x 20"). The timer is set to 11 minutes every 2 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/21/2023 | Dec 30 1899 2:30PM
12/14/2023 | Alternative | RoutineScheduled | 13-113-181 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/14/2023 | 12:00 AM
07/20/2023 | Alternative | RoutineScheduled | 12-142-0104 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/15/2023 | Alternative | RoutineScheduled | 154-05-0808 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
09/15/2023 | Alternative | RoutineScheduled | 05-125-067 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/15/2023 | 12:00 AM
03/01/2023 |  | Follow-Up | 101-19-0173 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | [9 empty] | [] | [] | [18 empty] | Replaced UV components. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | 01:20 PM
05/17/2023 | Alternative | Follow-Up | 234-16-209 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Hooked up the pressure switch on the aerator and the UV power wire. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/17/2023 | Dec 30 1899 12:00PM
09/11/2023 | Alternative | RoutineScheduled | 03-197-A16 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | Musty | Clear | 6.500000 | 6.000000 |  | -1.000000 | [11 empty] | needs tablets | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
04/27/2023 |  | Initial Visit | 015-STS-337269 | Augusta | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Gravity | Discharge | UV |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/27/2023 | 12:00 AM
08/04/2023 | Alternative | Routine/Scheduled |  | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level - FOG Present! Aeration Tank - normal level - mixing present - compressor serviced. Pump TAnk - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | 11:00 AM
05/16/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  |  | Drip |  |  | ["BlowerCompressorAerator Operation","Auxiliary Filter","SludgeScum Accumulation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 12:00 AM
11/01/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Rappahannock | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1250 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [17 empty] | The compressor filter was replaced. The discharge control panel will no longer save data. The control panel may eventually cease functioning, entirely. The control panel may need replacing in the near future. Weir cleaned. Pressure sensor not working. System is working but needs a new panel and Pressure sensor. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | 11:59 AM
08/17/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Micro fast | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
06/06/2023 | Alternative | Pump-Out Only | 228-17-0059 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/06/2023 | Dec 30 1899 12:34PM
08/01/2023 | Alternative | RoutineScheduled | 177-16-0020-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2500 | Ecopod |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["SludgeScum Accumulation","Other"] | NA | Musty | Clear | [14 empty] | Pumped Out | Real Estate Transfer/Transaction Septic Tank Pumped Distribution Box Re-Timed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/01/2023 | 10:00 AM
09/19/2023 | Alternative | RoutineScheduled | 101-STS-95144 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/06/2023 | Alternative | Routine/Scheduled | 04-137-0309 | Goochland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | No service since 2018! - Processing tank pumped empty due to reported backup in residence. RSV, recirc pump and effluetn screen serviced. Treatment Module - media lid is fractured, media drapes serviced best able - bridging and ponding present. Pump Tank - float sensors, pump and controls operating DBox - intact. Recommend upgrading pumps and float sensors - replacing media drapes. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/10/2023 | Dec 30 1899 7:45AM
04/11/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
12/13/2023 | Alternative | Routine/Scheduled | 14-120-0331A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/13/2023 | Dec 30 1899 2:31PM
11/09/2023 | Alternative |  | 06-197-021 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/09/2023 |  | 14.900000 |  |  | 14.800000 |  |  | Will be sent separately |  | BOD: 14.9 TSS: 14.8 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/09/2023 | 12:00 AM
05/16/2023 |  | RoutineScheduled | 175-04-0410 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  | ["SludgeScum Accumulation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
02/19/2023 |  | Routine/Scheduled | 041-STS-259695 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [16 empty] | recommend pumpout | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/19/2023 | Jan 1 1900 11:30AM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | Delta Environmental Products, DF Series | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | One air release valve is not functioning properly. Corrections in progress. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/29/2023 | Alternative | Routine/Scheduled |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component Did not excavate. Septic tank is about 36" below grade. VA regulations state that tanks below 30" grade are to have a riser access Recirculation Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Recirculation pump has exceeded life expectancy. Recirculation pump plumbing has exceeded life expectancy. Recirculation floats have exceeded life expectancy. RSV (Recirculating Splitter Valve) Condition of above Component Notes for above Component Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly. Media Sheets Condition of above Component Notes for above Component Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Checked and confirmed spray height is good. Media has exceeded life expectancy. Media lid safety support struts have failed. Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Control panel has exceeded life expectancy Distribution Box Condition of above Component Notes for above Component Water level normal. Distribution box is cracked | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2024 | Dec 30 1899 10:03AM
06/22/2023 | Alternative | RoutineScheduled | S-12-111-0081 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 2.000000 | 4500 | Septic Tank Only | Ecopod | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The controls were operating as designed. The blower filter was cleaned. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | Jan 1 1900 8:25PM
03/08/2023 |  | RoutineScheduled | 175-17-0048 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
03/01/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Keep drainfield clear and mowed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
03/31/2023 |  | Routine/Scheduled | 234-17-173 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/31/2023 | Jan 1 1900 2:15PM
06/23/2023 | Alternative |  |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | 12:00 AM
01/10/2023 |  | RoutineScheduled | 107-11-0213 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/08/2023 | 12:00 AM
01/20/2023 | Alternative | RoutineScheduled | 061-16-250 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Biweekly inspection. In the past 10 days, the system pumped an average of 1,329.1 gals/day at 369.1 gals/cycle (avg.) for a total of 13,291 gallons. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
11/16/2023 | Alternative |  | 027-STS-17384 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/16/2023 |  | 6.370000 |  |  | 1.600000 |  |  | Will be sent separately |  | BOD: 6.37 TSS: 1.60 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/16/2023 | 12:00 AM
08/11/2023 | Alternative | Pump-Out Only | 117-STS-13263 | Mecklenburg | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Southside | Matthews Sanitation Services Llc | 1942001226 | Brian | Matthews | 2.000000 | 1000 |  |  | Pump |  | Trenches |  |  | [] | [] | [17 empty] | Pumped Out |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/14/2023 | 12:00 AM
09/06/2023 | Alternative | RoutineScheduled | SD-12-190 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 62.500000 | ["SludgeScum Accumulation","Effluent Screens"] | ["SludgeScum Accumulation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 09:00 AM
08/08/2023 | Alternative | Routine/Scheduled | S 800-13-0257 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | EcoPod |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | Dec 30 1899 9:02AM
08/09/2023 | Alternative | Routine/Scheduled | 234-16-272 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | Dec 30 1899 1:40PM
09/28/2023 | Alternative | Reportable Incident Component Maintenance | 153-STS-20297 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced drip pump WE20G05P4-21 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
07/18/2023 | Alternative | RoutineScheduled Component Maintenance | 179-16-0372-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
02/23/2023 |  | Routine/Scheduled | 243-03-10611 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/23/2023 | Jan 1 1900 9:30AM
09/15/2023 | Alternative | Routine/Scheduled | 06-137-0075 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out. Noted signs of groundwater infiltration around base of riser. -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Recirculation pump has exceeded life expectancy. Recirculation pump plumbing has exceeded life expectancy. Recirculation floats have exceeded life expectancy. -RSV: Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Noted signs of groundwater infiltration within discharge riser. Discharge pump has exceeded life expectancy. Discharge pump plumbing has exceeded life expectancy. Discharge floats have exceeded life expectancy -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Checked and confirmed spray height is good. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Control panel has exceeded life expectancy. -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | Dec 30 1899 2:03PM
10/18/2023 | Alternative | RoutineScheduled | 07-197-A10 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  | ["Disinfection"] | [19 empty] | No de-chlorine tablets in chamber | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
01/13/2023 |  | Follow-Up | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1500 |  |  | Pump | Gravity |  | Not Applicable |  | ["Other"] | ["Other"] | NO | [17 empty] | Peat Moss turned to reactivate- Peat Moss is still in good condition and functioning as intended- no leaks found | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/01/2023 | Jan 1 1900 3:35PM
04/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/26/2023 | Alternative |  | 179-19-0019-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
05/02/2023 |  | Routine/Scheduled | 11-120-0104 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Trash Tank - normal level Aeration Tank - normal level - mixing present - aspirator serviced. Clarifier - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Dbox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/03/2023 | Jan 1 1900 6:45AM
07/21/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1500 |  |  | Pump |  | Pad | Not Applicable | 450.000000 | ["None"] | ["None"] | NO | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | Dec 30 1899 4:30PM
05/12/2023 | Alternative | RoutineScheduled | S-13-111-0067 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Delta Environmental DF60 |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Routine inspection visit- Sludge levels- 2-3" Scum and 16" sludge, clear effluent on top, try to reduce scum FOG input (fat oil and grease in system, also cleaners, sanitizers and antibiotic soaps etc.) Treatment tank under 1" scum and 12" sludge- Blower has been replace once, Blower alarm works, Blower works. CLeaned blower filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | Jan 1 1900 9:30AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/06/2023 | Alternative |  | 179-STS-86827 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
02/17/2023 |  |  | 154-19-0130 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
03/27/2023 |  | RoutineScheduled | 175-19-0162 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-6"sludge 8"scum/ Microfast-12"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ Recommend pump out of the Septic Microfast Tank before next March inspection/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-1651 ETM-75h 15m On-2m 40s Off-6h Dose 131.25 gal / High-7 / No breakout or spongy areas on the drainfield and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/07/2023 | Alternative | RoutineScheduled | 17-137-0148 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Carrington Pump & Irrigation | 1942001121 | John | Carrington |  |  | Norweco |  | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 12:00 AM
11/17/2023 | Alternative | RoutineScheduled Component Maintenance | 179-11-0181-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium"] | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
04/18/2023 |  | RoutineScheduled | 175-09-0420 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
10/24/2023 | Alternative | Routine/Scheduled | 13-120-0034A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/24/2023 | Dec 30 1899 4:37PM
09/14/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Clearstream | none | Pump | Gravity |  | UV |  |  |  | NA | Musty | Clear | 6.800000 | 11.400000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 10/16/2023 | Dec 30 1899 12:58PM
11/08/2023 | Alternative | RoutineScheduled | SD-06-338 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 62.500000 | ["Attached Growth Medium","SludgeScum Accumulation","Effluent Screens"] | ["Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/15/2023 | 03:00 PM
08/16/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] |  | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 09/15/2023 | Dec 30 1899 2:41PM
11/20/2023 | Alternative | Routine/Scheduled |  | Dinwiddie | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/20/2023 | Dec 30 1899 1:37PM
04/10/2023 |  | Reportable Incident |  | King William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 0.000000 | 0 | None | None | Gravity | Gravity | Discharge | Not Applicable | 450.000000 | [20 empty] | Site evaluated - new owner - reports residence vacant for 5+ years !!! Located agriculture chemical tank being used as septic tank. Located 1 drain line daylighting on side of bank into stream. Spoke with customer about the system not being up to code. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/11/2023 | 07:15 AM
03/29/2023 |  | RoutineScheduled | 175-01-0073 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["Distribution Pump Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Both disc filters were dirty. Improved closing action of blue valve (backwash) #1 by shimming the spring. High rate on zone 1 was caused by continuous dosing to zone 2 through a torn diaphragm - replaced it, rate dropped from 9.6 to 7.0 gpm. Zone 2 solenoid was badly corroded and not working - replaced it. Advised owners that the hydraulic unit and control panel were both over 20 years old and probably nearing the end of their useful lives. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
01/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Cleaned the air pre-filter as preventative maintenance. "Power On" light (green) was burnt out, replaced the assembly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
11/01/2023 |  | Routine, Scheduled | SWP-03-820 | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | JENKINS, TIMOTHY R | 1934000017 | TIMOTHY | JENKINS |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/29/2011 | 10:16 AM
11/28/2023 | Alternative | Routine/Scheduled | 196-07-258 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2500 | Ecoflo |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 06:23 PM
09/05/2023 | Alternative | RoutineScheduled | 03-100-1546 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | ECOFLO |  | Pump | Gravity | Mound | Not Applicable | 600.000000 | [] | [] | NA | [17 empty] | SLUDGE JUDGE SEPTIC TANK 5-6" FROM BOTTOM 2" FROM TOP EVERYTHING WORKING AS IT SHOULD PEAT MAY NEED REPLACING NEXT YEAR | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | 12:00 PM
09/22/2023 | Alternative | RoutineScheduled Component Maintenance | 061-STS-24498 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation"] | ["Effluent Screens" ,"Level Sensor Operation"] | YES | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Annual inspection. Pumps run individually and alternate - each doses one half of the LPD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
11/13/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | Dec 30 1899 11:50AM
12/13/2023 | Alternative | RoutineScheduled | 167-STS-17800 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/13/2023 | 12:00 AM
12/15/2023 | Alternative | Routine/Scheduled | 149-11-048 | King & Queen | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component Normal Level 9" of sludge and 1" of solids No signs of infiltration Discharge/Pump Tank Condition of above Component Notes for above Component Above normal Level All floats and pump are functioning properly however floats are Aged Pulled and cleaned pump screen and Vortex filter Proper pressure on gauges Aeration Condition of above Component Notes for above Component Normal Level Less than 1" of suspended solids Aerating properly No signs of infiltration Air Pump/Blower Condition of above Component Notes for above Component 120v Pulled and cleaned air filter Cleaned out housing for air pump Control Panel Condition of above Component Notes for above Component 120v Panel in alarm. All audible and visual alarms are functioning properly Discharge pump pulled 10.8amps Air pump pulled 1.68amps Drip Field Condition of above Component Notes for above Component No signs of surfacing Field was wet Flushed field until water ran clear | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 10:11 AM
06/29/2023 | Alternative | RoutineScheduled | 05-100-0859 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | ECOFLO |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | [] | [] | YES | [17 empty] | REPLACED XT ALARM BULB EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | 11:50 AM
07/28/2023 | Alternative | Routine/Scheduled | 234-15-216 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/28/2023 | Dec 30 1899 10:00AM
05/31/2023 | Alternative | RoutineScheduled Component Maintenance | 179-12-0273-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
01/18/2023 |  | Routine/Scheduled | 03-172-0334A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level Processing TAnk - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/19/2023 | Jan 1 1900 7:15AM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/07/2023 | Alternative | Routine/Scheduled | 150-04-070 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. BioFilter - peatmoss in good condition - raked / turned. Pump Basin - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/08/2023 | 10:30 AM
01/02/2023 |  | Routine/Scheduled | 06-120-0042A | Chesterfield | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Discharge | UV | 450.000000 | Dispersal System Operation | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. U.V. Disinfection - Bulb and housing serviced. Pump Tank - float sensors, pump and controls operating. Spray Irrigation - one spray head missing! | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/03/2022 | Jan 1 1900 7:30AM
06/19/2023 |  | RoutineScheduled | 109-STS-33153 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 12:00 AM
01/27/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.210000 |  |  |  |  | 01/27/2023 |  | 23.000000 |  |  | 12.200000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2023 | 08:00 AM
04/06/2023 |  | RoutineScheduled | 175-18-0221 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
05/18/2023 | Alternative | Follow-Up | 093-18-0087 | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Hooked up the pressure switch. Performed a draw down test - 32.5 gallons per dose. Set the timer to 8 minutes every 1.5 hours. 585 gallons per day. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/18/2023 | Dec 30 1899 12:00PM
01/30/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim |  |  |  |  | Pump |  | Drip | UV |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | Dec 30 1899 2:55PM
06/24/2023 | Alternative | RoutineScheduled | 175-10-0305 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura flo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 6.500000 |  |  | 2.100000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/03/2023 | 12:00 AM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/28/2023 | Alternative | Reportable Incident | 159-01-056 | Middlesex | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 2000 | Clearstream | Clearstream | Pump | Pressure | Trenches | Not Applicable | 1500.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Alarm Event - Continuate from Saturday 02/25/2023. Primary septic tank pumped empty for storage. All Tanks flooded - compressor 1 & 2 are functioning, Compressor three making a noise as if bearings are failing. Pump Tank pumped empty - oily sheen on effluent - all pumps tested in HAND and failed to function. No Service agreement in place. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/01/2023 | 09:15 AM
09/04/2023 | Alternative | Routine/Scheduled | 109-06-0961 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Multiflo FTB |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/04/2023 | 09:45 AM
01/25/2023 |  | Routine/Scheduled | 093-07-0226 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | Jan 1 1900 12:15PM
04/28/2023 | Alternative | RoutineScheduled | 04-197-A15 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/28/2023 | 12:00 AM
02/06/2023 | Alternative | RoutineScheduled | 049-STS-25843 | Cumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Bobby's septic inspections LLC | 1942001548 | Robert | Burnett | 1.000000 | 1000 | septic tank | ecoflow | Gravity | Gravity | Discharge | Chlorination | 350.000000 | ["Disinfection","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation","Attached Growth Medium"] | ["Attached Growth Medium","Disinfection","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | None | Clear | 6.800000 |  | 0.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | Dec 30 1899 12:00PM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20513 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter"] | ["Effluent Screens" ,"Auxiliary Filter"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
09/07/2023 | Alternative | Initial Visit |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun |  | 1942001734 | Richard | Morrison | 1.000000 | 1500 | EZ Treat 750GPD |  | Gravity | Gravity | Trenches | UV | 750.000000 | [] | [] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/11/2023 | 12:00 AM
01/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection"] | ["BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2023 | Dec 30 1899 8:47AM
03/15/2023 | Alternative | RoutineScheduled | 159-17-0110 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Aquasafe |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | [] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
06/30/2023 | Alternative | Routine/Scheduled | 550-STS-6411 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | Dec 30 1899 10:40AM
08/01/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["SludgeScum Accumulation"] | [] | YES | [17 empty] | Everything Working Just Recommend Pumping | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
02/16/2023 | Alternative | RoutineScheduled | 121-STS-11849 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 3.000000 | 3000 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] |  | Septic | Cloudy | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/28/2023 | Alternative | RoutineScheduled | 182-01-0572 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | Quick connect/disconnect leaking (does not seal well when seated) | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
09/18/2023 | Alternative | RoutineScheduled | 159-03-016 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/18/2023 | 12:00 AM
08/29/2023 | Alternative | Routine/Scheduled | 234-15-166 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/29/2023 | Dec 30 1899 1:40PM
09/12/2023 | Alternative | RoutineScheduled |  | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2000 | septic | Microfast 1.5 | Gravity | Pressure | Drip | Not Applicable |  | [] | [] | YES | Musty | Clear |  | 7.100000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | 09:55 AM
05/05/2023 | Alternative | RoutineScheduled | SD-06-336 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 65.630000 | ["SludgeScum Accumulation","Effluent Screens"] | ["Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/09/2023 | 09:00 AM
06/09/2023 | Alternative | Reportable Incident | 019-STS-25308 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Readjusted float | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
08/17/2023 | Alternative | Routine/Scheduled | 14-174-0158 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | EcoPod |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/17/2023 | Dec 30 1899 8:22AM
05/09/2023 |  | RoutineScheduled | 108-16-0011 | Bath | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 2.000000 | 2500 | Septic Tank Only | MicroFast | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The blower and the spin clean filter were both cleaned. The pressure bell was pulled and reset. The controls were operating as designed. There were no visible leaks in the drip field. There were return effluent coming back to the pump tank so the drip field was operating as designed. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/03/2023 | 12:25 PM
10/12/2023 | Alternative | RoutineScheduled Component Maintenance | SD-04-455 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Pad | Chlorination |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
10/12/2023 | Alternative | RoutineScheduled | 95-197-A6 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | JET |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","SludgeScum Accumulation","Dispersal System Operation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/12/2023 | 12:00 AM
02/21/2023 |  | RoutineScheduled | 033-14-0139-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance | 182-19-0172 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 06/19/2023 |  | 52.000000 | [5 empty] | Will be sent separately | Inspected | Repaired air supply Repaired riser connection Added media cleaner Adjust levelers in dbox | This AOSS should now return to normal function after having provided the above state routine maintenance | 08/23/2023 | 06:57 AM
05/10/2023 |  | RoutineScheduled | 2011-143-0156 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Carrington Pump & Irrigation | 1942001121 | John | Carrington |  |  | Norweco |  | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Level Sensor Operation","Effluent Screens","Distribution Pump Operation","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 12:00 AM
01/17/2023 |  | RoutineScheduled |  | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Dispersal System Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation"] | NA | [7 empty] | 01/17/2023 |  | 414.000000 | [5 empty] | Will be sent separately | Inspected | Repaired leak in field Installed reman. blower Upgraded timer Repaired valve box lid Uncovered access to pump tank | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
01/20/2023 |  |  | 087-STS-6315 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [17 empty] | Pumped Out | Replaced control panel and added two floats | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/03/2023 | 12:00 AM
11/20/2023 | Alternative |  | 150-03-243 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/27/2023 | Alternative | RoutineScheduled | 06-120-0838 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Ecoflo |  |  |  | Trenches |  |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Level Sensor Operation"] |  | Musty | Cloudy | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/27/2023 | 12:00 AM
12/21/2023 | Alternative | Follow-Up Component Maintenance | SWP-05-259 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Removed roots from headers as best as possible and resealed header penetrations in distribution box. Peat moss does not need replacing but does need maintenance, performed maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 07:39 AM
04/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Effluent pump appears to be near the end of its life but is functioning at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/25/2023 | Alternative | Follow-Up Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Repaired force main in EQ tank & replaced 42" concrete lid. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/16/2023 | Dec 30 1899 12:58PM
12/15/2023 | Alternative | Follow-Up Component Maintenance | SD-14-87 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Chemically treated media the day before cleaning. FAST unit pumped out by others. Washed down media. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
05/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/20/2023 |  | RoutineScheduled | 177-16-0051-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Grease and sanitary wipes accumulating in septic tank. Treatment is ok. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
11/27/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/27/2023 | Dec 30 1899 1:45PM
04/25/2023 |  | RoutineScheduled | 179-STS-88955 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. RECIRC: HL 4,LL 18, OVERRIDE 1478. DISCHARGE: HL 1. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
03/17/2023 | Alternative | Routine/Scheduled | 157-12-0113 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Aeration Tank - normal level - mixing present - compressor serviced. PUmp tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/20/2023 | 09:30 AM
12/04/2023 | Alternative | Reportable Incident Component Maintenance | 175-00-0896 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | Atu alarm. Replaced failed compressor (and the air filter). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
03/08/2023 |  | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 |  |  | Pump | Pressure | Trenches |  | 750.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 11:00 AM
11/02/2023 | Alternative | RoutineScheduled |  | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1000 | 750 | 250 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Septic Tank Baffles"] | YES | Pungent | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | 12:00 AM
05/17/2023 | Alternative | Initial Visit | 183-STS-10197 | Sussex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 17.000000 | [7 empty] | Contractor contacted us about an alarm. Serviced system. Cleaned the filter and the diffuser in the Clearstream and cleaned the filter in the aerator. Replaced the 3/4" nipples with longer ones. The timer is set to 2 minute every 4 hours. Took BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | Dec 30 1899 3:30PM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/28/2023 |  | RoutineScheduled | ST-97-276 | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Effluent Screens" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend pumping the septic tank due to sludge accumulation in the tank. There are two wet areas in the dispersal area where it appears the emitters have failed. We recommend excavating by hand to uncover them & repairing the drip tubing. We will also plan to locate the second air release valve and evaluate the check valves. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/02/2023 | 07:49 AM
07/20/2023 | Alternative | RoutineScheduled Component Maintenance | 175-17-0444 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
05/24/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
06/01/2023 |  | Routine/Scheduled | NYII-B9RNK3 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | Jan 1 1900 2:15PM
03/29/2023 |  | RoutineScheduled | 124-STS-2379 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 2.000000 |  | Norweco Singulair |  | Pump | Pressure | Drip |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 12:00 AM
02/08/2023 |  |  | 033-06-0126-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
03/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/15/2023 |  |  | 033-15-0078-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Multi-Flo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
03/29/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/17/2023 | Alternative | RoutineScheduled | 14-100-0137 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 500 | AQUASAFE |  | Pump | Gravity | Mound | UV | 450.000000 | [] | [] | [18 empty] | EVERYTHING WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/18/2023 | 09:10 AM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Multiflo FTB | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/13/2023 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Loudoun | SLUSSER, JAMES B | 1934000064 | JAMES | SLUSSER |  |  | Puraflo | Septic Tank Only | Pump | Distribution Box | Aggregate Trench | None |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/12/2013 | 12:29 PM
05/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 5.000000 |  | Clearstream | Clearstream | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Effluent pump in (600NC on Left from Splitter) is stuck on and will not stop running without shutting off breakers. Pump was left running so as not to flood the tank and cause further issues. Repairs are in progress | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
01/30/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim |  |  |  |  | Pump | Pressure | Drip | UV |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | Dec 30 1899 2:55PM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
11/10/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-87183 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation"] | ["Distribution Pump Operation" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
03/01/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 03/01/2023 |  | 8.000000 | [5 empty] | Will be sent separately | Inspected | Lab Normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
05/19/2023 | Alternative | Reportable Incident | 800-12-0014 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/19/2023 | Dec 30 1899 8:00AM
03/18/2023 |  | RoutineScheduled | 133 06 0598 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank with a 4" solids crust. Flushed treatment unit spray manifold. Cleaned recirculation pump basket filter. 2" of solids in discharge pump tank. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/09/2023 | 07:03 PM
03/17/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The surge box, d-box and all header lines replaced. Septic system is in working condition at this time. This repair does not guarantee the life of any component. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/01/2023 |  | Routine/Scheduled | {FIPSCode}-STS-4015 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | Jan 1 1900 12:01PM
04/26/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
03/28/2023 |  | RoutineScheduled | 179-11-0209-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | YES | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
12/06/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 12:00 AM
01/18/2023 | Alternative | RoutineScheduled | 05-183-025 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Attached Growth Medium","Control Operation","Distribution Pump Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/18/2023 | 12:00 AM
11/28/2023 | Alternative | Follow-Up |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Meet with the pumping company and pumped and cleaned the septic tank, Clearstream tank, and pump tank. Cleaned the disc filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | Dec 30 1899 9:00AM
03/03/2023 |  |  | 14-120-0453A | Chesterfield | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 1.000000 | 2300 | 2300 |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["Effluent Screens","Control Operation","SludgeScum Accumulation"] | YES | None | Discolored | 7.000000 |  | 6.000000 | [13 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/03/2023 | Jan 1 1900 11:30AM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | peat starting to fail | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
04/07/2023 |  |  |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/20/2023 |  | Routine/Scheduled | 234-16-36 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | EZ Treat Sandfilter |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | Jan 1 1900 10:00AM
04/13/2023 |  | Routine/Scheduled | 133 15 0106 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 10:30 AM
04/25/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Dispersal System Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/22/2023 | 11:15 AM
03/23/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
04/24/2023 | Alternative | RoutineScheduled | 107-13-0324 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
02/17/2023 | Alternative | Routine/Scheduled | 157-99-079 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. BioFilter - peatmoss in poor condition - wet - 22" of standing effluent in sample port. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 10:35 AM
05/20/2023 | Alternative | RoutineScheduled | SD-07-289 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | ATU | Polishing Sand Filter |  |  |  |  | 250.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 6.900000 |  |  | 2.100000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/22/2023 | 12:00 AM
06/22/2023 | Alternative | RoutineScheduled | 177-STS-92596 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco | Norweco | Gravity | Pressure | Mound | Not Applicable | 900.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | 12:00 AM
12/19/2023 | Alternative | Routine/Scheduled | 04-163-0152 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Trash Tank Condition of above Component Notes for above Component Found at normal level 6in of sludge and less than 1in of solids. Recirculation Tank Condition of above Component Notes for above Component Found at normal level, 1in of sludge and less than 1in of solids. Pulled and cleaned pump floats and biotube filter. Roots growing against the riser and its deforming the riser RSV (Recirculating Splitter Valve) Condition of above Component Notes for above Component Pulled and cleaned inside and out Discharge/Pump Tank Condition of above Component Notes for above Component Found at normal level, fixed wiring issue onsite. Less than 1in of sludge and solids. Tesyd floats and pump. Pump pulling high amps. Plumbing has met life expectancy Media Sheets Condition of above Component Notes for above Component Media lid hinges are broken. Sparyed media sheets brushed laterals and flushed unit. Control Panel Condition of above Component Notes for above Component Panel has met life expectancy. 120 volts audio and visual alarms working as they should. Fixed wiring issue for discharge. Recirc pulled 10.7 amps Discharge pulled 15.2 amps Distribution Box Condition of above Component Notes for above Component Surge box. Found at normal level rwmoved small roots while onsite. Dbox found at normal level. Lines balanced and taking water. Drain Field Condition of above Component Notes for above Component No signs of surfacing in drainfield area | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | Dec 30 1899 8:16AM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | DSS removed roots and resealed distribution box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/09/2023 | Alternative | RoutineScheduled | 2022-06-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | Chlorination | 500.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | 6.900000 |  |  | 1.400000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/11/2023 | 12:00 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The inlet riser on the septic tank is damaged and requires replacement. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/19/2023 | Alternative | RoutineScheduled | 17-192-006 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | CLEARSTREAM |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Septic Tank Baffles","Disinfection","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/19/2023 | 12:00 AM
05/05/2023 | Alternative | Routine/Scheduled | 166-15-0104 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Pressure | Mound |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 45.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/05/2023 | 05:25 PM
08/03/2023 | Alternative | RoutineScheduled Component Maintenance | {FIPSCode}-STS-78803 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter" ,"Distribution Pump Operation"] | ["Effluent Screens" ,"Auxiliary Filter" ,"Distribution Pump Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
09/05/2023 | Alternative | Routine/Scheduled | 11-120-0363AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 2.000000 | 1000 | Sandfilter, Non-recirculating |  | Pump | Gravity | Pad | Not Applicable |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | Effluent filter cleaned. Control panel tested. Sample chamber checked. Sample chamber dry. Panel working. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | Dec 30 1899 4:18PM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/20/2023 | Alternative | RoutineScheduled | 154-02-1073 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Advantex |  | Gravity | Pressure | Drip | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | 12:00 AM
04/10/2023 |  | RoutineScheduled | 153-STS-18988 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 04:23 AM
12/08/2023 | Alternative | RoutineScheduled Component Maintenance | 177-06-0361-SWP | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | As noted previously, the water meter is not working and should be replaced. Additionally the dispersal area should be mowed and maintained in a mowed condition. Also, the riser on the pump tank is leaking. We recommend excavating and resealing this riser, especially if you get alarms during periods of heavy rain. Please contact our office when you would like estimates for these repairs. 2-21-24: Per email from Ed Scott to MWebb: "There was no response to our recommendations. " | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 01/02/2024 | 11:12 AM
05/03/2023 |  | Pump-Out Only | 234-15-47 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/03/2023 | Jan 1 1900 9:00AM
12/13/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 1:50PM
01/05/2023 |  | Routine/Scheduled | 228-15-0385 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/05/2023 | Jan 1 1900 2:20PM
02/10/2023 |  | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Multiflo FTB | [6 empty] | Attached Growth Medium | Attached Growth Medium | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | 12:38 PM
12/08/2023 | Alternative | Reportable Incident | 093-11-0053 | Isle of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Environmental Services of Virginia | 1942001182 | Steve | Haley | 1.000000 | 450 | CSNCT3T |  | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | YES | Musty | Clear | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/08/2023 | 12:00 AM
02/05/2023 |  | Routine/Scheduled | 041-STS-259722 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/05/2023 | Jan 1 1900 9:00AM
01/13/2023 |  | Routine/Scheduled | 234-13-417 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/13/2023 | Jan 1 1900 1:55PM
05/30/2023 | Alternative | RoutineScheduled | NCRS-B84S3S | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection and maintenance completed. Replaced uv lamp as maintenance. Return line pressure has dropped about 6 psi per year since June of 2021. This could be for a variety of reasons, none of which are obvious at this point. Backpressure is still more than adequate to cause emitters to open. If return line pressure or flush rate drops any further, additional testing and investigation will be required. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
01/18/2023 |  | RoutineScheduled | Discharge | Pulaski | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - New River | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 7 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/18/2023 | 12:00 AM
09/06/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
03/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
12/07/2023 | Alternative | RoutineScheduled Component Maintenance | 107-04-0222 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
12/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Orange | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | The blower motor for the aerobic treatment unit is not working and should be replaced. We can furnish and install a new blower motor for $1320.00. Please contact our office when you would like to schedule this work. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 01/02/2024 | 11:12 AM
06/06/2023 |  |  | {FIPSCode}-STS-79408 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
10/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 10/18/2023 |  | 19.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
07/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2024 | 12:23 PM
12/08/2023 | Alternative | RoutineScheduled | 05-142-0420 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C & E Mechanical Corporation | 1942001339 | Louis | Timberlake | 1.000000 |  | Delta White Water |  | Pump | Gravity | Trenches |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [6 empty] | Blower housing is low in mulch & should be raised; air filter cleaned | [9 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/15/2023 | Dec 30 1899 3:45PM
04/21/2023 |  | Routine/Scheduled |  | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Aqua Klear |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Primary septic tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/24/2023 | Jan 1 1900 10:00AM
08/02/2023 | Alternative | RoutineScheduled | 085-STS-31547 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Control Operation","Distribution Pump Operation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/22/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/12/2023 | Alternative | RoutineScheduled | 04-184-5003 | Scott | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | EHD - Lenowisco | Scott County Health Department | 1940001589 | Nathaniel | Rasnake |  |  |  |  | Gravity | Gravity | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation","Other"] | ["None"] | NO | Septic | Cloudy | 7.000000 | 3.000000 |  |  | TRC After Dechlorination: 0.0 | [10 empty] | Field tests not within regulation | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/29/2023 | 12:00 AM
06/02/2023 |  | RoutineScheduled | 101-18-0194 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 12:00 AM
08/16/2023 | Alternative | Routine/Scheduled | 03-160-0427 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/16/2023 | 12:30 PM
04/18/2023 |  |  | 169-STS-26550 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 04/18/2023 |  | 2.460000 |  |  | 1.700000 |  |  | Will be sent separately |  | BOD: 2.46 TSS: 1.70 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/18/2023 | 12:00 AM
10/18/2023 | Alternative | Reportable Incident | 228-17-0280 A | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/18/2023 | Dec 30 1899 4:30PM
05/22/2023 |  | Routine/Scheduled | 234-16-192 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/22/2023 | Jan 1 1900 12:45PM
06/20/2023 | Alternative | Reportable Incident | 234-14-278 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Control Operation","Disinfection"] | ["Control Operation","Disinfection"] | N/A | [17 empty] | Replaced UV control panel and bulb | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/20/2023 | Dec 30 1899 7:00AM
04/21/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
09/06/2023 | Alternative | RoutineScheduled Component Maintenance | 177-17-0074-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. HL-29, ETM-0H0M. PEAK CNTS-29, ETM 439H51M. Off float for discharge took a 45 seconds to open but tested few times and open and close. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
04/03/2023 |  | RoutineScheduled | 153-STS-20353 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon |  |  | Septic Tank/ Advantex Recirculation Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | [18 empty] | Septic Tank-4"sludge 0"scum/ Recirc. Tank-4"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Recirculation pump intake cleaned/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump-3284 ETM-371h 5m/ On-6m 55s Off-2h 33m/ Advantex Run Time-303.5 Total Cycles-57910.0/ Zone1-2.0/ Zone2-2.8/ High-21/ Peak-3/ Recirc. Media in good condition and dosing properly/ No breakout or spongy areas on the drip field and dosing correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/14/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Ecoflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/26/2023 | 09:42 AM
04/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/17/2023 | 12:44 PM
06/08/2023 | Alternative | Initial Visit | 085-STS-33971 | Hanover | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Received a call about a smell. The aux solenoid is not opening and plastic fitting is broken. The UV tube is broke (Quartz tube) and the UV bulb is bad. There is a 240 volt pump with Orenco panel for the UV and pump. Adjusted pipe in the Clearstream - cut off return hose in the septic tank. The inlet tee is backgrading to the house. The issues need to be addressed and/or fixed. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/08/2023 | Dec 30 1899 12:00PM
07/18/2023 | Alternative | Reportable Incident Component Maintenance | 177-11-0116-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Owner called about exposed piece of drip tubing. This system had been installed in woods. Owners working on cleaning up brush and remnants from wind storm damage. Cut out a kinked piece of tubing in zone 2 and attempted to run a test cycle. Pump making a loud noise but not pumping. Separated pump from motor (turbine) and sprayed off the pump (has plastic gears). Motor by itself ran fairly quiet. Reinstalled pump assembly and it went on to working correctly. Pump is now 11 years old so not sure how much longer it will last. Eliminating the tubing kink boosted the flush rate for zone 2 from 7.9 to 10.1. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 07:01 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/08/2023 | Alternative | Reportable Incident | 03-120-0053A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | - Upon arrival, I found the recirculation tank in low level due to low usage. I met with Mr Mik and informed him that the system should return to normal in about a week to two weeks. I showed him how to disable the audible alarm and that he will need to reconnect in about two weeks after the system returns to normal. I did a walkthrough of the system to educate Mr Mik and went over expectations for the service | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | Dec 30 1899 9:55AM
09/28/2023 | Alternative | RoutineScheduled | 177-STS-87709 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 0-3 3-0 | 0-0 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","BlowerCompressorAerator Operation"] |  | None | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/28/2023 | 03:00 PM
03/31/2023 |  | Follow-Up | 179-STS-88001 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Follow up. Replaced damaged lid plus riser on pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
04/13/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 5000 | EcoPOD |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Tank SLudge volumes- Septic Tank by store has 4-5 in scum layer on surface unable to check sludge on bottom, Reccomend to pump this scum and remove all and sludge on bottom, Septic Tank by Shower has about 12 inch sludge on bottom and minimal scum, Septic Tank by unit #17 ok, Old Blower unit not working on arrival - breaker tripped - owner has replacment to install it himslef. Discharge alarm and pump to drainfield good. -Tank near new flower and mulch bed 2-3" scum 8-12" sludge. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
02/19/2023 |  | Routine/Scheduled | 041-STS-259116 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 2.000000 | 1250 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/19/2023 | Jan 1 1900 12:30PM
02/11/2023 |  | RoutineScheduled | 2086-04-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.400000 |  |  | 2.200000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/08/2023 | 12:00 AM
04/18/2023 |  | RoutineScheduled | 153-STS-20350 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | NA | [17 empty] | Septic Tank-4"sludge 2"scum/ Microfast-2"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Faulty Timer enable float replaced/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-420 ETM-31h 9m/ High-10 Dose 262.5 gal On-4m 49s Off-12h Pump-54gpm/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
01/26/2023 |  | Routine/Scheduled | C-175-17-0088 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | Jan 1 1900 9:13AM
01/26/2023 |  | RoutineScheduled | 179-12-0130-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
07/18/2023 | Alternative | RoutineScheduled | 175-04-0728 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-4"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Puraflo Peat was turned, media is damp and may need to be replaced soon but it is good at this time/ Recommend wide angle float for the floats/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-054135 ETM-0045915/ Recommend triming or removal of the Holly Tree near the Puraflo Modules/ No breakout or spongy areas on the Drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/02/2023 | Alternative | RoutineScheduled | SD-11-044 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Compressor needs replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | 12:05 PM
11/06/2023 | Alternative | RoutineScheduled |  | Warren | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | McKim Septic and pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/15/2023 | 11:00 PM
03/06/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | Routine Inspection - Septic tank 2" scum 6-12" sludge - Pump Tank Trace sludge, Recirc Tank - trace sludge. Effluent filter clean, system discharge pump was not powering on and no voltage on pump. Found the breaker had tripped and been reset but was not fully switched off and on. Reseting the breaker returned it to normal operation. This has occured over each prior winter and appears a posisble electrical line maybe exposed to ground when heavy rains occur. We cannot located or detect the point of ground but system works fine when on. The septic gets used infrequently. More investigation into electrical issue may follow but system is working fine when breaklers on.. Home is vacant at this time. Septic tank does not need pumping. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/26/2022 | 09:30 AM
11/07/2023 | Alternative | RoutineScheduled | 06-113-241 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 10 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/07/2023 | 12:00 AM
06/12/2023 | Alternative | Initial Visit | 133-STS-96201 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Advanced Septic |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Visit - Reported installed 1 year ago. Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump tAnk - float sensors, pump and controls operating. DBox - not excavated and inspected at owners request. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 02:23 PM
01/24/2023 |  | RoutineScheduled | 101-02-0137 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | MicroFast |  | Gravity | Pressure | Trenches | Not Applicable | 500.000000 | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/28/2023 | 12:00 AM
10/19/2023 | Alternative | Routine/Scheduled | 228-18-0309 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/19/2023 | Dec 30 1899 8:30AM
03/03/2023 |  | Routine/Scheduled | 147-03-0147 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | ["Attached Growth Medium","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Biofilter changeout. 02/27/2023 - septic tank pumped empty for peatmoss to dry. 03/03/2023 - biofilter changeout conducted - | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | Jan 1 1900 6:30AM
05/30/2023 | Alternative | RoutineScheduled | 159-STS-95150 | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/14/2023 |  | RoutineScheduled | 154-07-0576 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Norweco 960 |  | Pump | Pressure | Mound | Not Applicable | 150.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | 01:05 PM
03/03/2023 |  | Follow-Up | 179-09-0056-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to meet with homeowner to verify where drainfield was located after getting the septic records. Drainfield is over grown with small trees. Homeowner will clear the trees. Recomend after trees are cleared we dig up the distribution box and video inspect the drainfield to check for roots in the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
10/09/2023 | Alternative | RoutineScheduled Component Maintenance | 179-12-0087-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
11/16/2023 | Alternative | RoutineScheduled | 043090057 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | 12:00 AM
04/12/2023 |  | RoutineScheduled | 101-03-0605 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Advantex |  | Gravity | Pressure | Drip | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/16/2023 | 12:00 AM
03/23/2023 |  | Follow-Up | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Distribution Pump Operation" ,"Dispersal System Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced Step 20 pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Jan 1 1900 12:05PM
11/09/2023 | Alternative | Reportable Incident Component Maintenance | 179-07-0164-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for blower not running due to blown fuse in panel. Replaced fuse. Timer float was stuck on. Replaced failed float. Float being stuck on could of damaged discharge pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
07/06/2023 | Alternative | RoutineScheduled | 109-08-0160 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank Pumped | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | Septic Tank 1" scum layer,18-24" sludge, Pump Tank 10" trace of sludge, Cleaned Effluent filter , Pump runs when called and alarm testedoperational but a little slow to respond. both float switches operational.Turned Peat in1 of 4 pods, Peat in good condition for age. Out said they would replace the lid on D box plastic tuftite 8 in lid to minimizing run off to back yard. Made reccomedation to get septic tank pumped out and rotorooter came to pump out the next day. Reccomend to owner to cut back all vines and shrubs around peat pods so they are accesible for future inspection.. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/30/2023 | 09:30 AM
10/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
04/13/2023 |  | Reportable Incident |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Attached Growth Medium | Attached Growth Medium | N/A | [17 empty] | AOSS - Maintenance Replaced textile media drapes with new Upgraded installation bars, hangers and lid locks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | Jan 1 1900 9:15AM
05/25/2023 | Alternative | Pump-Out Only | 095-STS-5058 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Aqua Klear |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Pumped and cleaned processing tank. Installed access riser to grade on septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | Dec 30 1899 1:00PM
09/25/2023 | Alternative | Reportable Incident Component Maintenance | 061-18-409 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["SludgeScum Accumulation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | High level alarm. Control panel showing float error and would not allow alarm to be silenced. Pulled up float tree, alarm light stayed on. Cut off corroded wire nuts and made new connections, alarm turned off. Hole in pump tank lid was lined up with opening in top of interior splice box. Rotated lid for now, but lid needs replaced. Pump was running, but effluent level was not noticeably dropping. Cleaned dirty pump intake, replaced return line pressure gauge, replaced clogged spin filter. Pump started and stopped when manipulating bottom float - supposed to be time-dosed. Wasp control pad would not cycle past the screen for elapsed pump time, and would not show pump settings. Aerator had been running but suddenly stopped running. Control pad indicated locked up or shorted aerator. Aerator was not locked up and owner was later able to run it by connecting to an extension cord. These symptoms indicate that the control pad needs to be replaced. Advised owner to arrange for the pump out of the pump tank and septic tank ASAP. Treatment quality is poor. Hopefully will improve after tanks are pumped and biokinetics filter is cleaned. Septic tank does not have a sanitary inlet tee. Not sure if required. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
09/01/2023 | Alternative | RoutineScheduled | 171-09-0115 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | YES | [16 empty] | Inspected | Sludge level- under 1" scum- 12" sludge in Septic tank, Peat drains but had 25% ponding in 2 quadrants, it drains slowly when it was turned and broken up in all 4 quadrants. Owne has worked to improve runoff around system and reduce infiltration.Roof is slightly saging close to stopping the tipping tray. Pump run time 482:07:10 vs 420:39:40 -last year approx 62 hour reduced from 80 hours running prior year- Doses 28,258 vs 24.631 last year= 3627 cycles vs 4766 cycles prior year- appears to have reduce infiltration by 25% but may still have some issue with infiltration. cleaned effluent filter and alarm and pump work, changed the battery in control box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/30/2023 | 09:30 AM
03/06/2023 |  | Routine/Scheduled | 136-07-0084 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level. Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | 10:15 AM
03/13/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | BEST1 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Sludge level-1-2" Scum layer on top- 27" Sludge layer on bottom- Treatment has good aeration and a Trace sludge- Discharge has 1" scum and 8-12" sludge in the discharge zone- Effluent filter Dirty and Cleaned -Alarm test operational. Cleaned blower airfilter. Does not need pumping this year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/23/2023 | 09:30 AM
05/02/2023 |  | RoutineScheduled | 101-10-0340 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Recirc Sand Bed |  | Pump | Gravity | Trenches |  | 150.000000 | ["Auxiliary Filter","Control Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Control Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | 09:10 AM
11/02/2023 | Alternative | Routine/Scheduled | 2016-143-0206 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/02/2023 | 11:20 AM
10/10/2023 | Alternative | Follow-Up | 175-03-0838 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | McKim septic and Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Air blower was replaced and tank was pumped out. septic system is working as it should | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/16/2023 | 11:00 AM
08/01/2023 | Alternative | RoutineScheduled | 166-17-042 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/24/2023 | Alternative | Routine/Scheduled |  | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Outlet tee appears to be intact. Not due for pump out. -Discharge/Pump Tank: Water level normal upon arrival. High level upon departure. Checked and found that discharge pump intake was clogged and contributing to high water level. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Water level should return to normal within 48 hours. Checked and confirmed discharge floats are functioning properly. -Aeration: Water level normal. Flushed and cleaned effluent screen assembly. Not due for pump out. -Air Pump/Blower: Checked and confirmed aerator is functioning properly. Arrestor plate and aspirator tip are missing. -Control Panel: Checked and confirmed components within control panels are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly -Drip Field: Flushed and cleaned vortex filter. Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | Dec 30 1899 9:46AM
03/06/2023 | Alternative | Follow-Up | 061-STS-24826 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Resealed pump tank inlet & outlet risers. Re-used existing risers. Retimed distribution box. The Advantex lid was installed backwards, proposal to be sent to homeowner to correct. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
08/15/2023 | Alternative | RoutineScheduled | Discharge | Pulaski | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - New River | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 10 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/15/2023 | 12:00 AM
08/11/2023 | Alternative | Follow-Up | 175-15-0089 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Replaced Faulty blower Fuji VFC200P-5T/ Tested and functioning properly at this time. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
08/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | keep septic area clean and maintained | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
07/19/2023 | Alternative | RoutineScheduled Component Maintenance | 107-12-0139 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Raised valve box | This AOSS should now return to normal function after having provided the above state routine maintenance | 08/23/2023 | 06:57 AM
07/14/2023 | Alternative | Routine/Scheduled | 151-08-0282 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - at grade - Infiltrators NOT accepting effluent properly. One Chamber appears damaged. - Underground consult. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/17/2023 | 09:15 AM
02/01/2023 | Alternative | Routine/Scheduled | 151-17-0036 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3000 | EcoPod |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 45.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/01/2023 | 05:48 PM
06/15/2023 | Alternative | Routine/Scheduled | 04-160-0560 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/15/2023 | 10:30 AM
07/31/2023 | Alternative | RoutineScheduled | 133-STS-96766 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/16/2023 | Alternative | Reportable Incident Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced E140 effluent pump, brass check valve & 3 control floats. Replaced effluent filter. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/29/2023 | Dec 30 1899 12:05PM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-86725 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/10/2023 | 10:02 AM
07/19/2023 | Alternative | RoutineScheduled Component Maintenance | 175-18-0222 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 08/15/2023 | 01:44 PM
08/15/2023 | Alternative | RoutineScheduled | 10-142-0151 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1250 | Clearstream |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 12:00 AM
12/07/2023 | Alternative | RoutineScheduled | 18-100-0457 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | JEFulbright Septic, LLC | 1942001131 | Jason | Fulbright | 1.000000 | 1000 |  |  | Pump | Gravity | Mound | UV | 450.000000 | [] | [] | NA | Musty | Clear | 7.230000 | 3.800000 |  |  |  | 12/07/2023 | Pump Chamber | 3.000000 |  | 2.000000 | 4.000000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/29/2023 | 03:15 PM
06/06/2023 | Alternative | RoutineScheduled |  | Page | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Auxiliary Filter","Dispersal System Operation"] | ["Dispersal System Operation","Auxiliary Filter","BlowerCompressorAerator Operation"] | [18 empty] | Repaired leak (drip tube) . System is shared with 174 Shady Oak Ln | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/06/2023 | 12:00 AM
07/14/2023 | Alternative | RoutineScheduled | 075-STS-32927 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 |  | EZ Treat |  | Pump | Pressure | Trenches |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | 12:00 AM
03/30/2023 |  | RoutineScheduled | 10-142-0151 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1250 | Clearstream |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 12:00 AM
09/18/2023 | Alternative | RoutineScheduled Component Maintenance | SP-05-501 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | The distribution box lid is damaged and should be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
06/02/2023 | Alternative | Reportable Incident | 061-16-351 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Replaced failed pump and alarm float. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
12/04/2023 | Alternative | Routine/Scheduled | 136-13-0195 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component At normal level Has 3" of solids and 8" of sludge Discharge/Pump Tank Condition of above Component Notes for above Component At normal level Pump and float working properly Pulled and cleaned pump and spin filter Aeration Condition of above Component Notes for above Component At normal level Has 4" of sludge Pulled and cleaned wier and defuser Air Pump/Blower Condition of above Component Notes for above Component Air pump working properly Pulled and cleaned filter Control Panel Condition of above Component Notes for above Component Panel working properly Visual and audible alarms working Drain Field Condition of above Component Notes for above Component Showing no signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 09:34 AM
02/13/2023 |  | RoutineScheduled | 179-STS-91626 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 7386.000000 | [] | [] |  |  |  | 7.530000 | 1.240000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 10:45 AM
04/12/2023 |  | Routine/Scheduled | 18-142-0091 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1060.000000 |  | Purasys |  | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | [17 empty] | System checked. Septic tank needs to be pumped out and refilled. System appears to be operating normally. Aerator: 1086.24, Clearwater: 50.22, sludge: 33.40. Grommets in treatment tank are leaking and need to be sealed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/12/2023 | Jan 1 1900 10:39AM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | 099-12-0001-SR | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | Upon arrival discharge chamber was in low level due to defective off float. Installed new float and completed annual inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
07/25/2023 | Alternative | Reportable Incident | 06-120-0152A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 600.000000 | ["Control Operation","Level Sensor Operation"] | ["Control Operation","Level Sensor Operation"] | N/A | [17 empty] | System reported to have been alarming for 1+ weeks - found discharge timer enable float sensor had failed - system has been operating in demand mode from high level discharge timer float. All discharge float sensors replaced - system due for full service in September. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | Dec 30 1899 7:45AM
03/31/2023 |  | RoutineScheduled | 154-05-0426 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | 12:00 AM
10/05/2023 | Alternative | Routine/Scheduled | 166-05-649 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Found at normal level, 3in of sludge and less than 1in of solids. Pulled and cleaned filter. Tank has multiple visible cracks. -Discharge/Pump Tank: Found at normal level, tested floats and pump all working as they should. Pump chamber showing signs of leaking. No visible cracks but bulging at the bottom. Splices inside tank -Peat Moss: Tipping bucket and trays are in working order. Raked out peat on both sides peat still has life. Unit has shifted and lid doesn't fit 100% correct. There is a crack on the roof of the unit -Control Panel: 120 volts, audio and visual alarms working as they should -Drain Field: No signs of surfacing in drainfield area | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 09:36 AM
06/20/2023 | Alternative | Routine/Scheduled | 234-13-129 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | Dec 30 1899 1:15PM
10/04/2023 | Alternative | RoutineScheduled | 115-05-0384 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Other conventional maintenance performed | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 12000 | Biomicrobics Fast 2.5 |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | YES | [16 empty] | Inspected | Initial Pump draw down test for calculating flow. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | 09:30 PM
04/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/31/2023 | Alternative | Routine/Scheduled | 179-04-047 | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2750 | Microfast | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 20.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/31/2023 | 09:50 AM
04/09/2023 |  |  |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 1.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/09/2023 | 12:00 AM
09/29/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1125 | septic | pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/20/2023 | Alternative |  | 027-STS-15637 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/20/2023 |  | 3.170000 |  |  | 4.530000 |  |  | Will be sent separately |  | BOD: 3.17 DC TSS: 4.53 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/20/2023 | 12:00 AM
07/06/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | Dec 30 1899 12:46PM
03/03/2023 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | [28 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 01:25 PM
09/27/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Multiflo FTB |  | Pump | Gravity | Trenches |  | 450.000000 | ["BlowerCompressorAerator Operation","Distribution Pump Operation"] | BlowerCompressorAerator Operation | N/A | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/12/2023 | 12:45 PM
10/02/2023 | Alternative | RoutineScheduled | 154-05-1039 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2000 | Puraflow - 4 Pods |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Auxiliary Filter"] | NA | Musty | Clear | [14 empty] | Inspected | Sludge/Scum accumulations - Septic 4" sludge, Pump Station 0". Peet Moss raked - good condition Deck posts blocks the ability to open the control panel. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/02/2023 | 12:00 AM
02/09/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity |  | UV |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | 7.100000 | 6.400000 |  |  |  | 02/09/2023 |  | 8.000000 |  | 1.800000 |  |  |  | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/15/2023 | Dec 30 1899 12:05PM
04/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/11/2023 | Alternative |  | 124-STS-2379 | Richmond City | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Rejected | EHD - Three Rivers | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 1.000000 | 1500 | 1500 |  | Pump | Pressure | Discharge | UV |  | [] | ["Attached Growth Medium","Control Operation","Disinfection","SludgeScum Accumulation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles"] | YES | Pungent | Cloudy | 9.000000 |  | 4.000000 | [13 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/11/2023 | 10:00 AM
10/02/2023 | Alternative | RoutineScheduled | 151-13-0080 | Lancaster | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | replaced float, system check - okay, peat saturated | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12:00 AM
07/24/2023 | Alternative | RoutineScheduled | 145-18-0008 | Highland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | AdvantexAX20RT | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | YES | [7 empty] | 07/24/2023 | Pump Chamber | 2.000000 |  |  | 1.300000 |  |  | Attached to this report | Pumped Out | The effluent filter was pulled and cleaned. The AdvantexAX20RT unit was pumped out and cleaned. The unit was then refilled with fresh water to inshore a fresh restart. The textile sheets were sprayed off and cleaned. The recirculating and discharge pumps were both pulled and cleaned. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | 03:40 PM
05/31/2023 | Alternative |  | 16-160-0188 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 | 1500 | Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/15/2023 | 12:00 AM
01/11/2023 |  | RoutineScheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [7 empty] | 01/11/2023 |  | 68.000000 | [5 empty] | Will be sent separately | Inspected | Peat ponding needs replacement Replaced sample port lid | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/18/2023 | 04:10 AM
05/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Ecoflo is in poor condition. There is severe root infiltration and a large amount of ponding. The homeowners are going to take the path of replacing the Ecoflo with a modern treatment unit. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
12/12/2023 | Alternative |  | 91-184-5002 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/12/2023 |  | 3.860000 |  |  | 4.000000 |  |  | Will be sent separately |  | BOD: 3.86 TSS: 4.00 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 12:00 AM
12/21/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Norweco | Pump | Pressure | Drip |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","SludgeScum Accumulation","Level Sensor Operation"] | [18 empty] | Hard thick layer of scum on top, Cant get a reading on sludge. Recommend pumping. They had it pumped of 1/4/2024. Cleaned all filters. pump, floats, high water alarm working. Aerator is not working, They had it changed on 1/10/2024. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/13/2024 | 09:45 AM
05/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
05/20/2023 | Alternative | Routine/Scheduled | 127-STS-32857 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Leave septic power on or flip septic breaker in the house to power the septic panels. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/20/2023 | Dec 30 1899 11:30AM
04/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/11/2023 | Alternative | RoutineScheduled | 099-14-0043-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Elite Onsite | 1942001726 | Drew | Saunders | 2.000000 | 1500 | 1000 | 500 | Pump | Pressure | Mound | Not Applicable | 200.000000 | ["Effluent Screens","BlowerCompressorAerator Operation"] | ["Effluent Screens","BlowerCompressorAerator Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/13/2023 | 05:25 PM
08/08/2023 | Alternative | Routine/Scheduled | 07-118-0028 | Charles City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/08/2023 | Dec 30 1899 10:33AM
02/22/2023 | Alternative | RoutineScheduled | 115-07-0522 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 12000 | Dual Biomicrobics Fast 2.5 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Level Sensor Operation","Control Operation","Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Effluent Screens","Level Sensor Operation","Control Operation","Auxiliary Filter","BlowerCompressorAerator Operation"] | YES |  |  | 7.300000 | 8.800000 |  |  | 15 | 02/23/2023 | Pump Chamber | [7 empty] | Inspected | Septic Tank #1 Sludge levels- 1-2" scum and 16" light sludge trace ( tanks were pumped in august), septic tank #2 minimal scum and 10-12" light sludge trace- Fast treatment unit has good Aeration Fast #1 6" sludge trace and Fast #2 trace-" sludge. The system tanks were pumped 2 visita ago. Cleaned blower airfilter, Good Aeration observed from both Blowers, cleaned all the probes. One probe TSS in for replacment. Took Ph and Do Readings. Cleaned both Effluent screens. Treatment unit #1 7.7 DO and 6.6 pH. Treatment unit #2 7.1 DO, pH 7.1. pH . In pump tank Ph was 7.04 @ 18.8c - Effluent meter reading 6541110 Previous 6399314 previous 6325462. Over 83 days, The current flow 141,796 Gallons or 1,708 Gallons per day on average. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/23/2023 | 09:30 AM
06/06/2023 |  | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | DeHaven's Backhoe Service Inc. | 1942001541 | Wayne | Edmonson | 1.000000 | 1500 | Aquarobic |  | Pump | Gravity | Mound | Not Applicable | 175.000000 | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | NA | [17 empty] | Replaced diffusers in tank unstopped manifold on top of the mound | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/12/2023 | 08:00 PM
08/02/2023 | Alternative | RoutineScheduled Component Maintenance | 061-STS-27116 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Control Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Control Operation"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Annual inspection. Observed check valve on pump #1 leaking externally (rotten) during 1st test cycle. Removed pump to change the check valve and discovered that the pump was 28 years old. Replaced both pumps (duplex setup), brass check valves, and camlocks. Cleaned very dirty globe valves. Flushed laterals, balanced as best as possible. Some laterals obviously still have some clogged orifices (as evidenced by the higher effluent levels in some of the clear riser test pipes). There is nothing to suggest that the field is suffering from the unequal distribution and there is no cleaning method guaranteed to clear the orifices (especially if clogged with small roots). System is considered to be working fairly well considering its age and lack of pretreatment. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
08/23/2023 | Alternative | Routine/Scheduled | 96-142-0592 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine service Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Biofilter - 4 modules - Peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | Dec 30 1899 9:30AM
12/19/2023 | Alternative | RoutineScheduled Component Maintenance | 177-10-0096-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Distribution Pump Operation" ,"Dispersal System Operation"] | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
05/17/2023 |  |  |  | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Puraflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/02/2023 | 12:00 AM
11/08/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | Western Virginia Water Authority | 1942001145 | Michael | Doss |  |  |  |  | Gravity | Pressure | Drip | UV |  | [] | [] | NA | None | Clear | [5 empty] | 11/08/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 01:55 PM
03/07/2023 |  | Routine/Scheduled | 041-STS-258018 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. BioFilter - Peatmoss is in fair condition - raked / turned. Pump Basin - float sensors, pump and controls operating. DBox - on adjoining property - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/08/2023 | Jan 1 1900 10:15AM
09/19/2023 | Alternative | Routine/Scheduled | 03-160-0128 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/19/2023 | 06:00 PM
02/15/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
09/15/2023 | Alternative | RoutineScheduled | 09-125-052 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Pump | Pressure | Drip | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens","Recirculation Pump","SludgeScum Accumulation","Septic Tank Baffles"] | ["SludgeScum Accumulation","Septic Tank Baffles","Recirculation Pump","Level Sensor Operation","Effluent Screens","Distribution Pump Operation","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/15/2023 | 12:00 AM
12/13/2023 | Alternative | RoutineScheduled | 08-197-A2 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Multiflo |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/13/2023 | 12:00 AM
09/04/2023 | Alternative | RoutineScheduled | 171-16-0002 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 14" of accumulated solids in septic tank. Cleaned septic tank filter. Flushed treatment unit spray manifold. 10" of solids in recirculation portion of treatment unit. 8" of solids in discharge portion of treatment unit. Cleaned recirculation pump intake screen. Tested floats, pumps and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/24/2023 | 07:03 PM
09/25/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/25/2023 | Dec 30 1899 2:30PM
11/07/2023 | Alternative | Routine/Scheduled | 06-120-0597A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Ecoflo |  | Gravity | Gravity | Trenches |  |  | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/07/2023 | Dec 30 1899 8:47AM
01/05/2023 |  | RoutineScheduled | 175-12-0069 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 02:21 PM
02/28/2023 |  | Reportable Incident | {FIPSCode}-STS-1787 | Chesapeake | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Chesapeake | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 2500 | Cajun Aire ATU |  | Pump | Gravity | Discharge | UV | 1000.000000 | Disinfection | ["Disinfection","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Pumped primary and secondary septic tanks to effect repairs, remove roots and re-parge seams as noted in previous inspection report. Replaced failed Salcor UV system with new Norweco AT1500 UV system. Replaced all float sensors and installed direct discharge signage. | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 03/01/2023 | Jan 1 1900 10:30AM
03/02/2023 |  | Reportable Incident | SWP-03-784 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Septic Tank Baffles" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Septic Tank Baffles" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Complaint inspection. System was on peak level due to both backwash valves stock open. replaced both valves and diaphragm for filter # 2 valve. System back and working. Cleaned both disc filters and 90 screen filter. Drip flow slow due to system having to much solids in it. Control panel for blower was bypassed. Enabler float takes long time to open recommend replacing. Both tanks need pump out due to sludge levels. spongy spot-on drip field but no water above surface. System needs: Both tanks need pumping. Control panel for air blower. Drip field needs bleach flush. Enabler float. Will send proposal for repairs. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
09/08/2023 | Alternative | RoutineScheduled | 181-17-0148 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | AdvantexAX20RT | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The textile sheets were sprayed off. The recirculating pump was pulled and sprayed off. The controls were operating as designed. The pump timer was adjusted to suit the number of residents. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | 09:30 PM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance | SD-03-111 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
10/19/2023 | Alternative | RoutineScheduled Component Maintenance | 175-14-0093 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
10/23/2023 | Alternative |  | 099-14-0066-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/27/2023 | Alternative | Routine/Scheduled | 08-120-0495A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Hoot |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Treatment tank needs pumping | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/27/2023 | Dec 30 1899 9:32AM
10/18/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out. -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Not due for pump out. -RSV (Recirculating Splitter Valve): Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact. -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | Dec 30 1899 11:43AM
11/13/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/25/2023 | Alternative | RoutineScheduled | 195-STS-26918 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | YY Services LLC | 1965006418 | Brian | Stewart | 2.000000 | 1000 |  |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | [] | [] | NA | None | Clear | 7.000000 | 1.500000 | 0.000000 | 2.000000 |  | 07/25/2023 | Sample Tap | 7.910000 |  |  | 12.600000 |  |  | Will be sent separately | Pumped Out | EMI results on hand if needed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/14/2023 | Dec 30 1899 11:20AM
12/13/2023 | Alternative | RoutineScheduled | 181-12-0021 | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 5.000000 | 7000 | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","Effluent Screens","SludgeScum Accumulation"] | ["Auxiliary Filter","Effluent Screens"] | [17 empty] | Pumped Out | Filters and screens checked and cleaned. Pumped treatment units and pump tanks. Control panels, floats, and pumps all functioning properly. There were no apparent leaks in system or drain field area. Lids were properly secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/09/2024 | 07:05 PM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
08/08/2023 | Alternative | RoutineScheduled | 128-14-0062 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned atu filters, replaced pump intake filter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/28/2023 |  | Routine/Scheduled | {FIPSCode}-STS-3839 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | EZ Treat Sandfilter |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/28/2023 | Jan 1 1900 2:00PM
06/16/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Control Operation","Level Sensor Operation"] | ["Control Operation","Level Sensor Operation"] | N/A | [17 empty] | Replaced pump float and over ride float | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/16/2023 | Dec 30 1899 9:00AM
04/28/2023 | Alternative | RoutineScheduled | 06-197-025 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/28/2023 | 12:00 AM
01/13/2023 |  | RoutineScheduled | 05-197-171 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Fast |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/13/2023 | 12:00 AM
11/16/2023 | Alternative |  | 06-184-5001 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/16/2023 |  | 4.740000 |  |  | 3.700000 |  |  | Will be sent separately |  | BOD: 4.74 TSS: 3.70 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | 12:00 AM
09/07/2023 | Alternative | RoutineScheduled Component Maintenance | VAG401694 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | Enviro-Flo | none | Gravity | Gravity |  | Chlorination |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
05/12/2023 |  | Pump-Out Only | 234-14-295 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/12/2023 | Jan 1 1900 11:00AM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/16/2023 | Alternative | RoutineScheduled | 08-197-A15 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 7.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
11/21/2023 | Alternative | Routine/Scheduled | 45500 | Clarke | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches |  | 600.000000 | ["Auxiliary Filter","Level Sensor Operation"] | ["Auxiliary Filter","Level Sensor Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/22/2023 | 11:44 AM
07/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 07/25/2023 |  | 9.000000 | [5 empty] | Will be sent separately | Inspected | Pumped by another company Replaced bad blower panel | This AOSS should now return to normal function after having provided the above state routine maintenance | 09/20/2023 | 01:07 PM
03/03/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower connection was repaired. System appears to be functioning as designed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
09/05/2023 | Alternative | RoutineScheduled Component Maintenance | 177-07-0131-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend treating the area around the Puraflo Modules for ants. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
11/29/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | [18 empty] | air relief not found in drip area | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/29/2023 | 12:00 AM
09/29/2023 | Alternative | RoutineScheduled Component Maintenance | 175-05-0624 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
08/07/2023 | Alternative | Reportable Incident | 234-15-78 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/07/2023 | Dec 30 1899 3:00PM
09/27/2023 | Alternative | RoutineScheduled Component Maintenance | 099-07-0018-SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Roots in pod, added root destroyer. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
02/13/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["Dispersal System Operation" ,"Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"Auxiliary Filter" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Added riser to inlet | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/13/2023 |  | RoutineScheduled | 153-STS-20306 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter"] | ["Effluent Screens" ,"Auxiliary Filter"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
02/10/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | None | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 09:20 AM
07/06/2023 | Alternative | RoutineScheduled |  | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
08/29/2023 | Alternative | Routine/Scheduled | 550-STS-5876 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | UV is not working, replaced pump | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/29/2023 | Dec 30 1899 9:05AM
09/08/2023 | Alternative | RoutineScheduled Component Maintenance | 179-18-0181-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"SludgeScum Accumulation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | YES | Pungent | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend pumping the septic tank, aerobic treatment unit and pump tank due to scum and sludge accumulation in this tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
10/27/2023 | Alternative |  | SD-15-147 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 12:00 AM
01/20/2023 |  | RoutineScheduled | 003-STS-33876 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 12:00 AM
09/11/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-3859 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 8 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/11/2023 | 12:00 AM
11/08/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/30/2023 | 12:00 AM
03/10/2023 |  | RoutineScheduled | 099-06-0071-SP | King George | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/03/2023 | 08:19 AM
05/03/2023 |  | Pump-Out Only |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Aquarobic Mini Plant | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 01:25 PM
06/28/2023 | Alternative | Routine/Scheduled | 04-172-0277A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & Effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/29/2023 | Dec 30 1899 7:45AM
01/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
01/18/2023 |  | RoutineScheduled | 06-198-066 | Wythe | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Advantex |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Distribution Pump Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Distribution Pump Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | 12:00 AM
10/18/2023 | Alternative | Routine/Scheduled | 151-11-0105 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [16 empty] | Inspected | Full system inspection for REI: -Was there any evidence of back-ups inside the home?: No -Type of System: Advantex Ax20rt -Septic Tank: -Depth to the top of the Septic Tank: 0-12" below grade -Riser present?: yes -Condition of Lid: Intact -Tank Level: Normal operating level: -Condition of Inlet Tee: Satisfactory -Condition of Outlet Tee: Satisfactory -Effluent Filter present? Yes -Effluent filter cleaned at time of service? yes -Media Sheets: -Was the media serviced at time of inspection? yes -Condition of Spray Grids: Satisfactory -Overall function of the Media: Satisfactory -Media Sheets - Additional Notes: Pulled and cleaned biotube filter for recirc pump Pulled and cleaned recirc pump, discharge pump and all floats -Control Panel: -Was the control panel powered at time of inspection? yes -Were alarms tested at time of inspection? Yes -Control Panel - Additional Notes Recirculation contactor is bad -Distribution Box: -Depth to the top of the Distribution Box: 0-12" below grade -Type of Material: Plastic -Condition of Lid: Intact -Distribution Box found: at normal operating level -Condition of Distribution Box: Satisfactory -Number of Drain Lines: 4 Repair (10/19): -Installation of Orenco ABB contactor | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 11:02 AM
05/11/2023 |  | RoutineScheduled | 177-10-0241 SWP | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | NA | Septic | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment looks really dangerous due to blower line coming apart at coupling inside unit, fixed temporarily just to get system going but needs to be glued back together and gasket sealed. Water on top of ground at dripfield due to bad Treatment. Will follow up in about 2 weeks to evaluate tubing and to repair blower line. Will send proposal. Blower 2.99 amps. 18 psi at return. 6/7/23 - MW has reached out to DSS to get update. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/01/2023 | 04:39 AM
04/18/2023 |  | RoutineScheduled | 179-07-0388-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
09/19/2023 | Alternative | RoutineScheduled | 10-100-0526 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | Bio-Coir |  | Pump | Pressure | Mound | UV | 600.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | Shared system with 4379 Ridge Rd. Sludge judge test revealed 4-5 inches from bottom of septic tank. No pumping was needed. System and components are working as designed. UV light is working. Media was in good at the right level and in good condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 09:05 AM
05/03/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | Distribution uncovered on 05/12/2023. System does not have FDV. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | Dec 30 1899 12:05PM
04/23/2023 |  | Follow-Up |  | James City | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 4.000000 | 9000 | None | None | Pump | Pressure | Trenches | Not Applicable | 4000.000000 | ["Dispersal System Operation","Distribution Pump Operation"] | ["Dispersal System Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out | Follow-up - found leaks outside of pump tank - excavation revealed that sometime in the past, someone has made repairs with Non-Pressure rated fittings and eight (8) Fernco fittings - all fernco fittings are leaking. Pumped septic tank and pump tank empty to provide storage. Plan is to excavate and replace plumbing and all NON pressure fittings and Fernco Fittings with proper pressure rated PVC fittings come Monday afternoon. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/24/2023 | Jan 1 1900 10:45AM
04/07/2023 |  | Reportable Incident | 550-STS-5885 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/07/2023 | Jan 1 1900 11:00AM
04/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20377 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
01/03/2023 |  | RoutineScheduled | 179-09-0138-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Pump not pumping the gpm required by manufacturer, recommend to upgrade pump when it goes bad. Replaced riser in sample with a used one that was In better shape. Proposal was giving to upgrade pump. Will send new proposal this year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 09:31 AM
03/15/2023 |  | Routine/Scheduled | 550-STS-6405 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | Jan 1 1900 11:40AM
05/20/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | BioMicrobics MicroFast |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter","Distribution Pump Operation"] | ["Auxiliary Filter","Distribution Pump Operation"] | NA | [17 empty] | Annual inspection. Septic Tank - First section - 14" accumulated solids, Second section - 12" accumulated solids. 6" of solids in discharge pump tank. Removed and cleaned septic tank filter. Discharge pump 2" PVC line cracked at 90 elbow. Repaired on 6-9-2023. Replaced tri-check on 6-12-2023. Excellent treatment quality. Cleaned blower air filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 07:03 PM
06/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | NA | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
04/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/11/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic/atu tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
07/19/2023 | Alternative | RoutineScheduled | 151-16-0007 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned atu filter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/14/2023 | Alternative | RoutineScheduled | 101-STS-92573 | King William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 1.000000 | 1500 gallons | Clearstream ATU |  | Pump | Pressure | Pad | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation","Level Sensor Operation","Distribution Pump Operation"] | ["SludgeScum Accumulation","Level Sensor Operation","Control Operation","Distribution Pump Operation","BlowerCompressorAerator Operation"] | NA | Musty | Clear |  |  | 5.000000 | [11 empty] | Pumped Out | Septic tank less than 1" fog, 28" soft sludge, level in trash compartment high due to sludge accumulation pushing into outlet tee. Pumped trash compartment. Clearstream ATU less than 5% SS. Cleaned pump screen. Pump, floats, alarm, controls operating properly. Drain field surface dry at this time. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/23/2023 | 05:55 PM
10/04/2023 | Alternative | RoutineScheduled | 150-07-089 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Advantex |  | Gravity | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Recirculation Pump","Control Operation","Level Sensor Operation","Auxiliary Filter"] | NA | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | 12:00 AM
06/22/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/27/2023 | Dec 30 1899 11:25AM
03/31/2023 | Alternative | Routine/Scheduled | 159-12-067 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 1.25 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/31/2023 | 03:45 PM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Pad | Chlorination |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | buzzer, new bulb ballast no dechlor tab, Please keep at least 3 in all feeders at all times Replaced blower NO LAB AVAILABLE | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/06/2023 | 08:40 AM
07/18/2023 | Alternative | Routine/Scheduled | 550-STS-6348 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/18/2023 | Dec 30 1899 9:35AM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance | 061-18-332 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | UV |  | ["Disinfection" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The UV bulb is not working and should be replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/03/2023 | 05:43 AM
09/12/2023 | Alternative | Reportable Incident | 136-10-0156 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | -Installation of new Ecopod Blower -Installation of an Ecopod 1" Intake Filter -Installation of a 1" piping intake Filter Assembly -Installation of a Float Tree Assembly to secure existing floats | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | 12:44 PM
06/29/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | [17 empty] | Septic Tank-10"sludge 1"scum/ Microfast-16"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ Pump out required on the Septic-Microfast Tank/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-1499 ETM-76h 30m/ Pump2-1479 ETM-75h 34m/ Peak-26/ High-23 On-3m 5s Off-6h/ No breakout or spongy areas on the LPD Pad Site and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/17/2023 |  | RoutineScheduled | 175-12-0010 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
01/06/2023 |  | Routine/Scheduled | {FIPSCode}-STS-1098 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/06/2023 | Jan 1 1900 11:20AM
05/05/2023 | Alternative | RoutineScheduled | 154-01-0052 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump Station #1: K Rain Valve is sticking. Replacement is recommended Pump Station #3: There is a break in the plumbing between Pump Station #3 & Pump Station #5. We recommend excavating by machine & repairing this. Pump Station #5 There is a break in the plumbing between Pump Station #3 & Pump Station #5. We recommend excavating by machine & repairing this | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
06/30/2023 | Alternative | Routine/Scheduled | 03-160-0510 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable |  | None | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | 12:00 PM
06/14/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 12:00 AM
01/03/2023 |  | RoutineScheduled | 179-13-0239-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium"] | ["Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 09:31 AM
02/17/2023 |  |  | 041-STS-259652 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 3050 | 1200 | 750 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Distribution Pump Operation","Control Operation","SludgeScum Accumulation"] | YES | None | Clear | 7.000000 |  | 7.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/17/2023 | Jan 1 1900 10:15AM
09/12/2023 | Alternative | RoutineScheduled | 085-STS-34449 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/28/2023 | Alternative | RoutineScheduled | SWP-04-266 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 0-6 | 0-0 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear |  |  | 12.000000 | [11 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/28/2023 | 02:00 PM
10/30/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-17112 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | JET |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 15 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/30/2023 | 12:00 AM
05/11/2023 |  | Routine/Scheduled | 127-STS-33673 | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 400 | Fuji |  | Gravity | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Air filter cleaned. Fuji maintenance procedure performed. Fuji pump out procedure performed. System should return to normal operation. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/11/2023 | Jan 1 1900 10:06AM
05/15/2023 |  | RoutineScheduled | 175-05-0078 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/10/2023 | Alternative | Reportable Incident Component Maintenance | 175-04-0023 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed WE20G05P4-21 drip pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
09/12/2023 | Alternative | RoutineScheduled Component Maintenance | 175-06-0334 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
07/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-4"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Puraflo Peat turned in all 5 modules and in good condition/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1- 10739 ETM-96h 18m/ Pump2-10700 ETM-95h 58m/ Peak-53/ High-38/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/01/2023 |  | RoutineScheduled | 177-06-0275-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Media was ponding, augered and started draining. Media showing its age should be evaluated for replacement next year. Distribution box should be dug up and lines camera snake due to roots above ground going into drainfield lines at time of peat replacement. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
11/08/2023 | Alternative | RoutineScheduled | 108-05-0013 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Delta Whitewater |  |  | Pressure | Drip | Not Applicable |  | ["Control Operation","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | [18 empty] | operating as designed. Follow up scheduled to fix leaks in drip field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/08/2023 | 12:00 AM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | fixed air vac audible alarm and psi blower was off Recommend pumping of primary tank | This AOSS should now return to normal function after having provided the above state routine maintenance | 07/06/2023 | 08:40 AM
08/07/2023 | Alternative | Reportable Incident Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Control Operation" ,"Dispersal System Operation"] | ["Control Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced contactor in control panel & repaired broken fittings in hydraulic unit. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/29/2023 | Dec 30 1899 3:58AM
08/25/2023 | Alternative | RoutineScheduled Component Maintenance | 099-15-0094 SR | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Septic Tank Baffles" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. HL-225, LL-37, OVERRIDE-1627. "R" counts back zero. Roots in lower d-box, removed roots and added root-x. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
07/18/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["Other"] | ["None"] | YES | [16 empty] | Inspected | Needs 4 Peat Pods Topped Off | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/12/2023 | 12:00 AM
06/08/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | MicroFast | Pump | Pressure | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [17 empty] | 4" of scum and 8 " of sludge. Pump Tank is clean. Cleaned to blower filter and spin filter. All alarms work. Floats and pump works. Field is dry and has no leaks. 3278 Events 553.15 hrs. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | 10:30 AM
07/07/2023 | Alternative | RoutineScheduled | 005-STS-42606 | Alleghany | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | AdvantexAX20RT | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was cleaned. The textile sheets were sprayed off. The recirculating and discharge pumps were both pulled and cleaned. The spin filter was pulled and cleaned. The controls were operating as designed. There was return effluent returning to the pump tank, so the drip field was operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | Jan 1 1900 9:25PM
01/11/2023 |  | RoutineScheduled | 179-08-0117-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The filter media is clogging and should be cleaned with the Septic Tank, ATU, and the distribution box pumped afterwards. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
10/20/2023 | Alternative | Routine/Scheduled | 136-09-0266 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level Has solids build up around tee -Discharge/Pump Tank: At normal level Pump and floats working Pulled and cleaned pump, removed internal check from pump to prevent air locking -Aeration: At normal level Pulled and cleaned defuser and wier Alarm float working Has 11" of settled suspended solids -Air Pump/Blower: Working properly Pulled and cleaned filter -Control Panel: Visual and audible alarms working Air pump pulling .82amps Discharge pump pulling 7.66amps -Drip Field: Showing no signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 01:43 PM
02/27/2023 |  | Routine/Scheduled | 147-13-0038 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - recommend pumping. Aeration Tank - compressor failure - requires replacing - no mixing. U.V. - serviced bulb and housing. PUmp Tank - float sensors, pump and controls operating. Drip - headworks serviced - have an area of wetness in field present. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/28/2023 | Jan 1 1900 7:30AM
08/18/2023 | Alternative | RoutineScheduled | 099-16-0099 SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | pumped out atu & clarifier, cleaned filters | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/16/2023 | Alternative | Routine/Scheduled | 15-120-0478AR | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/16/2023 | Dec 30 1899 8:52AM
12/20/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 | ["None"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
09/01/2023 | Alternative | Routine/Scheduled | 136-08-0453 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump and effluent screen serviced. Treatment Module - media drapes & spray grid serviced. DBox - plastic - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | 07:30 AM
10/19/2023 | Alternative | Initial Visit | 770-STS-43442 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | None |  | Gravity | Gravity | Mound | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | Initial start-up inspection. Gravity system to a sand mound. Sand mound area approx. 45 by 25. Septic tank not full to date. The septic tank effluent tee has an effluent solids filter. The sand mound does have established grass cover. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/23/2023 | 12:00 AM
04/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/01/2023 |  | RoutineScheduled | 067-STS-37840 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20-RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | Advantex AX20RT -Minimal scum layer and 8" light sludge in septic tank, 6-10" sludge in recirculation zone, 6-14" sludge in discharge zone. No live roots observed and removed a few dead ones in a fitting. Good spray pattern in tank, adjusted settings. Alarm test good, 3 floats operational. Filter was cleaned . Owner if dealing with soil/water infiltration as noted last year around the lid. Recirculation Pump run time 1078.1 hours 79,532 cycles. No ALarms last year in history, Alerts on 3/10 7/31 5/17 and 6/17, Adjusted setting minimaly to reduce alerts. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
07/25/2023 | Alternative | RoutineScheduled Component Maintenance | 099-06-0253-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Septic Tank Baffles" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Cracks in pod, not ideal but since it's a pod site, not super critical yet. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 07:01 AM
11/07/2023 | Alternative | Routine/Scheduled | 08-120-0531 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Hoot |  | Pump |  | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/07/2023 | Dec 30 1899 9:28AM
07/21/2023 | Alternative | Routine/Scheduled | 228-17-0123 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/21/2023 | Dec 30 1899 9:45AM
12/05/2023 | Alternative |  | Discharge | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/05/2023 |  | 21.700000 |  |  | 1.900000 |  |  | Will be sent separately |  | BOD: 21.7 TSS: 1.90 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 12:00 AM
02/27/2023 |  | RoutineScheduled |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 3.000000 | 1500 | 0-2 0-1 0-3 | 0-1 | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear |  |  | 4.000000 | [11 empty] | Inspected | sealed all the tank risers | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/27/2023 | 11:00 AM
11/27/2023 | Alternative | RoutineScheduled Component Maintenance | 175-14-0147 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 09:34 AM
09/07/2023 | Alternative | Reportable Incident | 550-STS-6322 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner had called about the pump won't turn off. Serviced system. Checked the panel and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the relay and wire it through the pump float. Disconnected the pressure switch on the aerator and cut the UV breaker off due to the tanks being pumped the previous day. Replaced the UV light bulb. The timer is set to 2 minutes every 1 hour. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/07/2023 | Dec 30 1899 9:00AM
03/07/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"Effluent Screens"] | ["Disinfection" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | Jan 1 1900 12:26PM
09/26/2023 | Alternative | RoutineScheduled | 027-STS-17468 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Pump | Pressure | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 15 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/26/2023 | 12:00 AM
09/13/2023 | Alternative | RoutineScheduled | 14-197-A4 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | FAST |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","Disinfection","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/13/2023 | 12:00 AM
02/06/2023 |  | Routine/Scheduled | 234-15-302 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | Jan 1 1900 1:05PM
11/08/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-22991 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | CLEARSTREAM |  | Pump | Pressure | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 10 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/08/2023 | 12:00 AM
04/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | An inspection of an alternative septic system. The exterior time dosed septic control panel lights, alarm and wiring were all in good working order. There is a 4" pvc cleanout near the house we ran the camera snake thru to the tank and the sewer line is clear. The septic tank has a plastic riser on the outlet side with a filter. The filter was cleaned. The manufacture recommends the filter be cleaned every 6 months. The tank was sludge judged. That means that the solid level in the tank was measured and does not need to be pumped. The effluent was at the proper level. The pump tank, riser, electric box, floats, pump and force main were inspected. The 5 Puraflo pods were opened up and the peat fiber was inspected. Peat is still in good condition. The black plastic sample box is also good. The 9 port plastic d-box was dug up it was 12" under the ground. All 5 header lines were camera snaked and were clear. The drain field was probed and dry. At time of inspection septic system was in good working condition. This inspection does not guarantee the life of any components, | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
11/13/2023 | Alternative | RoutineScheduled | 2006-143-0137 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/13/2023 | Alternative | Routine/Scheduled | 93-STS-13796 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the both Clearstreams. Changed the diffuser in both Clearstreams and changed the filter in both aerators. There is not tee on the inlet end of the septic tank - needs to be one. Also, there are no risers on the oulet end of the septic tank. The timer is set to 1.75 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | Dec 30 1899 12:00PM
09/14/2023 | Alternative | RoutineScheduled | 167-STS-15451 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 - Blue Crystal tablets installed 6 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/14/2023 | 12:00 AM
05/27/2023 | Alternative | RoutineScheduled | 157-19-0050 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Virginia Septic Solutions LLC | 1942001500 | Justin | Barker | 1.000000 |  | Clearstream 600DC |  | Pump | Gravity | Trenches | Not Applicable | 150.000000 | ["None"] | ["None"] | NA | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/27/2023 | 12:00 AM
10/25/2023 | Alternative | Routine/Scheduled | C800-14-0073 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Aqua Klear |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/25/2023 | Dec 30 1899 2:15PM
03/09/2023 |  | Routine/Scheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  | 600.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/15/2023 | 09:38 AM
10/12/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  | Microfast Drip |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2024 | 12:00 AM
10/11/2023 | Alternative | RoutineScheduled | 2005-143-0098 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Control Operation","Distribution Pump Operation","Attached Growth Medium","Effluent Screens"] | ["Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/19/2023 | Alternative | RoutineScheduled | 2115-06-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.400000 |  |  | 1.600000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
11/29/2023 | Alternative | Follow-Up Component Maintenance | 179-10-0079-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Bionest | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation"] | ["Control Operation" ,"Distribution Pump Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Added flow meter in order to accurately check drip rate and flush rate. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
11/30/2023 | Alternative | RoutineScheduled | 13-184-5003 | Scott | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | Pungent | Discolored | [16 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/04/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Western Tidewater | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.640000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | Dec 30 1899 12:35PM
08/21/2023 | Alternative | Routine/Scheduled | 12-142-0176 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1250 | Multiflo ATU |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [17 empty] | System checked. 6 overrides in last 6 months. System appears to be operating normally. Tree fell on the multiflo and cracked the lid and inside cone. They will need to be replaced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | Dec 30 1899 11:28AM
09/22/2023 | Alternative | RoutineScheduled | 03-125-111 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/22/2023 | 12:00 AM
11/22/2023 | Alternative | RoutineScheduled | 12-163-0045 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Norweco Singulair |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Control Operation","Level Sensor Operation","BlowerCompressorAerator Operation"] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/22/2023 | 12:00 AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
03/17/2023 |  | Routine/Scheduled | 234-16-209 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The aerator should be raised. The UV is not working - needs a new circuit board assembly, cord, bulb, and tube assembly. The septic tank needs to be pumped out and pump the Clearstream as well. The timer is set to 2 minutes every 2 hour. Could not take the 5 year labs due to the UV not working. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/17/2023 | Jan 1 1900 10:45AM
04/18/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | 12:00 AM
02/07/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
08/17/2023 | Alternative | RoutineScheduled | 182-09-0316 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Best 1 |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Septic Tank Baffles","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Septic Tank Baffles","Dispersal System Operation"] | [18 empty] | filters cleaned. broken pump line repaired | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/06/2023 | 12:00 AM
02/24/2023 |  | RoutineScheduled | SWP-03-534 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Leak on recirc tank outlet riser (roots growing inside). Bad bottom float in recirc tank. Leak on pump tank riser. 90 percent of sheet hangers are cracked or broken plus sheets stretched (recommend to replace them with new style) or replace hangers and cut sheets as needed. Unit needs new gas struts and vent cap. Customer had both tanks replaced by others. Customer said discharge pump went bad so it was replaced by others also 3 new floats were installed same day. Adjusted run time due to new gallons per minute on new pump. DISCHARGE: OVERRIDE 2526. RECIRC:OVERRIDE 1388. CUSTOMER WANTS PROPOSAL FOR REPAIRS. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
05/24/2023 |  | Routine/Scheduled | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Recommend pumpout and refill. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | Jan 1 1900 11:30AM
03/04/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 2000 | Orenco Advantex |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | YES | [17 empty] | Annual inspection. Septic tank - 2" crust, 2" of accumulated solids on the bottom. Cleaned septic tank solids filter. Flushed drip manifold spin filter. Flushed treatment unit spray manifold. Tested floats, pumps and alarm,. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 07:03 PM
07/25/2023 | Alternative | RoutineScheduled |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Prince William | Dabney & Crooks, Inc. | 1942001489 | Robert | Fessler | 2.000000 |  | Pura Flo |  | Pump | Gravity | Pad | Not Applicable | 500.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | 12:00 AM
02/23/2023 |  | RoutineScheduled |  | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 2.000000 | 1500 | Biomicrobics Micro-Fast |  | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation"] | [] | NA | [16 empty] | Inspected | New Client -1st Yearly visit- Routine Inspection - System was installed by smith Farris Last year and started up then working but tanks empty- I return today for the yearly inspection - System has not been used and tanks are still empty of water or filled to lowest level. Tested pump and alarm and float swiutches and all operational. Tested blower cleaned airfilter, checked alarm all functional. Need water added to all tanks but appear as new and unsed and fully opperational. Good aeration heard through observation port and trough looks dry but okay, water level not submeging pipe or media.Reccomended to owner to run water to fill as needed and check level upon completion. System has 3-4 tanks each over 1000 Gallons so will take time to fill up on well water with minimal use. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/24/2023 | 09:30 AM
09/18/2023 | Alternative |  | ST-05-599 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
04/20/2023 | Alternative | RoutineScheduled | 015-STS-338151 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | UV |  | ["Auxiliary Filter" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 04/20/2023 |  | 8.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
05/16/2023 |  | RoutineScheduled |  | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Septic Tank minimal scum and 6-8" sludge trace, 10" sludge in discharge. Clean Bio-filter, pulled RSV, Good spray pattern in box, Ran system in test mode, Alarm opperational, Need to replace alarm float, other floats operational, 3,365.4hours on recirc pump run time and 60,782 cycles | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/30/2023 | 09:30 AM
04/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/10/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel |  | 1 | 1 |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Sulphitic | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/12/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-03-134 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Found roots inside D-box coming in from top line (line #1) closer to trees, removed root and apply Root-x. Recommend applying Root-x at least once a year until trees are taking down. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
09/19/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | ATU control panel replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
09/19/2023 | Alternative | Routine/Scheduled | 157-12-0064 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream. Changed the filter in the aerator. The timer is set to 2 minutes every 3 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/19/2023 | 09:45 AM
08/22/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20373 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
05/18/2023 | Alternative | Routine/Scheduled | 179-19-0041 | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 40.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/18/2023 | 04:57 PM
06/28/2023 | Alternative | Routine/Scheduled | 151-16-0144 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3000 | EcoPod |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 35.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 04:04 PM
08/08/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | Dec 30 1899 3:58AM
12/04/2023 | Alternative | RoutineScheduled | 107-10-0181 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/04/2023 | 12:00 AM
11/02/2023 | Alternative | RoutineScheduled | 115-09-0015 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | NA | Musty | [15 empty] | Inspected | Sludge level-minimal Scum level & 6" Sludge in Septic tank. Pump Chamber 6" sludge. Cleaned Effluent screen filter-it was very dirty and floated up. Alarm functional and pump is operational, Peat was replaced recently. Peat was moist and 1 quad had some standing water.. We Turned peat in all 4 quadrants. Drains good. The tipping tray was ok. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 05:30 PM
12/07/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/07/2023 | Dec 30 1899 2:30PM
11/04/2023 | Alternative | RoutineScheduled | 181-06-0267 | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Valley Soil & Environmental Consulting, LLC | 1942001218 | John | Lam | 1.000000 | 1000 | Septic tank |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["Distribution Pump Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation"] | ["Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | [17 empty] | Replace LPD pump, control panel, and system floats. Installed Orenco S2 control panel, Liberty FL102M-2 1HP pump, system control floats, float tree, and electrical disconnect. LPD pump: 9.10 amps; Lot 10: measured 12" solids-recommend replacing toilet flapper valve. Recommend replacing access lid at LPD pump tank with old style EZ-Set lid. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/01/2023 | 12:00 AM
04/25/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
12/14/2023 | Alternative | Routine/Scheduled |  | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | 09:30 AM
02/06/2023 |  | Routine/Scheduled | {FIPSCode}-STS-2143 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | Jan 1 1900 11:53AM
04/14/2023 | Alternative | RoutineScheduled | 105-15-0002 | Appomattox | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Central | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1500 | Septic Tank | Aqua Safe - Singulair 960 ATU 600 GPD | Pump | Pressure | Mound | Not Applicable | 600.000000 | ["Effluent Screens","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | The aerator needs to be replaced, it is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/14/2023 | 10:00 AM
04/20/2023 |  | Initial Visit | 550-STS-6307 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 3.000000 |  | 5.000000 | [5 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the UV light bulb. The timer is set to 1.5 minutes every 2.5 hours. Took BOD and Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/20/2023 | Jan 1 1900 2:30PM
03/30/2023 |  | RoutineScheduled | 179-16-0421-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 2-6 | 0-2 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear |  |  | 15.000000 | [11 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 02:00 PM
10/18/2023 | Alternative | RoutineScheduled | 02-197-188 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  | ["Disinfection"] |  |  | None | Clear | 6.500000 | 7.000000 |  | 0.000000 | [11 empty] | Need de-chlorinator tablets | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
07/12/2023 | Alternative | Routine/Scheduled | 08-174-0149 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Puraflo |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/12/2023 | Dec 30 1899 2:58PM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/30/2023 |  | Follow-Up | 175-13-0135 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Installed new sample box, UV cord & bulb. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
07/05/2023 | Alternative | RoutineScheduled Component Maintenance | 175-05-0086 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | S.A.P. inspection for pool installation. Air filter was recently replaced by the regular service provider. Tank was pumped less than 5 years ago, does not need pumping again yet. Owner indicated that they had recently lost some willow trees to willow slugs and are looking into getting replacement trees. Filterbed shows no signs of banding, has no soft or soggy spots. In the short term (until trees are planted), it is expected to continue operating fine. Blower was running at 2.68 amps and aeration pattern looked okay. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
09/09/2023 | Alternative | RoutineScheduled Component Maintenance | 177-07-0079-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Recirculation Pump" ,"Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Recirculation Pump" ,"Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
06/14/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | Dec 30 1899 12:05PM
04/26/2023 |  | RoutineScheduled | 05-192-144 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 11 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/26/2023 | 12:00 AM
08/30/2023 | Alternative | Reportable Incident |  | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Attached Growth Medium | Attached Growth Medium | YES | [16 empty] | Pumped Out | Biofilter media replacement. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/06/2023 | 08:30 AM
12/18/2023 | Alternative | Reportable Incident Component Maintenance | SWP-02- | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite after a heavy rain fall. We received multiple emails stating the system was in high level. We found the inlet riser on recirc tank is leaking and the rsv pipe is leaking ground water into the pump tank. Proposal to be sentt to correct the infiltration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
04/11/2023 |  | RoutineScheduled | 175-05-0735 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/17/2023 | 12:44 PM
03/15/2023 |  | RoutineScheduled | SWP-05-89 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 2.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. 2 puraflow pods have corners burned, recommend to repair or replace when peat gets replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
06/05/2023 | Alternative | Routine/Scheduled | 234-18-244 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Drip | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. U.V. - bulb and housing serviced. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | Dec 30 1899 7:15AM
03/02/2023 |  | Routine/Scheduled | 07-120-0542A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Pressure | Drip |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/02/2023 | Jan 1 1900 5:08PM
12/03/2023 | Alternative | Routine/Scheduled | 093-13-0058 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Outlet tee appears to be intact. Due for pump out. Refill not required -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed transducer is functioning properly. Flushed and cleaned vortex filter. No quick disconnect union for discharge pump -Aeration: Water level normal. Flushed and cleaned weir. Airline is non-serviceable. Due for pump out. Refill is required for proper operation and to prevent damage to components -Air Pump/Blower: Checked and confirmed aerator is functioning properly. Flushed and cleaned aerator air intake filter -Control Panel: Audible alarm is not functioning properly. Visual alarm is not functioning properly. Panel door is broken. -Drip Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 9:15AM
04/12/2023 |  | RoutineScheduled | 175-08-0072 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 04:23 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/30/2023 | 10:30 AM
11/21/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | Dec 30 1899 9:34AM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance | 175-13-0360 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Clearstream compressor needs replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/11/2023 | 11:24 AM
02/15/2023 |  | RoutineScheduled | 099-13-0102-SR | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Elite Onsite | 1942001726 | Drew | Saunders | 1.000000 | 1200 | 600 | 600 | Gravity | Gravity | Pad | Not Applicable | 350.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | 07:00 PM
01/25/2023 | Alternative | RoutineScheduled | SD-07-364 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Need to dig up d-box and check for blockage; water level in Fast unit is above normal level. Effluent has quite the noticeable greenish-blue tint to it. Recommend back off a bit on toilet sanitizers. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
09/27/2023 | Alternative | RoutineScheduled Component Maintenance | 175-02-0474 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
01/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
10/03/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | None |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | Meters - A - 950, B -680, C - 910. Tested both discharge pumps in "HAND", both pumping. Still no gallons pumped to drain field. Water has added to model home on Cliffs Drive. Approximately 2,400 gallons added over several days. Owner is looking into pressure testing the force main system again to look for leaks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | 07:03 PM
01/09/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1000 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 02/14/2023 | Sample Chamber | 5.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/06/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  |  |  | 7.830000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 02:00 PM
02/13/2023 |  | RoutineScheduled | 107-02-0362 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  |  | Trenches |  |  | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | dbox lid to be replaced. Septic needs pumping | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | 12:00 AM
02/14/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | timer was set to 0 off | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/11/2023 | Alternative | Reportable Incident | 043-STS-34936 | Clarke | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Other"] | ["Auxiliary Filter","Other"] | NA | [17 empty] | Homeowner called had an alarm going off. This septic system is a microfast drip. When arrived all lids were opened, and pump tank was in high water. The spin filter on the force main in the pump tank was opened up and filter was clogged. Filter was cleaned and pump was turned on and was pumping. But the amount of effluent coming back from the return line that is located in the pump tank was the same volume that was being pumped out. The PSI was set to high and was adjusted. Floats were checked and were working as they should. The septic/atu tank was inspected and found the plastic riser on the atu side cracked from top to bottom and small roots coming thru. This riser appeared to have been cracked for some time. A new riser needs to be installed on the atu side. The risers are also ground level. But where the tanks are located when it rains the ground water flows over the lids. I would recommend they have risers added to them so they stick up above the ground at least 6 inches. The microfast unit is in a plastic tank. Pictures were taken that we will be getting with microfast about. It looks as though the atu unit is maybe bowing. This system was installed last year by another company. Home owner indicated that they have had been in alarm 17 times. since they moved in. | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/12/2023 | 11:20 AM
07/19/2023 | Alternative | RoutineScheduled | 02-163-0345 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Advantex |  | Pump |  |  |  |  | [] | ["Recirculation Pump","Control Operation","Level Sensor Operation","Attached Growth Medium"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | 12:00 AM
03/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air blower is not working needs replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
04/03/2023 | Alternative | Routine/Scheduled | 800-05-0181 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | Dec 30 1899 11:55AM
03/21/2023 |  | Pump-Out Only | 043190008 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | McKim Septic & Pumping | 1942001330 | Michelle | McKim | 1.000000 | 1500 |  |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Pumped Out | Septic tank pumped out Conventional gravity | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | 03:20 PM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance | 179-07-0236-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 2.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Replaced air filter for blower. Dozing rate in zone 2 is lower than it was few years ago plus has a soft spot, Recommend to bleach flush it. Pump tank needs to be pumped due to solids. Will send proposal for flushing all 3 zones. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
02/22/2023 |  | RoutineScheduled | 177-STS-89388 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | Upon arrival, the air line for the blower had settled and become disconnected. Line was reconnected by the builder. Blower working properly during follow-up visit on 2/27. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
03/14/2023 |  | Initial Visit | 107-13-0005 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  |  | Trenches |  |  | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 12:00 AM
03/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/16/2023 | Alternative | RoutineScheduled | 08-197-A8 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.500000 | 7.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
02/16/2023 |  | Routine/Scheduled | 2009-143-0012 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Supervised pumpout of treatment system by Commonwealth Waste Solutions ... serviced effluent screen, aspirator and drip headworks. Refilled processing tank and pump tank with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 07:15 AM
10/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Need to put power in conduit to panel | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
01/31/2023 |  | RoutineScheduled |  | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock-Rapidan | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Advantex |  | Gravity | Pressure | Trenches | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
05/08/2023 |  | Routine/Scheduled | SD-89-66 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 |  |  | Pump | Pressure | Trenches |  | 450.000000 | None | None | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | 12:33 PM
03/15/2023 | Alternative | RoutineScheduled | 159-17-0219 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Aquasafe |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | [] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
11/17/2023 | Alternative | RoutineScheduled | 06-197-025 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/17/2023 | 12:00 AM
03/06/2023 |  | RoutineScheduled | 107-09-0295 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 1.000000 |  | 0.5 FAST |  | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | YES | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 06:00 PM
06/15/2023 | Alternative | RoutineScheduled | 150-07-0281 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 1.000000 | 1200 gallons | Best 1 |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["SludgeScum Accumulation","Level Sensor Operation","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["SludgeScum Accumulation","Level Sensor Operation","Distribution Pump Operation","Control Operation","BlowerCompressorAerator Operation"] | YES | Musty | Clear |  |  | 20.000000 | [12 empty] | Best 1 trash compartment less than 1" fog, 3" sludge. Treatment unit 20% SS, cleaned effluent screen filter, serviced aerator. Pump, alarm, floats, controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/23/2023 | 06:15 PM
02/27/2023 | Alternative | RoutineScheduled | 154-08-0068 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | The vent cap for the Advantex module is broken and should be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
09/01/2023 | Alternative |  | 139-08-0018 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Robert | Hamblin | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was not functioning. When replacing, recommend lifting the housing. The control panel was having problems and did not appear to be cycling correctly. Parts have been ordered for replacement. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
07/31/2023 | Alternative | Reportable Incident | {FIPSCode}-STS-1983 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/31/2023 | Dec 30 1899 8:30AM
09/26/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation","Attached Growth Medium","Disinfection","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation","Disinfection","Level Sensor Operation"] | NA | [17 empty] | Septic Tank-12"sludge 2"scum/ Microfast-20"sludge (clogged media) Pump Tank-2"sludge/ Chemical cleaning and pump out required on the Septic-Microfast Tank/ UV-Light cord and bulb requires replacement/ Control contactor and timer enable float was faulty and replaced during inspection/ 3 damaged drip valve covers were replaced/ Controls, pump, floats and alarms are functioning properly/ Blower air filter cleaned and blower is working correctly/ Counts: Pump-4234 ETM-906h 39m On-15m Off-3h 45m/Peak-56 ETM-229h 18m Peak Off-2h 57m/ High-30/ Watermeter-0,297,960.26/ No breakout or spongy areas on the drip field and dosing properly. Returned on 10/6/2023: Replaced UV-Light Cord and Bulb/ Chemical cleaning and pump out. System now functioning properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
01/10/2023 |  | RoutineScheduled | 177-07-0219-SWP | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation" ,"Dispersal System Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | There is effluent coming to the ground surface in several areas in the drip field. We recommend contacting an alternative Onsite Soil Evaluator to consider a new dispersal area. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/02/2023 | 07:17 AM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 182-05-0450 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
04/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/12/2023 | Alternative | Pump-Out Only |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | [23 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | Dec 30 1899 3:00PM
11/06/2023 | Alternative | Follow-Up | 136-02-117 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [16 empty] | Pumped Out | * pumped 750 gallons * no solids medium sludge * pumped for Zach to inspect tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 09:35 AM
09/26/2023 | Alternative | Reportable Incident | 175-18-0479 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | [18 empty] | Alarm : Found the Zoeller N-140 pump was faulty. Installed a new Zoeller N-140 pump/ Tested and system is now pumping properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
04/26/2023 |  | Routine/Scheduled | 550-STS-6649 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | Jan 1 1900 8:30AM
10/26/2023 | Alternative | RoutineScheduled Component Maintenance | 2090-04-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Chlorination |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 11/15/2023 | 02:02 PM
01/14/2023 |  | RoutineScheduled | 132-05-0264 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Norweco 960 |  | Pump | Pressure | Mound | Not Applicable | 150.000000 | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/05/2023 | 12:00 AM
11/24/2023 | Alternative | RoutineScheduled | 2099-05-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | 7.400000 |  |  | 1.600000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
11/07/2023 | Alternative | RoutineScheduled | 151-13-0081 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/05/2023 | Alternative | Routine/Scheduled | 15-120-0261A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Aqua Klear |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/05/2023 | Dec 30 1899 8:29AM
04/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Peat fiber is very broken down and sandy needs to be replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
08/24/2023 | Alternative | RoutineScheduled |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Prince William | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 2.000000 | 1530 | Micro-fast |  | Pump | Pressure | Drip | UV | 100.000000 | ["BlowerCompressorAerator Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | System is operational and in compliance with the health department regulations and approved plans. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/24/2023 | 4pm
02/03/2023 |  | RoutineScheduled |  | Alleghany | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Alleghany-Roanoke | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | Jan 1 1900 4:10AM
06/21/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-4588 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Hoot |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [12 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | Dec 30 1899 9:00AM
06/22/2023 | Alternative | RoutineScheduled Component Maintenance | 175-02-0748 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | 11:24 AM
07/14/2023 | Alternative | RoutineScheduled Component Maintenance | 177-07-0379-SWT | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Peat Moss is on its last year it should be replaced before next inspection. Will send proposal for peat replacement. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/18/2023 | 11:45 AM
04/06/2023 |  | Routine/Scheduled |  | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | UV | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. UV - bulb and housing serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | Jan 1 1900 7:15AM
06/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Lower line of the drainfield appears to possibly be hydraulically saturated and allowing effluent to seep perpendicular to the drainfield line. The distribution box lids were damaged by open space bush hogging. Recommended homeowner contact DSS to address the lid issue and the lower line. Recommend checking back in 4-6 months to reassess the lower line | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/19/2023 | Alternative | Reportable Incident | 128-12-069 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm Call: -Came out for a Options consult. Talked with Customer and let her know what we could do. Made options again and sent them over by email. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/06/2023 | 12:41 PM
09/13/2023 | Alternative | RoutineScheduled | 09-197-A3 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | Musty | Clear | 5.500000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/27/2023 | Alternative | RoutineScheduled | VAG408228 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 1.000000 |  | Constructed Wetlands |  | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | NA | None | [16 empty] | Not discharging at time of inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/12/2023 | 09:00 AM
07/05/2023 | Alternative | Routine/Scheduled | 228-16-0058 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | Dec 30 1899 10:22AM
01/05/2023 |  | Routine/Scheduled | 228-04-0270 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/05/2023 | Jan 1 1900 10:30AM
01/11/2023 |  | RoutineScheduled | 033-STS-89642 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/03/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/13/2023 | Alternative | Routine/Scheduled | 151-09-0151 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal level 8in of sludge and 1" solids Pulled and cleaned filter filter is discontinued model No riser on septic tank Infiltration around inlet pipe -Discharge/Pump Tank: Normal level Pulled and tested floats all working properly Pump pulled 9.2 amps No signs of infiltration -Peat Moss: Dispersal trays and tipping bucket are intact Peat moss completely saturated and broken down | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 03:07 PM
07/10/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/19/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/24/2023 | Dec 30 1899 9:25AM
06/03/2023 | Alternative | RoutineScheduled | 133 14 0072 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 10" of accumulated solids in septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. Removed floating solids from recirculation pump area. Cleaned recirculation pump intake screen. 8" of solids in recirculation portion of treatment unit. 6" of solids in discharge portion of treatment unit. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/04/2023 | 07:03 PM
04/13/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | YES | Musty | [15 empty] | Inspected | Scum minimal-sludge 5-6" in Septic zone- Recirculation zone 5" sludge- light color - Discharge basin 12" light color- - Cleaned Biofilter, Brushed and flushed manifold, cleaned RSV, sprayed off media. Flushed system well. Ran in test mode, Alarm functional.A few alarms in history. 3-28-23 & 5-31-22 minimal alerts- toilet running?- All functional - appears biology is improved but continue to minimize chemicals cleaners and sanitizer and antibiotics used on the home drain and sinks to improve system function. odors are improved over last year. System was pumped out last year- No roots observed this year-. flushed until clear after cleaning the media and retested. spray is good. 341.1 hrs vs 193.4 hrs on pump run and 65901 cycles vs 37377 cycles on recirc pump-- 211.6 hrs vs 121.3 hrs and 3659 cycles vs 2122 cycles on discahrge pump. 3 years history. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
06/23/2023 | Alternative | RoutineScheduled Component Maintenance | 175-16-0341 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"Disinfection" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | 11:24 AM
04/05/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump chamber wall appears to be compromised. Homeowner is looking into process of repair. Dwelling in not occupied. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
09/28/2023 | Alternative | RoutineScheduled Component Maintenance | 182-07-0118 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 09/28/2023 |  | 15.000000 | [5 empty] | Will be sent separately | Inspected | Replaced filter Lab sample normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
07/26/2023 | Alternative | RoutineScheduled Component Maintenance | 179-16-0333-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
03/27/2023 | Alternative | RoutineScheduled | SD-13-176 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation"] | ["Control Operation" ,"Distribution Pump Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | Drip rate was high (7.7 gpm) for zone 2 on first test cycle due to the check valve on zone 1 being stuck open (looked like calcium deposits). Replaced brass check valve with plastic ck valve (similar to originally installed valve). High level counter in control panel is at 36. Septic tank is over 50 years old. Recommend replace. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
01/02/2023 | Alternative |  | 101-10-0140 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Seth | Oldham | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/04/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Infiltrator ATL |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge level- sludge trace in Septic tank - Tank level not full yet, No Occupancy- Brand new install, Some fill sand/soil will be added around the septic tank outline, the Treatment drainfiled has no port and appears smooth and dry and grass just planted. Appears it will be fully functional when useage begins. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/05/2023 | 09:30 AM
11/01/2023 | Alternative | Routine/Scheduled | 093-06-0183 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | Dec 30 1899 11:40AM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/13/2023 | Alternative | RoutineScheduled Component Maintenance | 099-11-0040-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Distribution Pump Operation"] | ["Recirculation Pump" ,"Effluent Screens" ,"Distribution Pump Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | As noted on our last inspection, we recommend replacing the Advantex module vent cap. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
01/09/2023 |  | Routine/Scheduled | 196-15-0009 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3000 | EcoPod |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 35.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 05:48 PM
03/09/2023 |  | RoutineScheduled | 179-STS-89977 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
07/18/2023 | Alternative | Routine/Scheduled | 234-17-0332 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/18/2023 | Dec 30 1899 9:05AM
03/02/2023 |  | RoutineScheduled |  | Page | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation","Auxiliary Filter"] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/02/2023 | 12:00 AM
05/02/2023 | Alternative | Routine/Scheduled | 800-11-0275 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | Dec 30 1899 12:15PM
06/23/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-388 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Solids are bridging on the Advantex textile media sheets. We recommend scraping the sheets and pumping the Advantex tank afterwards. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/10/2023 | 10:02 AM
02/16/2023 |  | RoutineScheduled | 179-11-0189-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Effluent Screens"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | As previously noted, we recommend replacing the Monster Box distribution box due to root growth and seals. The peat has settled and is aging. Peat replacement or the installation of a different treatment system may be necessary in the next several years. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
01/04/2023 | Alternative | RoutineScheduled | 061-17-175 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/24/2023 | 08:34 AM
12/07/2023 | Alternative | Reportable Incident Component Maintenance | SWP-01-576 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Hoot | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | None | [14 empty] | Will be sent separately | Inspected | High level alarm 2 days ago, still in peak status today. Backwash valves were not closing completely which allowed some of each dose to recirc back to the septic tank. It also caused the disc filters to get dirty, which in turn, slowed down the drip rate to the zones. Cleaned both backwash valves, the zone return valve and both disc filters and then ran a test cycle for each zone. No further problems found. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
09/05/2023 | Alternative | Routine/Scheduled | 234-18-388 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | Dec 30 1899 9:55AM
01/30/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Microfast needs pumped out. Also need new concrete lid with pump tank and new junction box. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/13/2023 | 11:23 AM
09/05/2023 | Alternative | RoutineScheduled | 07-197-A4 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece |  |  | ATU |  |  |  | Discharge | Chlorination |  |  |  |  | None | Clear | 5.500000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/05/2023 | 12:00 AM
03/30/2023 |  | RoutineScheduled | 07-113-164 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 3 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/30/2023 | 12:00 AM
04/05/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Microfast needs pumping. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/17/2023 | Jan 1 1900 12:44PM
03/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The system appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/27/2023 |  | Pump-Out Only | 228-14-0301 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/27/2023 | Jan 1 1900 2:50PM
10/23/2023 | Alternative | Reportable Incident Component Maintenance | SD-97-164 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | High level alarm. Pump not running due to a failed contactor. Replaced contactor and ran test cycle. Found back wash valves not closing properly and low flush rate. Pump intake was clogged which decreased flow available to properly backwash the disc filters and lowered the flush rate. Also had to clean debris from under the diaphragms in the backwash valves. High level count at 18. Effluent filter was very dirty. Observed numerous wipes in the septic tank (and 2 in the pump tank). Advised owner not to flush any wipes, even those marked safe for septic. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
09/26/2023 | Alternative | RoutineScheduled | 12-197-A2 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 |  | ATU |  |  |  |  | Chlorination |  |  |  |  | None | Clear | 6.500000 | 3.000000 |  | -1.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
05/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/27/2023 |  | RoutineScheduled | 177-18-0057-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | The installer has addressed the settling of the Advantex module. The module is not totally level but the installer indicates that it should not settle further. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
08/09/2023 | Alternative | Routine/Scheduled | 550-STS-6365 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | Dec 30 1899 9:25AM
03/30/2023 |  | RoutineScheduled | 182-17-0047 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Control Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation"] | [18 empty] | repaired alarm. septic/FAST needs to be pumped | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 12:00 AM
10/31/2023 | Alternative | RoutineScheduled | 181-12-0015 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
05/19/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced Salcor head board & UV bulb. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
11/13/2023 | Alternative | RoutineScheduled | 182-12-0081 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 12:00 AM
06/21/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | DSS repaired issues with junction boxes. The system should return to functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/27/2023 | Alternative | Reportable Incident | 147-11-0051 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Pressure | Drip | UV | 450.000000 | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | System alarming high level - been in alarm since 06/23 - Found drip screens clogged and discharge pump "ragged" Serviced screens, serviced pump, owner declined pumping. System still in high level alarm on departure - should pump down given time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | Dec 30 1899 10:30AM
04/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/20/2023 | Alternative | RoutineScheduled Component Maintenance | 177-08-0270 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Pumper pumped out septic tank. Disassembled components in recirc tank and assisted pumper with proper pump out. Reassembled components and homeowner refilled tank to proper levels. Replaced failed override float in drip discharge tank. Replaced 2 broken fittings in drip field on zone 2. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
04/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/01/2023 |  | RoutineScheduled | 162-14-0062 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Biomicrobics |  | Pump | Pressure | Drip |  | 150.000000 | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | 09:05 AM
01/27/2023 |  | Routine/Scheduled | 11-120-0282AR | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1500 | Norweco Singulair ATU |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Trash chamber pumped out Blower shaft was found disconnected, it was reattached. Dirt needs to be added to top of tank and low spot near tank. Power wire needs to be buried | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/27/2023 | Jan 1 1900 11:42AM
06/28/2023 | Alternative | Routine/Scheduled | 033-STS-90453 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 650 |  |  | Pump | Pressure | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 12:00 PM
10/23/2023 | Alternative | RoutineScheduled | 92-100-0801 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | SANDFILTER |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | [] | [] | NA | [17 empty] | SLUDGE JUDGE 5-6" FROM BOTTOM 1-2" FROM TOP EVERYTHING WORKING AS IT SHOULD | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/02/2023 | 11:15 AM
12/03/2023 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Loudoun | SLUSSER, JAMES B | 1934000064 | JAMES | SLUSSER | 1.000000 |  | Best 1 | Septic Tank Only | Pump | Distribution Box | Aggregate Trench | None |  |  | ["BlowerCompressorAerator Operation"] | [18 empty] | [Comments]: Blower was replaced. Air filter was cleaned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2012 | 08:46 PM
07/13/2023 | Alternative | Pump-Out Only | 043-11-0011 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 | [8 empty] | [] | [] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/13/2023 | 12:00 AM
04/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. Compressor needs replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/17/2023 | 12:44 PM
11/28/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-92119 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
11/01/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20300 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
06/13/2023 | Alternative | RoutineScheduled | 143-STS-17493 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1200 | EcoPod |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. Septic tank- 4" crust, 6" accumulated solids on bottom. Excellent aeration. Cleaned blower air filter. 10" of solids in discharge pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 07:03 PM
11/27/2023 | Alternative | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/29/2024 | 12:50 PM
05/23/2023 | Alternative | RoutineScheduled | 14-173-030 | Prince Edward | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 2000 | Septic | Eljen | Pump | Pressure | Mound |  | 450.000000 | ["Effluent Screens"] | ["Control Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation","Level Sensor Operation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/23/2023 | Dec 30 1899 12:45PM
07/10/2023 | Alternative | RoutineScheduled Component Maintenance | SP-04-100 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Ecoflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Peat was ponding, augered and it drained. Alot of slime in septic tank, pump basing and also in Peat that stuff is what causes Peat to pond. Evaluate Peat for replacement next year. Removed roots from pod recommend to add root destroyer in pad every year after Peat replacement. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
08/10/2023 | Alternative | Reportable Incident Component Maintenance | 177-06-0325-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system having a blower alarm due to a failed pressure switch. Replaced switch. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
03/02/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
07/25/2023 | Alternative | RoutineScheduled Component Maintenance | VAG401493 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Gravity | Gravity |  | Chlorination |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
01/02/2023 |  |  | 09-192-191 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/02/2023 |  | 2.700000 |  |  | 1.600000 |  |  | Will be sent separately |  | BOD: 2.70 TSS: 1.60 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/02/2023 | 12:00 AM
08/04/2023 | Alternative | Routine/Scheduled |  | Gloucester | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Attached Growth Medium | ["Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Conducted Saturation Test of Tanks to determine any point of infiltration. Septic tank pumped empty - remaining effluent level measured - Normal Rain fall occurring - set up sprinkler system. Evaluated after 4 hours - Septic has leaks at outlet riser, inlet riser and top seam. Peat chamber (concrete) is also leaking. Onsite Evaluation required. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/07/2023 | 10:15 AM
03/29/2023 |  | RoutineScheduled | 04-197-A11 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","SludgeScum Accumulation","Effluent Screens"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/29/2023 | 12:00 AM
05/10/2023 | Alternative | RoutineScheduled | 108-00-0107 (LEGACY ALT. SYSTEM) | Bath | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NO | [17 empty] | The system did not need to be pumped. The blower and spin filter were both cleaned. The controls were operating as designed. There were no visible leaks in the drip field. There was return effluent returning to the pump tank so the drip field was operating as designed. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/06/2023 | 09:40 PM
02/23/2023 |  | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Microfast | Pump | Pressure | Mound | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | owner had tanks pumped before the inspection so no scum and sludge. Checked everything out and found some bad floats. came back and Changed all floats. ran pump verified field was not leaking. Everything working. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/23/2023 | 02:35 PM
08/02/2023 | Alternative | RoutineScheduled | 04-125-163 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/02/2023 | 12:00 AM
10/23/2023 | Alternative | Follow-Up Component Maintenance |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installer came and evaluated pipe and found leaks coming from tank riser and repaired | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
11/09/2023 | Alternative | RoutineScheduled | 166-04-160 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | peat checked, cleaned filters, system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced 2 gauges and valve box lid | This AOSS should now return to normal function after having provided the above state routine maintenance | 09/20/2023 | 01:07 PM
01/09/2023 |  | Routine/Scheduled | 234-12-85 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | Jan 1 1900 9:00AM
12/11/2023 | Alternative |  | 08-113-200 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/11/2023 |  | 5.420000 |  |  | 1.100000 |  |  | Will be sent separately |  | BOD: 5.42 TSS: 1.10 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/11/2023 | 12:00 AM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
02/21/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/05/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Multiflo |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge level-Septic tank 2-4" scum, layer- 6" sludge- try to minimize FOG inout, fat oil grease, Treatment Tank 2"scum on top and 6" slduge with Aspirator-on, Treatment has Good aeration, Alarm Operational,Washed down the riser in treamtnet tank and reccomended to owner to minimze soap, not use antibiotic soap and snaitizers. minimize strong soaps, cleaner and no Oxi or strong cleaning high bubbling soaps. Spreading out wash times over a weak should. deck has about 2 inches of scum. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
09/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/20/2023 | Dec 30 1899 4:30PM
06/27/2023 | Alternative | Initial Visit | 136-02-0290 | Gloucester | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 2000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 750.000000 | ["Attached Growth Medium","Dispersal System Operation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | AOSS - Initial Visit Primary septic tank - normal level - pumped empty for inspection. Secondary septic tank - normal level - effluent screen missing handle and is broken - serviced best able - requires replacing. Pump Tank - float sensors, pump and controls operating. - FIG Tree located on top of tank! Biofilter - 6 Modules - modules and absorption bed located ten (10) feet from tidal marsh - inspection port has 36" of water present - all modules flooded, Peatmoss spent and requires replacing. Owner reports system 20+ years old - NO Known maintenance! | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/28/2023 | 10:30 AM
04/19/2023 | Alternative | RoutineScheduled | 09-160-0229 | Montgomery | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - New River | King's Alternative Septic | 1942001094 | David | King | 2.000000 | 1500 | BioMicrobics Microfast 0.5 |  | Pump | Pressure | Drip | Not Applicable | 200.000000 | ["Effluent Screens"] | ["Effluent Screens"] | NO | [17 empty] | Replaced Effluent filter | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/28/2023 | 12:00 AM
04/10/2023 |  | RoutineScheduled |  | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 2.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 04/10/2023 |  | 186.000000 | [5 empty] | Will be sent separately | Inspected | Pumped all tanks and added topsoil to drainfield | This AOSS should now return to normal function after having provided the above state routine maintenance | 05/22/2023 | 11:15 AM
02/28/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [8 empty] | 1571.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | all tanks pumped | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
07/17/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-1293 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [14 empty] | Replaced aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | Dec 30 1899 10:57AM
12/08/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | MicroFast | Pump | Pressure | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | [8 empty] | 12/08/2023 | Pump Chamber | 4.750000 | [5 empty] | Attached to this report |  | 0 scum, 2" of sludge. Pump tank clean. Blower and blower alarm working. Pump not coming on when I arrived. Talked with contractor. Moved wires around everything started working. Contractor going to look at it. Field is dry. Everything good and working when I left. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2024 | 07:00 AM
10/11/2023 | Alternative | RoutineScheduled Component Maintenance | 179-12-0250-SRWR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Treatment looks very good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
06/10/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 1.000000 | 1000 | [7 empty] | [] | [] |  | Septic | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 12:00 AM
09/07/2023 | Alternative | Initial Visit | 800-STS-15500 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 5.000000 | [7 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream (a lot of paint residue). Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 45 seconds every 2 hours. Took initial BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | Dec 30 1899 3:00PM
06/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Lower line of the drainfield appears to possibly be hydraulically saturated and allowing effluent to seep perpendicular to the drainfield line. The distribution box lids were damaged by open space bush hogging. Recommended homeowner contact DSS to address the lid issue and the lower line. Recommend checking back in 4-6 months to reassess the lower line | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/17/2023 |  | Routine/Scheduled |  | Frederick | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 |  |  | Pump | Gravity | Discharge | Chlorination |  | ["Control Operation","Distribution Pump Operation"] |  | N/A | [16 empty] | Pumped Out |  | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/22/2023 | 12:27 PM
01/30/2023 | Alternative | Reportable Incident | 150-06-379 | King William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Delta Environmental Products, UC Series |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Distribution Pump Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - System reported alarming last 7 days. Found discharge pump failed and plumbing in tank fractured. Replaced discharge pump like for like and repaired plumbing. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/31/2023 | 07:45 AM
03/13/2023 |  | Routine/Scheduled | 08-120-0431A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/13/2023 | Jan 1 1900 3:31PM
04/04/2023 |  | Routine/Scheduled | 2014-143-0040 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Multiflo FTB |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/04/2023 | 05:33 PM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/07/2023 | Alternative | RoutineScheduled | 05-160-0069 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | 3.000000 | 3000 | WHITE WATER |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NO | Septic | Cloudy | [13 empty] | Will be sent separately | Inspected | - RECOMMEND RISER BE INSTALLED FOR PROPER MAINTENANCE ACCESS - RECOMMEND ALL THREE TANKS BE SERVICED | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/13/2023 | 12:00 AM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
02/23/2023 | Alternative |  | 154-06-0440 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Bill | Jackson | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | clogged media cleared effluent pipe dislodge repaired Recommend pumping of tank | This AOSS should now return to normal function after having provided the above state routine maintenance | 01/15/2024 | 10:39 AM
03/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic/atu needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 182-11-0093 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Site pumped by another company. Rechecked still has 12" Sludge notified owner | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
09/13/2023 | Alternative | Routine/Scheduled | 093-11-0155 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | Dec 30 1899 12:30PM
02/02/2023 | Alternative | RoutineScheduled | 154-05-0537 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 3.000000 | 2000 | ECO-Flow |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Auxiliary Filter"] | NA | Musty | Clear | [14 empty] | Inspected | Sludge Scum Levels in Septic and Pump Tanks both below 6" Peat Moss starting to Pond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | 12:00 AM
12/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 12/19/2023 |  | 123.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
03/08/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
08/05/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex AX20RT |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. Cleaned septic tank solids filter. 0" of solids in recirculation portion of treatment unit. 10" of solids in discharge portion of treatment unit. Flushed treatment unit spray manifold. Excellent treatment quality. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/22/2023 | 07:03 PM
10/11/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-573 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Level Sensor Operation" ,"Recirculation Pump"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Defective recirculation pump and bottom float were replaced. New Advantex sheet kit to be installed in the near future. Will also install a new junction box at that time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
07/14/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Replaced timer enable float & UV bulb while on site. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/15/2023 | Dec 30 1899 1:44PM
12/14/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  | Microfast Trench |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 | ["None"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2024 | 12:00 AM
04/17/2023 |  | Routine/Scheduled | {FIPSCode}-STS-5545 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | Replaced UV Bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | Jan 1 1900 1:00PM
09/12/2023 | Alternative | RoutineScheduled Component Maintenance | 175-07-0041 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Sample box risers need replacement. Decking needs removing to inspect Puraflo modules. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | 12:58 PM
05/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend moving the newer tree that is in close proximity to the drainfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Ecoflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/11/2023 |  | Routine/Scheduled | 10-163-0060 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. BioFilter - peatmoss in fair condition - raked / turned. Pump Basin - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/12/2023 | Jan 1 1900 7:30AM
12/04/2023 | Alternative | Follow-Up Component Maintenance | 2105-11-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity |  | UV |  | ["Disinfection" ,"BlowerCompressorAerator Operation"] | ["Disinfection" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced UV bulb & ATU blower. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 12/06/2023 | 09:34 AM
12/27/2023 | Alternative | RoutineScheduled | 065-STS-31149 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Carrington Pump & Irrigation | 1942001121 | John | Carrington | 2.000000 |  | Norweco |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Level Sensor Operation","Distribution Pump Operation","Effluent Screens","Dispersal System Operation","Control Operation","Auxiliary Filter"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-87577 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001236 | Stuart | Lynn | 1.000000 | 4000 | none | none | Pump | Gravity | Drip | UV |  | ["Level Sensor Operation" ,"SludgeScum Accumulation" ,"Control Operation" ,"Disinfection" ,"Dispersal System Operation" ,"Attached Growth Medium"] | ["Disinfection" ,"Dispersal System Operation" ,"Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"SludgeScum Accumulation"] | NA | Musty | Cloudy | 7.200000 | 4.000000 |  |  |  | 09/26/2023 | Pump Chamber | 20.000000 |  | 1410.000000 | 22.000000 | 39.000000 |  | Will be sent separately | Inspected | 7-5-23 Routine serve, start Clean EZ Treat 3 flow last 7 days highs 7,660, low flow 4,847, average 6,612 7-10-23 Checked D6 Telemetry on plant, all alarms functioning 7-12-23 finish clean EZ 3 7-18-23 flow last 7 days highs 7,789 low flow 6,043, average 6,877 7-20-2023 Advantage Pump Out 4,000 7-23-23 Lot 45, Water line rupture, water turned off to three houses, repaired by Danielson backfill 7-24 by SESMAU 7-25-23 EZ treat 2 not running, replaced pump 8-4-2023 Weed Eat Mow 8-7-2023 Lot 23 water meter not working, swapped out for new one 8-7-20 Lot 32 Water Meter stopped reading, replaced, new reading start 253 8-22-23 Lot 43 Water leak repaired at the pressure tank 8-29-23 Routine service flow last 7 days highs 7,492, low flow 6,717, average 6.694 9-19-23 Routine service filters cleaned zones tested, drip field walkover needs mowing flow last 7 days highs 7,866 low flow 6,087, average 7,142 9-23-2023 Lot 11 Replaced damaged lid on tank 9-27-2023 Alarm Call Plant in high level, arrival drip in catastrophic alarm all zones. re set zones calibrated corrected | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | 01:58 PM
03/09/2023 |  | RoutineScheduled | 101-11-0116 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
02/21/2023 | Alternative | RoutineScheduled | 136-01-0625 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Hydro Action |  | Pump | Gravity | Trenches |  |  | [] | ["Control Operation","BlowerCompressorAerator Operation","Distribution Pump Operation","Auxiliary Filter","Level Sensor Operation"] |  | Musty | Clear | [14 empty] | Inspected |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/21/2023 | 12:00 AM
12/26/2023 | Alternative | RoutineScheduled | 2104-06-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | [] | [] | NO | Musty | Clear | 7.700000 |  |  | 1.900000 |  | 12/26/2023 | Sample Chamber | 2.000000 |  |  | 13.600000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/09/2024 | 12:00 AM
04/12/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Puraflo | [6 empty] | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/12/2023 | 12:00 AM
03/06/2023 |  | RoutineScheduled | 175-15-0432 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Blower 3.45. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
12/13/2023 | Alternative |  | 181-04-0254 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Acres of Virginia, Inc. |  | Melvin | Collins | 1.000000 | 1000 | Microfast |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/12/2024 | 12:00 AM
08/09/2023 | Alternative | RoutineScheduled Component Maintenance | 033-STS-90111 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
09/06/2023 | Alternative | Routine/Scheduled | 075-STS-34610 | Goochland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Fuji |  | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/06/2023 | Dec 30 1899 11:46AM
04/21/2023 | Alternative | Routine/Scheduled | C-11-111-0042 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/21/2023 | Jan 1 1900 9:30AM
06/05/2023 | Alternative | RoutineScheduled | 154-06-0467 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Norweco 960 |  | Pump | Pressure | Mound |  | 150.000000 | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | 11:25 AM
11/03/2023 | Alternative | Routine/Scheduled | 127-STS-34823 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [16 empty] | Recommends a pumpout | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/03/2023 | Dec 30 1899 10:00AM
12/02/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 500 | PuraFlo |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 10" of accumulated solids in septic tank. 10" of accumulated solids in septic tank not connected to the treatment unit. 4" of solids in pump tank. Cleaned septic tank solids filter. Raked peat in peat pods. Tested floats, pump and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2024 | 07:03 PM
04/13/2023 |  | Routine/Scheduled | 133 16 0059 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 12:50 PM
08/14/2023 | Alternative | Routine/Scheduled | 157-14-0066 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 2.000000 | [7 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 2 minutes every 2 hours. Took 5 year BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/14/2023 | 10:30 AM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
05/11/2023 |  | Routine/Scheduled | 05-120-0780A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. Dbox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/25/2023 | Jan 1 1900 11:15AM
09/11/2023 | Alternative | Routine/Scheduled | 157-07-0199 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1250 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | None | N/A | [17 empty] | System evaluated for Safe Adequate & Proper - owners wish to obtain permits to install bathroom facilities in detached garage. Will require a Minor Modification Permit be issued to connect to existing onsite facilities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 09:00 AM
06/05/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | DeHaven's Backhoe Service Inc. | 1942001541 | Wayne | Edmonson | 1.000000 | 1500 | Microfast |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 08:00 PM
07/14/2023 | Alternative | Routine/Scheduled | 155-STS-12306 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 11:30 AM
11/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Primary tank pumped | This AOSS should now return to normal function after having provided the above state routine maintenance | 01/15/2024 | 10:39 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/07/2023 |  | RoutineScheduled | 04-197-A4 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation","Disinfection"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/07/2023 | 12:00 AM
12/13/2023 | Alternative | RoutineScheduled | S16-180-0008 | Roanoke | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Fast Biomicrobics |  | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | NA | [16 empty] | Inspected | Sludge levels-- -trace scum/ 12" sludge in Septic tank. 12" in treatment zone. Treatment Tank had no aeration and blower was hot (locked up-pulling 5-6 amps but not running), found the air line had disconnected and due settling and pressure bent the pipe, Returned 12 20-23 to replace blower and repair the plumbing, system returned to normal after. Replaced the main air header line due to the bent pipe to make and glue the fitting tight to blower and no leak exhist anymore. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/28/2023 | Dec 30 1899 9:30AM
04/25/2023 |  | RoutineScheduled | 175-10-0327 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
08/24/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/22/2023 | Alternative | Reportable Incident | 095-STS-6977 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Pad | UV | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Repairs Ongoing - | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/26/2023 | Dec 30 1899 7:00AM
04/13/2023 |  | Routine/Scheduled | 133 16 0131 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable |  | SludgeScum Accumulation | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 10:15 AM
05/15/2023 | Alternative | RoutineScheduled | 115-05-0226 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | YES | Musty | [15 empty] | Inspected | Sludge level-Trace scum and 14" sludge in Septic tank - Trace of sludge in Pump tank. Float switches tested operational. Peat Looks dry yet moist and okay for age- not been used yet this season thus dry. Peat level is lower and is worn/aged -Peat was clumped, broken up and turned in both sides with more roots in the top half. Ttipping tray was normal. Raked all 4 quadrants. Alarm and pump are operational. Cleaned Effluent filter. Blackwidow spirders sprayed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
03/07/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | Jan 1 1900 12:26PM
06/07/2023 | Alternative | Follow-Up Component Maintenance | 179-16-0367-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 2.000000 |  | EZ Treat Sandfilter | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [7 empty] | 06/01/2023 |  | 77.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
04/11/2023 |  | RoutineScheduled | 177-STS-87529 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/18/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | Dec 30 1899 8:50AM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
01/05/2023 |  | RoutineScheduled | 175-07-0143 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 02:21 PM
05/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/03/2023 | Alternative | RoutineScheduled | 99-197-A5 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  | [] |  |  | None | Clear | 7.000000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
05/09/2023 |  | RoutineScheduled |  | Warren | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 1.000000 | 1250 |  |  | Gravity | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Effluent Screens","Septic Tank Baffles","Recirculation Pump","SludgeScum Accumulation"] | [18 empty] | Advantex tank needs pumped out | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/15/2023 | 11:00 AM
01/16/2023 |  | Routine/Scheduled | 234-14-304 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | EZ Treat Sandfilter |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | Jan 1 1900 9:05AM
01/24/2023 |  | RoutineScheduled | 08-192-203 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/24/2023 | 12:00 AM
09/15/2023 | Alternative | Follow-Up Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced Zoner. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
09/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/07/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Microfast compressor bad and needs replaced. Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 12:48 PM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | 165-STS-334204 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Please keep livestock off of drainfield Filter clog cleared | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
10/20/2023 | Alternative | Routine/Scheduled | 800-11-0365 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Puraflo | [6 empty] | Attached Growth Medium | Attached Growth Medium | N/A | [17 empty] | Replaced peat moss | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | Dec 30 1899 9:00AM
03/07/2023 | Alternative |  | 101-08-0092 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Brian | Bennett | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
06/15/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 12:00 AM
03/27/2023 |  | Routine/Scheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Pump | Pressure | Drip |  | 750.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/23/2023 | 12:42 PM
08/01/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Annual, should have about 2 to 3 years left of peat use. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/01/2023 | 12:00 AM
01/24/2023 |  | Routine/Scheduled | 550-STS-6641 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 01/24/2023 |  | 3.000000 |  | 1.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 9:50AM
11/09/2023 | Alternative | RoutineScheduled | 182-18-0332 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [18 empty] | recommend mowing drip field at least once a year | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/09/2023 | 12:00 AM
04/12/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
08/23/2023 | Alternative | RoutineScheduled | SD-13-061 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith |  |  | Septic Tank | Puraflo | Pump | Gravity | Trenches | Not Applicable | 65.000000 | ["SludgeScum Accumulation","Effluent Screens"] | ["Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 08:35 AM
01/19/2023 | Alternative | RoutineScheduled | 103-STS-101197 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [8 empty] | 01/19/2023 | [10 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/18/2023 | Alternative |  | 132-10-0111 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Andrew | Sheridan | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | DSS removed roots and resealed distribution box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/01/2023 | Alternative | RoutineScheduled Component Maintenance | 179-14-0069-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | There are roots growing down the header pipes. One drainfield line is completely blocked. We recommend excavating by machine to remove roots and repair or replace header lines as necessary. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
10/21/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex AX20RT |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. Cleaned septic tank solids filter. 14" of solids in recirculation portion of treatment unit. 10" of accumulated solids in discharge portion of treatment unit. Flushed treatment unit spray manifold. Tested floats, pump and alarm. Excellent treatment quality. A pump out may be necessary in two years. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 07:03 PM
10/30/2023 | Alternative | Routine/Scheduled | 2016-143-0209 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1250 | Puraflo |  | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | Effluent filter cleaned. Filter was clogged. Recommend pumpout at next visit. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 10:51 AM
12/04/2023 | Alternative | RoutineScheduled | 94-184-5001 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 4 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/04/2023 | 12:00 AM
10/30/2023 | Alternative | RoutineScheduled | 03-197-136 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 12 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/30/2023 | 12:00 AM
08/05/2023 | Alternative | RoutineScheduled | 109-13-0354 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Delta Whitewater, DF Series |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 18" of accumulated solids in septic tank. 4" of solids in treatment unit. Cleaned blower air filter. Excellent treatment quality. A pump out of the septic tank and treatment unit are not required at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/27/2023 | 07:03 PM
01/09/2023 |  | RoutineScheduled | 195-STS-26577 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Clearstream |  | Pump | Pressure | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 5 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/09/2023 | 12:00 AM
08/23/2023 | Alternative | Routine/Scheduled | 151-07-0369 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Puraflo | None | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES |  |  |  |  | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/23/2023 | 04:29 PM
03/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/27/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-5677 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Ecoflo | [6 empty] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Replaced Peat Moss | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/27/2023 | Dec 30 1899 7:30AM
03/24/2023 |  |  | 14-120-0354AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 1.000000 | 1000 | 1000 |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Septic Tank Baffles","Level Sensor Operation","Distribution Pump Operation"] | YES | Musty | Discolored | 6.000000 |  | 7.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/24/2023 | Jan 1 1900 11:15AM
06/07/2023 | Alternative | Routine/Scheduled | 17-142-0236 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Treatment Module - recirc - recirc pump, media drapes & spray grid serviced. Treatment Module - discharge - float sensors, pump and controls operating. Pumps to community pump station and absorption field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | Dec 30 1899 11:00AM
01/21/2023 |  | Routine/Scheduled | 149-STS-10962 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | -1.000000 | 450 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/21/2023 | Jan 1 1900 10:30AM
01/13/2023 | Alternative |  | 132-18-0124 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Daniel | Merchant | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/28/2023 | Alternative | RoutineScheduled | 105-10-0054 | Appomattox | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 300 | Best 1 |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | Sludge level-4-5" Scum layer on top- 6-8" Sludge layer on bottom-(does not NEED Pumping this year) Treatment has good aeration, Trace of Sludge, Pump tank has 7" sludge- Observed timer engage automatic one cycle- Blower operational- Cleaned blower airfilter. It was moderatly dirty/dusty. Effluent discharge filter was dirty- cleaned it. level correct- Clear effluent observed, Alarm tested operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
05/23/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Puraflo |  |  |  | Trenches |  |  | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Septic Tank Baffles"] | [18 empty] | Peat getting low in pods | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/23/2023 | 12:00 AM
01/30/2023 | Alternative | Routine/Scheduled | 136 05 187 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - minor root intrusion - removed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | 07:30 AM
02/28/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
10/23/2023 | Alternative |  | 099-STS-92237 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/31/2023 | Alternative | Initial Visit | 166-03-172 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit - Alarm Event. Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. BioFilter - Peatmoss in fair condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/07/2023 | 08:15 AM
12/08/2023 | Alternative | RoutineScheduled | 15-184-5001 | Scott | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.000000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-88976 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Disinfection" ,"Control Operation" ,"Attached Growth Medium"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Disinfection" ,"Control Operation" ,"Attached Growth Medium"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. UV bulb replaced. RECIERC: HL-6, LL-16, OVERRIDE-16. DISCHARGE: HL-8, LL-26, OVERRIDE-2. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
04/24/2023 |  | RoutineScheduled | VAG408329 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] | [18 empty] | Put in workorder to jet lines to unlcog dishcarge line. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/15/2023 | 12:00 AM
02/09/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
01/26/2023 |  | RoutineScheduled | 09-192-184 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/26/2023 | 12:00 AM
06/13/2023 |  | RoutineScheduled | 175-13-0028 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Dispersal System Operation" ,"Auxiliary Filter"] | ["Effluent Screens" ,"Auxiliary Filter"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Hydraulic Unit needs repair. Needs new Heater . Needs new enabler float. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | 12:05 PM
01/13/2023 |  | Reportable Incident | LEGACY | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | COSS - Maintenance - GMP2018-02 Primary septic tank pumped empty by Atlantic Septic Systems. Installed access riser on septic tank. Existing DBox replaced with new 8 port concrete DBox. New PVC header lines installed Spliced to existing conveyance line. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/16/2023 | Jan 1 1900 11:00AM
06/15/2023 | Alternative | RoutineScheduled | SD-09-311 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Septic Tank | PuraFlo | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation","Effluent Screens"] | ["SludgeScum Accumulation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/06/2023 | 12:00 AM
04/12/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
10/16/2023 | Alternative | Initial Visit | 041-STS-261827 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Septic Pro of Virginia | 1942001780 | Eric | Tambourine | 1.000000 |  | FujiClean CEN7 |  | Pump | Gravity | Pad | Not Applicable | 360.000000 | ["Control Operation"] | ["Control Operation"] | NA | Musty | Clear | [5 empty] | 10/16/2023 | Sample Chamber | 37.300000 | [5 empty] | Attached to this report |  | treatment system only operating for 2 weeks. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/25/2023 | Dec 30 1899 12:00PM
02/03/2023 | Alternative | Routine/Scheduled | 159-08-120 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Pad | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. BioFilter - 5 modules - Peatmoss spent - ponding - requires replacement. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | 11:30 AM
03/27/2023 |  | RoutineScheduled | 12-184-060 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | ATL |  | Gravity | Gravity | Mound | Not Applicable | 200.000000 | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/27/2023 | 12:00 AM
07/07/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["Distribution Pump Operation","Control Operation","BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/07/2023 | Alternative | Reportable Incident | 175-18-0362 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Control Operation","Dispersal System Operation","Other"] | ["Control Operation"] | [18 empty] | Service call only: System in alarm due to faulty contactor in the control box. Replaced the contactor and now functioning properly. Counts: Pump-6096 ETM-1704h 13m/ High level-3/ Watermeter-0,425,562.9 System repairs still needed: Replace 2 solenoids in the hydraulic unit NOTED: solenoids in manuel mode until repair is compleated/ Replace 1 cleanout cap and plug/ Replace 1- 24"riser lid. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
08/14/2023 | Alternative | Reportable Incident Component Maintenance | SD-14-230 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation"] | ["Control Operation" ,"Distribution Pump Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | High level alarm. Loose neutral connection at inlet side of pump circuit breaker in the septic control panel caused arcing and tripping of breaker. Installer had incorrectly placed incoming hots and neutral underneath the screws, rather than pinching them behind the little metal plates. Corrected all 3 connections (control and pump breakers) and checked top side of breakers as well. Used cycle start switch to initiate a drip cycle. All components worked correctly, pump amp draw was normal. Advised new owner that Virginia health department required annual inspections of all alternative septic systems. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
03/24/2023 |  |  | 08-142-0299 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Microfast | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
03/30/2023 |  | RoutineScheduled | 06-197-021 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Effluent Screens","Dispersal System Operation","Control Operation","Auxiliary Filter","Attached Growth Medium","BlowerCompressorAerator Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 12:00 AM
11/20/2023 | Alternative | Routine/Scheduled | 151-15-0100 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank Septic main house: Normal level 6" of sludge No filter in septic No signs of infiltration under riser but riser is sealed with spray foam -Trash Tank Trash side of Microfast: Slightly high level due settling of tank Less than 1" of sludge and solids -Discharge/Pump Tank 1 Pump tank and panel: Normal level All floats and pump functioning properly Floats are aged and zip tied to plumbing and hanging in tank Riser not leaking but is sealed with spray foam Panel had 120v All audible and visual alarms are functioning properly Pump pulling 7.7 amps Plumbing is outdated and low in tank -Discharge/Pump Tank 2 Microfast pump tank and panel: Normal level All floats and pump functioning properly However floats are aged Plumbing is leaking, aged and low in tank Riser is leaking 120v to panel All audible and visual alarms are functioning properly Pump pulling 7.8 -Discharge/Pump Tank 3 Lift station pump tank and panel: Normal level Both pumps and all floats functioning properly Pump 1 pulling 8 amps Pump 2 pulling 5.5 amps Floats are aged Riser is leaking -Aeration Treatment: Slightly above normal level due to settling of tank Aerating properly Air blower panel has 120v coming into it All audible and visual alarms are functioning properly Air blower pulled 3.3 amps -Distribution Box Surge box for Microfast: Slightly high level due to tank settling -Community Drainfield: Distribution box 1 concrete at grade in good condition and all lines taking water Distribution box 2 concrete at grade in good condition and all lines taking water Distribution box 3 concrete at grade in good condition and all lines taking water Distribution box 4 concrete at grade in good condition and all lines taking water Worked both valves both functioning freely | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 02:42 PM
04/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ Advantex Recirculation Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NO | [7 empty] | 04/13/2023 | Sample Chamber | 7.000000 | [7 empty] | Septic / Advantex Tank-3"sludge 0"scum/ Pump Tank-0"sludge/ No pump out needed at this time/ Recirc. pump intake cleaned/ AX-20 Serial # 235940-2 Media in good condition/ Controls, pumps, floats and alarms functioning properly/ Counts: Recirc pump-28642/ Recirc pump run time-231/ Discharge pump cnts-628/ Discharge pump run time-152/ Watermeter-6429.7/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/21/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 |  | Puraflow Trench |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | ["None"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | 12:00 AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | EcoPod | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Zone 1+2 solenoids are not functioning correctly. Strongly recommend thinning out vegetation around panels and tank access. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
06/29/2023 | Alternative | RoutineScheduled Component Maintenance | 033-06-0257-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump" ,"Effluent Screens"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
09/19/2023 | Alternative | RoutineScheduled | S-12-111-0081 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 2.000000 | 4500 | Septic Tank Only | Ecopod | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [7 empty] | 09/19/2023 | Pump Chamber | 5.800000 |  |  | 6.700000 |  |  | Attached to this report |  | The system did not need to be pumped. The controls were operating as designed. There were no visible leaks in the leech field. The leech field was brush hogged and cleaned up. The TSS and BOD were within the permitted limits. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | Dec 30 1899 5:15PM
12/27/2023 | Alternative | Routine/Scheduled | 151-91-333 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component Was flooded due to on/off float not working Has less than 1" of solids with 12" of sludge Pulled and cleaned filter Riser is leaking Discharge/Pump Tank Condition of above Component Notes for above Component Was flooded due to on/off float being bad Customer approved to replace both floats on site Confirmed new floats and pump are working properly Peat Moss Condition of above Component Notes for above Component Was flooded due to bad on/off float Tipping bucket and trays intact Peat has failed(customer is working on getting the money to replaced it). Ecoflow riser is leaking causing the Peat to pond water and compact Control Panel Condition of above Component Notes for above Component Panel is new but missing both screws, I had spare screws and put them in the panel door. Alarm working properly Discharge pump pulling 10amps Drain Field Condition of above Component Notes for above Component Plastic dbox was dug up a couple years ago with an excavator because it is about 5ft deep and looked like new. Field showing no signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2024 | 08:37 AM
04/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/24/2023 | Alternative | Initial Visit | 085-STS-33749 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit Trash Tank - normal level Aeration Tank - normal level - mixing present - aspirator serviced. Clarifier - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. DBox - concrete - at grade - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/25/2023 | Dec 30 1899 7:30AM
05/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Strongly recommend clearing the mounds. The vegitation is starting to get larger and thicker closer to the mounds. Machines should not be used and it should be cleared by hand. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/02/2023 | Alternative | RoutineScheduled Component Maintenance | 061-16-335 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for routine inspection. System has leaks on all risers, at the field flush line coming into the pump tank, gromet leaks for blower air line and outlet pipe on pump tank. Floats are to short to get proper storage in the tank between cycles. Two compartment microfast tank needs to be pumped out due to sludge levels on the treatment side of the tank. Homeowner to make arrangments to have the tank pumped out. Proposal to be sent to fix the infiltration on all tanks and replace the floats with longer ones. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
09/13/2023 | Alternative | RoutineScheduled | 051-STS-17202 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-89320 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
02/23/2023 | Alternative | RoutineScheduled | 154-10-0083 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/25/2023 | 12:00 AM
01/06/2023 |  | Routine/Scheduled | 2016-143-0154 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 2000 | None | None | Pump | Gravity | Mound | Not Applicable | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - STE Mound - Routine Service. Primary septic tank - normal level Secondary septic tank - normal level - effluent screen serviced. Pump tank - float sensors, pump and controls operating. Surge / DBox - normal level - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 09:30 AM
05/02/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
06/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/02/2023 | Alternative | Routine/Scheduled | 136-06-0520 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Biofilter - peatmoss spent - requires replacing - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/07/2023 | 12:00 PM
08/11/2023 | Alternative | Routine/Scheduled | 196-05-613 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3600 | Clearstream |  | Pump | Pressure | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES |  |  |  |  | 50.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 05:05 PM
08/22/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-747 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. System was barely out of high level when we arrived due to discharge pump working intermittently, replaced discharge pump with new Champions CPE5-12 (120V). Replaced tricheck-valve due to flapper stock open. Customer is being using RID-X once a month, advised him to stop because Is creating alot of sludge. Customer started using water softeners system due to mineral staining toilets and sinks inside the house but return pipe of system is hooked to sewer line, now is creating problems in septic system. Customer agreed to disconnect and reroute return line. Sheets have what appears to be iron attached To it and makes it hard to cleaned them, hopefully with water treatment system working and return line disconnected from sewer will help stop this problem. Replaced lid on inlet side of recirc tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
01/30/2023 |  | Routine/Scheduled | 550-STS-6594 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | Jan 1 1900 2:00PM
01/11/2023 |  | Initial Visit | 182-01-0242 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Sandfilter |  | Pump | Gravity | Trenches |  |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [18 empty] | sand in good shape. timers adjusted in d boxes. contactor working but has buzz | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/11/2023 | 12:00 AM
01/11/2023 | Alternative | RoutineScheduled | SD-04-455 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Pad | Chlorination |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy |  | 9.140000 |  |  |  | 01/11/2023 | Sample Chamber | 2.000000 | 0.030000 | 1553.100000 | 1.700000 |  |  | Will be sent separately | Inspected | Repairs on adjoining property appear to have crossed pump lines, but there is no evidence of effluent coming to the ground surface. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
03/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2024 | 05:34 PM
11/27/2023 | Alternative | RoutineScheduled | 047-17-296 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 3.000000 | 1000 | EZ Treat |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation","Recirculation Pump","Effluent Screens","Attached Growth Medium"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump","SludgeScum Accumulation","Attached Growth Medium"] | YES | Septic | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/01/2023 | 02:00 PM
06/03/2023 | Alternative | Routine/Scheduled | 041-STS-260852 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 2000 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/03/2023 | Dec 30 1899 11:30AM
10/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
03/29/2023 |  | Initial Visit | 041-STS-259356 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 2500 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit Primary septic tank - buried - no riser access Secondary septic tank - normal level - effluent screen serviced. BioFilter - concrete - peatmoss wet, but not ponding - raked / turned. Pump Tank - float sensors, pump and controls operating. DBox - intact - at grade | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | Jan 1 1900 7:30AM
01/18/2023 | Alternative | Routine/Scheduled | 151-06-0404 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2500 | Puraflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | 07:05 PM
11/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Pad | Chlorination |  | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired blower electrical Added tablets | This AOSS should now return to normal function after having provided the above state routine maintenance | 01/15/2024 | 10:39 AM
04/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/02/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-84055 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Replaced failed UV bulb. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/06/2023 | Alternative | RoutineScheduled | 137-STS-21670 | Orange | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Attached Growth Medium" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | NA | Pungent | Discolored | [13 empty] | Will be sent separately | Inspected | The Septic Tank & Aerobic Treatment Unit should be pumped due to scum & sludge accumulation. A new control panel has been installed by others and turns the pump on 24 times per day. Previously the system ran twice per day. Whomever installed this panel should verify this setting will not harm the drainfield. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/02/2023 | 07:49 AM
05/25/2023 |  | Routine/Scheduled | 2005-143-0048 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump tank - float sensors, pump and controls operating. Biofilter - four modules - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 01:45 PM
03/02/2023 | Alternative | RoutineScheduled | 08-100-0774 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | BIOCOIR |  | Pump | Gravity | Pad | Not Applicable | 600.000000 | [] | [] | YES | [17 empty] | EVERYTHING WORKING AS IT SHOULD. REPLACED FIBER. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/10/2023 | 11:25 AM
08/08/2023 | Alternative | Routine/Scheduled | S 800-19-0041 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | Dec 30 1899 9:59AM
11/28/2023 | Alternative | Reportable Incident | 136-16-0288 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Customer stated system had water standing around it Opened discharge tank and found above normal Level Water to top of riser Located distribution box and turned pump on with timer and water made it to distribution box but after 1.5 minutes the distribution box over flowed This is a timed system and there is signs of leaks. Also noted that the spin filter is not needed as this goes to a distribution box. Gave customer option for saturation test and she approved and paid in full Pump out 11/29: Signs of leaks in system Pump 1000 gallons for storage awaiting saturation test Pump out 12/01: Clearstream Alternative Septic System. Pumped 2000 gallons to completely empty the septic system for saturation test. SAT test 12/01: Set up saturation test to test for water infiltration. Found that all risers had heavy water infiltration and the midseam and inlet and outlet tee of septic tank. The air pump also isn't working. Emailed finance link over for customer to fill out Repairs 12/05: -Installation of a Clearstream Air Pump-Entry of tank to reseal and parge seams and penetrations in tank to prevent further root intrusion and ground water infiltration. No guarantee on longevity. -Installation of 18" Riser on the Septic Tank -Installation of 18" Riser on the Septic Tank -Installation of 24" Riser on the Pump Tank -Installation of 24" Riser on the Pump Tank | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/12/2023 | 02:06 PM
01/16/2023 |  | Reportable Incident | 17-142-0194 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. There was a lot of grease built up on the inlet tee of the septic tank. The timer is set to 8 minutes every 1 hour. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | Jan 1 1900 3:10PM
04/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/17/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None |  | 7.030000 |  |  |  |  | 07/17/2023 | Pump Chamber | 5.000000 |  |  | 4.600000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 10:35 AM
04/26/2023 |  | Initial Visit | 550-STS-6912 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). CLeaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The pipe in the Clearstream is not on grade - needs to be addressed and/or fixed. The risers on the Clearstream have been leaking - needs to be addressed and/or fixed. The UV is burnt up (not installed correctly) - needs to be fixed and/or addressed. The timer is set to 4.5 minutes every 1 hour. Did not take samples due to the UV not working. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/26/2023 | Jan 1 1900 1:30PM
10/04/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20415 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
08/11/2023 | Alternative | RoutineScheduled | 150-17-0135 | King William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Other"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Other"] | [18 empty] | Installed clear stream blower | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
04/19/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Peat fiber is badly broken down. Peat will need replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
07/03/2023 | Alternative | Routine/Scheduled | 228-13-0111 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/03/2023 | Dec 30 1899 10:55AM
11/17/2023 | Alternative |  | -STS-92398 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/04/2023 | Alternative | Routine/Scheduled | 150-17-0003 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Biofilter - peatmoss in good condition - raked / turned. Pump Basin - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/05/2023 | 07:00 AM
04/21/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | Installed EZTreat Step pump, water meter & chip upgrade for control panel. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
04/13/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced filter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
12/14/2023 | Alternative | RoutineScheduled | VAG401937 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] | [19 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/28/2023 | 12:00 AM
07/20/2023 | Alternative |  | 91-197-5001 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/20/2023 |  | 3.980000 |  |  | 5.500000 |  |  | Will be sent separately |  | BOD: 3.98 TSS: 5.50 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | 12:00 AM
08/11/2023 | Alternative | RoutineScheduled | 16-192-024 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | CLEARSTREAM |  | Pump | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 12:00 AM
01/18/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | [] | YES | [17 empty] | Septic Tank-6"sludge 2"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-083460 ETM-0031847/ Pump2-082370 ETM-0035192/ Noted: Puraflo Peat in all 6 modules is deteriorating and needs replacement/ No breakout or spongy areas on the drainfield. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12:00 AM
06/27/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/27/2023 | Dec 30 1899 9:30AM
01/03/2023 |  | RoutineScheduled | 179-07-0027-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"SludgeScum Accumulation"] | ["Attached Growth Medium"] | NA | Pungent | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the Septic Tank due to sludge accumulation in the tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
05/17/2023 | Alternative | RoutineScheduled | 031-STS-29146 | Campbell | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 2.000000 | 1500 | Sandfilter |  | Pump | Pressure | Trenches | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [16 empty] | Inspected | Septic tank #1 2-8" scum and 8-12" sludge, septic tank #2 5" sludge--Pump tanks trace sludge- - Water meter reading 5,150 G - Sand filter was backed up and we called Fallwell Corporation to come repair. System was pumped out completely after our visit. Alarm test good, pump and recirc pump test good. 5/11/23 flow meter 131,830 and 8/8/22 flow meter 920g total flow 130,910 over 276 days and avg of 475 gpd water use. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/30/2023 | 09:30 AM
06/30/2023 | Alternative | Follow-Up | 073-STS-93299 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 10.000000 |  | 19300.000000 | [5 empty] | Took BOD and Fecal samples. Replaced the diffuser in the Clearstream. Pumped out septic tank and trash out of the Clearstream tank. NOTE : BOD was good - Fecal sample was high - system should function properly after service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | 09:30 AM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
04/26/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
08/08/2023 | Alternative | RoutineScheduled | 023-STS-42583 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. 10" of solids in recirculation portion of treatment unit. 10" of solids in discharge portion of treatment unit. Tested floats, pump and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/25/2023 | 12:00 AM
04/25/2023 |  | Routine/Scheduled | NYII-B36RDV | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | Jan 1 1900 2:35PM
03/08/2023 | Alternative | Follow-Up | 159-01-056 | Middlesex | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 2000 | Clearstream | Clearstream | Pump | Pressure | Trenches | Not Applicable | 1500.000000 | ["Distribution Pump Operation","Recirculation Pump"] | ["Distribution Pump Operation","Recirculation Pump"] | N/A | [16 empty] | Pumped Out | Replaced failed Flow Equalization pumps with new Liberty 280 pumps. Replaced flow equalization pump plumbing. Replaced failed discharge pumps with new Liberty FL62M pumps. Owner not present - paid for REPAIRS Only - no service agreement. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/09/2023 | 07:30 AM
06/01/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 12:00 AM
05/01/2023 | Alternative | RoutineScheduled | 03-142-0394 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C & E Mechanical Corporation | 1942001339 | Louis | Timberlake | 1.000000 | 1250 | PremierTech EcoFlo |  | Gravity | Gravity | Trenches |  |  | ["Other","Effluent Screens","Dispersal System Operation"] | ["Other","Effluent Screens","Dispersal System Operation"] | YES | [6 empty] | All peatmoss & gravel were evacuated & replaced at visit | [9 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/25/2023 | Dec 30 1899 1:15PM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 12:05 PM
09/28/2023 | Alternative | RoutineScheduled Component Maintenance | VAG408490 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | UV |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | UV Bulb Replaced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
07/18/2023 | Alternative | RoutineScheduled Component Maintenance | {FIPSCode}-STS-64040 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"SludgeScum Accumulation" ,"Level Sensor Operation" ,"Distribution Pump Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 07:01 AM
04/25/2023 |  | Initial Visit |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip |  |  | ["Control Operation"] | ["Control Operation"] | [18 empty] | drip tubes exposed. follow up on zone valve | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | 12:00 AM
08/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/28/2023 | Alternative | Routine/Scheduled | 800-STS-14992 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | Dec 30 1899 2:10AM
08/17/2023 | Alternative | Routine/Scheduled |  | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service / Upgrades Primary septic tank - installed new access riser. Aeration tank - normal level - mixing present - compressor serviced - installed new access riser. Pump Tank - float sensors, pump and controls operating - installed new access riser. Drip - elevated headworks box above grade - repaired two locations that were damaged - | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | 09:15 AM
12/19/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Fairfax | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks | [8 empty] | 250.000000 | [] | [] | [8 empty] | 12/19/2023 | Sample Chamber | 4.000000 |  |  | 28.000000 | [5 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/30/2023 | 12:00 AM
12/05/2023 | Alternative | Routine/Scheduled | 06-120-0704A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Septic Tank Condition of above Component Notes for above Component Water level normal. Inlet tee appears to be intact. Flushed and cleaned effluent screen. Not due for pump out. Discharge/Pump Tank Condition of above Component Notes for above Component Water level normal. Structural integrity of tank appears to be intact. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. Peat Moss Condition of above Component Notes for above Component Structural integrity of tank appears to be intact. Structural integrity of tipping bucket appears to be intact. Checked and confirmed tipping bucket is functioning properly. Raked and tilled peat moss. Peat moss is in good condition. Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Distribution Box Condition of above Component Notes for above Component Homeowner declined excavation and inspection of distribution box this service. Previous services state that corner of distribution box lid is damaged Drain Field Condition of above Component Notes for above Component Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 9:56AM
10/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Replaced air pre-filter as preventative maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 06:43 AM
02/28/2023 |  | RoutineScheduled |  | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 2.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | alderon board and contractor replaced drip panel needs panel and will be repaired | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | UV bulb was burned out when visit occurred. Bulb was replaced while onsite. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/16/2023 | Dec 30 1899 12:58PM
08/22/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | Dec 30 1899 12:58PM
05/12/2023 |  |  | 2011-143-0078 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Norweco | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out | Replaced on/off float switch | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/05/2023 | 12:00 AM
08/11/2023 | Alternative | RoutineScheduled | 09-117-208 | Carroll | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | R & R Enterprises, Inc | 1942001111 | William | Robinson | 2.000000 | 1375 | AQUA SAFE AS500 |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | Dec 30 1899 12:00AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected | Peat in Puraflo's are in poor condition and units are holding water (6 puraflo units). | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/20/2023 | Dec 30 1899 12:57PM
05/18/2023 |  | Reportable Incident | 234-15-113 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/18/2023 | Jan 1 1900 8:00AM
11/30/2023 | Alternative |  | 001-STS-92314 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | 12:00 AM
05/04/2023 | Alternative | Routine/Scheduled | 05-174-0284 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/04/2023 | Dec 30 1899 11:06AM
11/08/2023 | Alternative |  | 033-08-0136-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/16/2023 | Alternative | RoutineScheduled | 136-02-0617 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Advantex |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Distribution Pump Operation","Control Operation","Effluent Screens","Recirculation Pump","Dispersal System Operation","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/16/2023 | 12:00 AM
06/30/2023 | Alternative | Reportable Incident | 166-14-176 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Trenches | UV | 450.000000 | ["Control Operation","Disinfection"] | ["Control Operation","Disinfection","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Repair - installed new access riser and sealed others. Installed new UV Control panel installed new Orenco single bulb UV system Removed failed Obsidian UV and repaired forcemain. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/05/2023 | 08:45 AM
07/05/2023 | Alternative | Routine/Scheduled | 04-160-0356 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | 11:15 AM
02/20/2023 |  | RoutineScheduled | 179-06-0265-SWP | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Dispersal System Operation"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Pungent | Discolored | [13 empty] | Will be sent separately | Inspected | As noted previously, we recommend replacing the Orenco riser & lid and junction box on the Advantex Tank. We also recommend cleaning the Advantex sheets and pumping the tank afterwards. Additionally, there is effluent coming to the ground surface along the bottom of the drainfield. We recommend excavating by hand to uncover the distribution box to evaluate its condition for repair or replacement. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/03/2023 | 08:19 AM
03/16/2023 | Alternative | Routine/Scheduled | 10-191-0027 | Sussex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Hoot |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/16/2023 | Dec 30 1899 8:53AM
03/28/2023 | Alternative | Routine/Scheduled | S175-11-0046 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | Dec 30 1899 1:12PM
04/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/28/2023 |  | Routine/Scheduled | 19-172-0128A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Processing Tank - recirc - recirc, pump, media drapes & spray grid serviced. Processing Tank - discharge - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | Jan 1 1900 10:00AM
10/04/2023 | Alternative | RoutineScheduled Component Maintenance | 175-04-0724 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Property owner not present at time of evaluation. No access - inside of house. Need to send letter to property owners notifying them they are in violation of 12VAC5-610-80. Discharge of untreated sewage. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | 12:58 PM
10/31/2023 | Alternative | RoutineScheduled | 02-113-304 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | 12:00 AM
12/08/2023 | Alternative | Routine/Scheduled | C08-180-0034 | Roanoke City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/08/2023 | Dec 30 1899 3:45PM
05/08/2023 |  | RoutineScheduled | 177-STS-87277 | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | UV |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Disinfection" ,"Effluent Screens"] | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | The EZ Treat UV light & cord are not working and should be replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/01/2023 | 06:29 AM
09/05/2023 | Alternative |  | 06-197-A9 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  |  |  | 1.000000 |  | ATU | [9 empty] | None | Clear | 7.000000 | 6.000000 | [14 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/05/2023 | 12:00 AM
06/28/2023 | Alternative |  | {FIPSCode}-STS-70987 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
04/04/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
09/05/2023 | Alternative | RoutineScheduled Component Maintenance | 107-06-0773 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
10/17/2023 | Alternative | Routine/Scheduled | 12-142-0146 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/17/2023 | Dec 30 1899 11:17AM
07/25/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/01/2023 | 12:00 AM
04/14/2023 |  | RoutineScheduled | 175-16-0470 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 04:23 AM
10/23/2023 | Alternative |  | 107-01-0804 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/23/2023 | 12:00 AM
10/13/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/01/2023 | Alternative | RoutineScheduled | 067-STS-38685 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | Modified Extended Aeration |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | YES | [17 empty] | Total flow to drain fields June 2023 -294,310 gallons. Average 8,409 gallons per day. All aspects of the system are operational. Wasting of settled mixed liquor from the clarifier to the digester and decanting of supernatant from digester are occurring regularly. Digester scheduled to be pumped out next week. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/04/2023 | 07:03 PM
02/07/2023 | Alternative | Pump-Out Only | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 1.000000 | 1500 |  |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["Other"] | NA | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/11/2023 | Dec 30 1899 1:50PM
09/27/2023 | Alternative | Routine/Scheduled | 157-09-0218 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Found at normal level. 16in of sludge and less than 1in of solids. Riser has root intrusion at casted in section. -Discharge/Pump Tank: Found at normal level, less than 1in of sludge and solids. Teste floats and pump all working as they should. Pulled and cleaned pump and spin filter. Riser showing signs of leaking. There is streaking under the outlet of discharge tank. Pump and floats are aged. -Aeration: Found at normal level, 4in of suspended sludge. Pulled and cleaned weir and diffuser. High level alarm float working properly. High level float is aged. Riser showing signs of leaking -Air Pump/Blower: Pulled an cleaned air filter. Air pressure sensor working as it should. Air pump pulled 1.5 amps. -Control Panel: 120 volts, visual alarm working as it should. Audio buzzer is not. Tested timer. Pump pulled 8.5 amps. -Drip Field: Walked drainfield while pump was running. No signs of surfacing in drainfield area. Located 2 vacuum breakers. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | 03:51 PM
02/16/2023 | Alternative | Reportable Incident | 136-03-0296 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Control Operation | Control Operation | YES | [17 empty] | Replaced failed controller with new Orenco MVP DM controls. System restored to proper operation. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/20/2023 | 07:30 AM
12/13/2023 | Alternative |  | 093-09-0066 | Isle of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | JEFulbright Septic, LLC | 1942001131 | Jason | Fulbright | 1.000000 | 3000 | PuraFlo |  | Pump | Gravity | Pad | Not Applicable | 2400.000000 | [] | [] | NA | Musty | Clear | 7.280000 | 4.200000 |  |  |  | 12/13/2023 | Pump Chamber | 4.000000 |  |  | 41.000000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/29/2023 | Dec 30 1899 3:25PM
03/13/2023 | Alternative | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | [18 empty] | Service call only: Replaced both discharge Zoeller N-161 Pumps | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
11/17/2023 | Alternative |  | 033-18-0032-SR | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/07/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-3222 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Hoot |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | Dec 30 1899 12:05PM
10/12/2023 | Alternative | RoutineScheduled | 04-100-1017 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1250 | PURAFLO |  | Pump | Gravity | Pad | Not Applicable |  | [] | [] | NA | [17 empty] | SLUDGE JUDGE SEPTIC TANK 4-5" FROM BOTTOM EVERYTHING WORKING AS IT SHOULD RAKED PEAT, GOOD LEVEL AND CONDITION | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:35 PM
10/24/2023 | Alternative | RoutineScheduled | 182-04-0396 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  |  | Drip | Not Applicable |  | ["Auxiliary Filter","Control Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","Control Operation","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Septic/FAST pumped 10/31. CP replaced | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/23/2023 | 12:00 AM
03/15/2023 |  |  | 19-120-0162A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1500 |  |  | Siphon | Gravity | Trenches | Not Applicable |  | [] | ["Distribution Pump Operation","Control Operation","Recirculation Pump","Dispersal System Operation","SludgeScum Accumulation"] |  | Musty | Clear | 6.000000 |  | 6.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/19/2023 | Alternative | RoutineScheduled | 196-14-118 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Elite Onsite | 1942001726 | Drew | Saunders | 2.000000 | 2000 | 1000 | 1000 | Pump | Pressure | Drip | Not Applicable | 450.000000 | ["Effluent Screens","Level Sensor Operation"] | ["Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2024 | 07:10 PM
10/16/2023 | Alternative | Routine/Scheduled | LEGACY | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal level 14 in of sludge 1 in of solids Pulled sprayed and brushed filter No signs of infiltration -Recirculation Tank: Normal level 12 in of suspended solids Tested floats and pump all working as should Pulled sprayed and brushed bio tube filter Vault intact Pulled and cleaned pump All plumbing intact and pump moving water properly No signs of infiltration -RSV (Recirculating Splitter Valve): Normal level 8 in of sludge less than 1 in of solids Pulled and flushed rsv Took apart cleaned check ball No signs of infiltration -Media Sheets 1: Brushed and flushed laterals Sprayed and cleaned media sheets Flushed media module until water ran clear -Media Sheets 2 (duplicate): Brushed and flushed laterals Sprayed and cleaned media sheets Flushed media module until water ran clear -Control Panel: 120 volts coming in All visual and audible alarms functioning properly Recirc pump pulled 11.7 amps All components properly working -Distribution Box: Normal level 10 lines all intact and properly taking water Speed balancers intact and properly working Box itself in good shape however lid has 2 hairline cracks -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | Dec 30 1899 9:37AM
11/01/2023 | Alternative | Routine/Scheduled | 151-15-0124 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3000 | EcoPod |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | 05:37 PM
04/21/2023 | Alternative | RoutineScheduled | SSD-08-82 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | trash/septic | Microfast | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | YES | Musty | Clear |  | 8.800000 | [14 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/26/2023 | 03:50 PM
06/30/2023 | Alternative | Routine/Scheduled | 234-13-206 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | Replaced timer enable float | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | Dec 30 1899 9:23AM
08/10/2023 | Alternative | Reportable Incident Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Installed Norewco UV unit. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/29/2023 | Dec 30 1899 3:58AM
06/14/2023 | Alternative | Reportable Incident Component Maintenance | 061-17-122 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to failed contactor. Replaced contactor. Saw signs of fabric softner use in the system. Let homeowner know this hurts their treatment and to stop using it. Gave them a copy of the do's and dont's. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
04/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/01/2023 |  | RoutineScheduled | 177-13-0268-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Recirculation Pump" ,"SludgeScum Accumulation" ,"Control Operation" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"Recirculation Pump" ,"Control Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Recirc panel maintained it's settings, but showed a number of high level alarms, pump fail, and contactor alerts throughout the year. Cleaned recirc pump intake, replaced the pump supply wire nuts and vacuumed out a few inches of water in the Orenco splice box. Drip rates have returned to design rates. Flush rates have increased by 1.5 to 2.0 gpm, but are still well below design. Both tanks need pumped out - an estimate will be sent to the homeowner. If flush rates haven't improved by next year's inspection, the drip tubing should be bleach flushed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
04/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 2.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Home owner refused to allow us to take a sample. Doesn't feel there's anything wrong. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
10/05/2023 | Alternative | RoutineScheduled Component Maintenance | 175-04-0320 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/15/2023 | 02:02 PM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Trees have been recently planted on/near the end of the drainfield lines. The homeowner is contacting the landscaper to remove the trees and an installer to assess and repair the lines in the appropriate manner. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
01/18/2023 |  | RoutineScheduled | 175-04-0584 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Advantex unit is holding effluent and needs to be cleaned. Advantex sheets need replacement. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/13/2023 | 11:23 AM
03/31/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | new air blower was installed and is working as it should | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
04/27/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Was unable to open the pump tank lid bushes surrounding the tank riser. need to cut back. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
07/19/2023 | Alternative | RoutineScheduled | SD-12-313 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | [9 empty] | ["Effluent Screens","Attached Growth Medium"] | ["Effluent Screens","Attached Growth Medium","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/28/2023 | 04:35 PM
08/14/2023 | Alternative |  | {FIPSCode}-STS-4720 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 08/14/2023 |  | 10.100000 |  |  | 2.300000 |  |  | Will be sent separately |  | BOD: 10.1 TSS: 2.30 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/14/2023 | 12:00 AM
05/12/2023 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/13/2023 | 09:50 AM
06/01/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/12/2023 | 11:35 AM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Enable float was bad and replaced while onsite. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/16/2023 | Dec 30 1899 12:58PM
07/31/2023 | Alternative | RoutineScheduled Component Maintenance | 175-13-0188 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Atu media is partially clogged from regrowth/sludge, recommend chemical cleaning followed by a pump-out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
01/30/2023 | Alternative | RoutineScheduled | 047-16-250 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity |  | UV |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Disinfection"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Disinfection"] | NA | Sulphitic | Discolored |  | 6.700000 |  |  |  | 01/30/2023 | Sample Chamber | 4.000000 |  | 1.000000 | 5.600000 |  |  | Will be sent separately | Inspected | As noted previously, we recommend replacing the EZ Treat module lid. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
10/04/2023 | Alternative | RoutineScheduled | 133-STS-96436 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | system check okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Loudoun | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | 10:00 AM
08/14/2023 | Alternative | Reportable Incident | 157-10-0140 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/14/2023 | 04:00 PM
05/18/2023 |  | Routine/Scheduled | 234-15-109 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/18/2023 | Jan 1 1900 12:40PM
03/07/2023 | Alternative | Routine/Scheduled | SHUN-BD9LAM | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Raised the aerator. The timer is set to 1.85 minutes every 1.85 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | Dec 30 1899 9:30AM
07/25/2023 | Alternative | Follow-Up Component Maintenance | 179-14-0212-SP | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Header lines; line 1 contains a few roots. Line 2 Ok contains a few roots. Line 3 root clog at d-box cleared by hand, line is dry. Line 4 few roots at d-box at beginning of header, line is saturated. Line 5 split, header crushed between 2&6 ft. from d-box. Water and camera can pass, line saturated. Added root-x to all lines. Recommend add 2-3 lines upslope and cut down Elm tree. Maybe able to use existing d-box. Replace 1st 6 ft of line header 5 at time of repair. Dozen trees to clear. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/26/2023 | 07:01 AM
03/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Microfast blower filter was missing. It was replaced. Bell cap for the hydraulic unit filter had broken. It was replaced. System appears to be functioning as designed now. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
03/28/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
01/26/2023 | Alternative | RoutineScheduled | 061-17-542 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Control Operation" ,"Recirculation Pump" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | AX20 lid is no longer attached to the pod. Hinges came epoxied in place, and that epoxy has failed. Need to reattach lid with stainless steel nuts and bolts. The struts that hold the lid open have rotted in half so that lid will not stay open for service. Recommend converting to new single prop rod. A repair proposal has been sent to the owner. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
06/15/2023 |  |  | 2004-143-0206 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Best |  | Pump | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","Distribution Pump Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/15/2023 | 12:00 AM
01/02/2023 |  | RoutineScheduled | 04-125-163 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 3 Chlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/02/2023 | 12:00 AM
09/12/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  | Microfast Drip |  | Pump | Pressure | Drip | Not Applicable | 600.000000 | ["None"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/26/2023 | 12:00 AM
01/25/2023 |  | Routine/Scheduled | 228-17-0123 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/25/2023 | Jan 1 1900 9:40AM
02/27/2023 |  | RoutineScheduled | 179-06-0150-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/10/2023 | 11:17 AM
12/07/2023 | Alternative | RoutineScheduled | 165-STS-333725 | Rockingham | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [18 empty] | Effluent not reaching pump tank. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/03/2024 | 12:00 AM
04/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/04/2023 | Alternative | Reportable Incident | 147-17-0106 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to a strong smell. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream - was stopped up. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the alarm light bulb. The Clearstream tank needs to be pumped and cleaned and the septic tank needs to be pumped out as well. The timer is set to 3.5 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/04/2023 | Dec 30 1899 11:30AM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/27/2023 | Alternative | RoutineScheduled | 182-18-0027 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  |  | Trenches | Not Applicable |  | ["Septic Tank Baffles"] | ["Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/27/2023 | 12:00 AM
10/12/2023 | Alternative |  | 179-STS-92021 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/07/2023 | Alternative | Initial Visit | 121-STS-13510 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000gal | LPD |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [] |  | Septic | Discolored | [14 empty] | Inspected | - system is not functioning, pumping down slow, recommend further evaluation | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/13/2023 | 12:00 AM
03/23/2023 |  | RoutineScheduled | 08-113-152 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Disinfection","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 2 Chlorine 4 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/23/2023 | 12:00 AM
03/07/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-6"sludge 4"scum/ Microfast-6"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-2537 ETM-392h 53m/ High-33 ETM-14h 46m/ Peak-31 ETM-199h 44m/ On-9m 32s Off-2h/ Peak off-1h 36m/ Watermeter-0,1814,366/ UV- Light sleeve cleaned and functioning correctly/ No breakout or spongy areas on the drip field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/14/2023 | Alternative | Initial Visit | 800-STS-14640 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 68.000000 | [7 empty] | Owner called due to the light being on for two weeks. Serviced system. Checked the pump and panel (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Fixed the grade on the pipe in the Clearstream. Replaced the pressure switch on the aerator (wired to high level alarm in panel - not to air sensor) - needs to be addressed and/or fixed. There is too much swing on the pump float - needs to be addressed and/or fixed. The timer is set to 1 minute every 3 hours. Took initial BOD sample. NOTE - BOD sample was high - system should function properly after servicing / fixing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | Dec 30 1899 1:00PM
04/04/2023 |  | Initial Visit | 182-14-0050 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | [17 empty] | Inspected | Septic pumped out | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | 12:00 AM
10/16/2023 | Alternative | RoutineScheduled | 175-06-0450 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank to Puraflo Modules | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Level Sensor Operation"] | ["Attached Growth Medium","Level Sensor Operation"] | NO | [17 empty] | Septic Tank-12"sludge 0"scum/ Pump Tank-2"sludge/ No pump out needed at this time/ Peat turned in all 5 modules and is in good condition/ Electiric Junction Box requires replacement/ Replaced jiunction box and float/ Controls, pump, floats and alarms are now functioning properly/ Counts: Pump-32146 ETM-28695/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/27/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
07/12/2023 | Alternative | RoutineScheduled Component Maintenance | SD-04-l88 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Spin filter was crushed again, yearly occurrence. Treatment is reasonably good and solenoids have been verified to be opening at proper time. Opened pump union to check for return flow (none) and pressure or suction (none). Jostled pump around a little to reconnect union. Next test cycle almost instantly plugged the spin filter with sludge. Only measured 2" of sludge in drip pump tank, but there may be deeper clumps around the pump. Recommend thorough cleaning of the drip pump tank, and then installing 4" blocks under the pump. Drilled weep hole near the high point of pump piping in pump tank to see if it will prevent spin filter from crushing. Will plug hole and add ARV if it helps. High level count at 69 and peak count at 2191 in drip panel. At around 16-1/2 years old, the peat is starting to show some signs of wearing out but still providing decent treatment. Will reevaluate next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 07:01 AM
09/04/2023 | Alternative | Routine/Scheduled | 019-STS-24227 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Aqua Safe |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/04/2023 | 11:45 AM
07/18/2023 | Alternative | Routine/Scheduled | 234-12-154 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the buzzer. The timer is set to 1 minute every 1.5 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/18/2023 | Dec 30 1899 3:30PM
08/04/2023 | Alternative | Routine/Scheduled |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Visit - Second Opinion - Service Provider = Farmer Septic. Primary septic tank - normal level - recommend pumpout. Aeration Tank - normal level - mixing present - compressor serviced Owner complained of compressor making excessive noise - reported to have been rebuilt by Service provider last month. Pump Tank - float sensors, pump and controls operating. DBox - no indications of surfacing - owner requested no excavation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | 10:45 AM
01/30/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
07/25/2023 | Alternative |  | 12-125-036 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/25/2023 |  | 11.000000 |  |  | 12.200000 |  |  | Will be sent separately |  | BOD: 11.0 TSS: 12.2 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/25/2023 | 12:00 AM
05/31/2023 | Alternative | Reportable Incident | 800-06-0020 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm over the weekend. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The aerator was full of fire ants. The septic tank needs additional risers on it to be properly inspected in the future. The | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/31/2023 | Dec 30 1899 4:15PM
05/24/2023 |  | RoutineScheduled | 177-07-0203-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | PuraFlo |  | Gravity | Pressure | Trenches | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/28/2023 | 12:00 AM
03/13/2023 |  | RoutineScheduled | 17-179-024 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Eljen |  | Pump | Pressure | Mound | Not Applicable | 200.000000 | ["Attached Growth Medium","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","Effluent Screens","Dispersal System Operation","Control Operation","Auxiliary Filter"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | 12:00 AM
07/01/2023 | Alternative | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 | 1000 |  |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | 12:00 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Bio Barrier | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | Dec 30 1899 12:05PM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/27/2023 | Alternative |  | 179-STS-92375 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/19/2023 | Alternative | RoutineScheduled | -STS-43175 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Delta Environmental DF Series |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [16 empty] | Inspected | Sludge levels-- -32" scum on top (Heavy on the wipes) and 6-10" sludge in Septic tank. May want to arrange a pump out this fall. Treatment Tank has good aeration and 3-12" thick scum on top and 3-4"- sludge trace - in Pump Tank 12" sludge. Doing good,, the treatment scum layer may need attention later this year. Good aeration in the treamtnet unit. System is pumping to drain field and drain field appears dry and unremarkable. 50psi going to drainfield, watermeter reading 1,840,520 vs 1,757,490 gallons approx 83,000 gallons this year about 227 gallons per day. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | Jan 1 1900 9:30AM
02/15/2023 |  | RoutineScheduled | 107-10-0114 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 2505.000000 | [] | [] |  |  |  | 6.950000 | 1.000000 | 28.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 10:45 AM
05/08/2023 |  | Reportable Incident | 228-19-0062 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/08/2023 | Jan 1 1900 8:00AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/03/2023 | Alternative | Routine/Scheduled | 093-02-0320 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/03/2023 | Dec 30 1899 10:58AM
08/27/2023 | Alternative | RoutineScheduled | SD-07-236 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2700 | septic | Microfast | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | 08:30 AM
02/19/2023 |  | Routine/Scheduled | 041-STS-257812 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/19/2023 | Jan 1 1900 9:00AM
10/04/2023 | Alternative |  | 107-06-0201 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
08/11/2023 | Alternative | RoutineScheduled Component Maintenance | 154-02-0991 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"SludgeScum Accumulation"] | ["Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the septic tank due to sludge accumulation in the tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
05/02/2023 |  | Routine/Scheduled | {FIPSCode}-STS-3313 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Hoot |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | Jan 1 1900 2:05PM
10/31/2023 | Alternative | RoutineScheduled | S102-17-0023 | Alleghany | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | AdvantexAX20RT | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The recirculating and discharge pumps were both pulled and cleaned. The textile sheets were sprayed off. the lateral pipe was flushed. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/27/2023 | Dec 30 1899 9:20PM
06/24/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Other"] | ["Other"] | NA | [16 empty] | Pumped Out | Annual inspection. Control panel in alarm condition due to high water level in septic/recirculation tank. Recirculation splitter valve (RSV) had broken off below water surface. Scheduled pump out of septic/recirculation tank to retrieve bottom half of RSV. Before pump out, 14" of accumulated solids in septic tank. Flushed treatment unit spray manifold. Cleaned recirculation pump solids basket filter. Unclogged many spray heads in treatment unit. Sprayed off treatment unit sheets. Tested floats, pumps and alarm. Septic tank pumped out the following week. Repaired RSV and reinstalled on 7-1-2023. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/24/2023 | 07:03 PM
10/17/2023 | Alternative | Routine/Scheduled | 093-07-0081 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | Dec 30 1899 11:30AM
08/14/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | Dec 30 1899 3:58AM
02/22/2023 |  | RoutineScheduled | 175-04-0876 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 02:21 PM
03/28/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | All 5 pods peat fiber is badly broken down and sandy. 3 pods are full of effluent. Peat fiber needs to be replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
10/17/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation"] |  | NA | [15 empty] | Will be sent separately | Inspected | Blower, effluent pump & floats need replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/15/2023 | Dec 30 1899 2:02PM
03/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 4.000000 |  | Septic Tank #1 | Septic Tank #2 | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump","Level Sensor Operation"] | ["Recirculation Pump","Level Sensor Operation"] | YES | [7 empty] | 03/22/2023 | Sample Chamber | 25.000000 | [5 empty] | Attached to this report |  | Septic Tank #1-4"sludge 2"scum/ Septic Tank #2-4"sludge 0"scum/ EZ-Treat Recirculation Tank-3"sludge 3"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Replaced 4 floats in the pump tank (Wide Angle) on 3/9/2023/ Recirc. pump intake cleaned , media in good condition, spray nozzles function properly/ Controls, pumps, floats and alarms now functioning properly / No breakout or spongy areas on the drainfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/08/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 1.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | NA | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/22/2023 | 12:00 AM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Only one spray head on the EZ treat was functioning. Flushed lines and replaced spray heads. EZ treat should return to proper function. There are roots growing in around the inlet pipe of the clarifying/EZ treat/DF pump tank. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
02/20/2023 | Alternative | RoutineScheduled | 128-18-0084 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Aquasafe |  | Gravity | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/01/2023 | 12:00 AM
08/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced alarm float | This AOSS should now return to normal function after having provided the above state routine maintenance | 09/20/2023 | 01:07 PM
03/15/2023 | Alternative | Routine/Scheduled | 151-02-174 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 1500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Primary septic tank - Cottage - normal level. Primary septic tank - main Residence - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox- at grade - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/16/2023 | 09:00 AM
10/26/2023 | Alternative | Follow-Up | 061-STS-22612 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Replaced broken risers. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/16/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/17/2023 | 12:02 PM
02/28/2023 |  | RoutineScheduled |  | Augusta | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | ET Bed failing and ponding needs repaired Pump supply line was clogged and repaired | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/18/2023 | 04:10 AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance | 175-09-0507 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
04/20/2023 |  | RoutineScheduled | 003-STS-29457 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/23/2023 | 12:00 AM
11/28/2023 | Alternative | Routine/Scheduled | 06-118-0094 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level high. Inlet tee appears to be intact. Not due for pump out. -Recirculation Tank: Water level high. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Recirculation pump has exceeded life expectancy. Recirculation pump plumbing has exceeded life expectancy. Recirculation floats have exceeded life expectancy. -RSV (Recirculating Splitter Valve): Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly. -Discharge/Pump Tank: Water level high. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Discharge pump has exceeded life expectancy. Discharge pump plumbing has exceeded life expectancy. Discharge floats have exceeded life expectancy. -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Checked and confirmed spray height is good -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Found program settings for discharge timer were default which will not keep up with usage for household. Set discharge timer settings to accommodate 3-4 bedroom home. Will need permit to verify timer settings. Homeowner states that it is a 5 bedroom house and they have 7 residents. I adjusted recirculation timer to accommodate for usage. Control panel is about 9 years old -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact. Noted one drainline taking water slowly or not at all -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | Dec 30 1899 2:15PM
03/29/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 3.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/09/2023 | Alternative | Initial Visit |  | Rappahannock | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 4.000000 | 6000 | Septic | Singulair | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | YES | [17 empty] | Repair | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/12/2024 | 08:40 AM
10/10/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS |  |  |  |  | Pump |  |  |  |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/10/2023 | 12:00 AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/08/2023 | Alternative | RoutineScheduled | 061-16-400 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Battlefield Soil And Septic LLC | 1942001084 | Josh | Johnston | 1.000000 | 1000 | Microfast |  | Pump | Pressure | Drip | Not Applicable | 200.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation"] | YES | None | Discolored | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/16/2023 | 08:35 AM
10/17/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-91636 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation" ,"Disinfection" ,"Level Sensor Operation"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Control Operation" ,"Disinfection" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Replaced uv bulb. Bad enabler float in discharge tank, will contact installer. RECIRC: HL-1, LL-15, OVERRIDE-591. DISCHARGE: HL9, PEAK-9. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
11/29/2023 | Alternative | RoutineScheduled | 03-163-0175sr | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Biomicrobics Microfast |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","Distribution Pump Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/29/2023 | 12:00 AM
04/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
11/06/2023 | Alternative | RoutineScheduled | 179-STS-91626 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 13467.000000 | [] | [] |  |  |  | 7.260000 | 1.160000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/15/2023 | 01:25 PM
05/31/2023 | Alternative | Initial Visit | 157-09-0202 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit - Primary septic tank - normal level - effluent screen serviced - recommend pumpout. Aeration Tank - normal level - mixing present - compressor serviced. Pump tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/07/2023 | 08:30 AM
01/30/2023 |  | RoutineScheduled | 177-13-0263-SR | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
10/30/2023 | Alternative | RoutineScheduled | 91-197-5001 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | JET |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/30/2023 | 12:00 AM
12/04/2023 | Alternative | Routine/Scheduled | 08-163-0037 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Trash Tank Condition of above Component Notes for above Component High level upon arrival 4 in of sludge 2 in of solids No signs of infiltration Recirculation Tank Condition of above Component Notes for above Component High level upon arrival 13 in of suspended solids Tested floats and pump all working as should however floats are aged Pulled and cleaned pump All plumbing intact and pump moving water properly however pump is aged No signs of infiltration RSV (Recirculating Splitter Valve) Condition of above Component Notes for above Component Male slide is not seating properly Pulled and flushed Removed rubber grommet and flushed inside Discharge/Pump Tank Condition of above Component Notes for above Component High level upon arrival 15 in of suspended solids Tested floats and pump however floats are aged Pulled and cleaned pump All plumbing intact and pump moving water properly however pump is aged No signs of infiltration Media Sheets Condition of above Component Notes for above Component Brushed and flushed laterals Sprayed media sheets Media sheets holding water due to bridging and sheet walls holding sludge Flushed module Control Panel Condition of above Component Notes for above Component In alarm upon arrival 120 volts coming in All visual and audible alarms functional Discharge pump pulled 11.45 amps Recirc pump pulled 11.83 amps All components working as should Distribution Box Condition of above Component Notes for above Component High level 3 lines all intact however taking water slowly No surfacing from the drain field however water is surfacing from the Dbox itself Drain Field Condition of above Component Notes for above Component No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 9:36AM
04/19/2023 |  | Routine/Scheduled | 14-142-0330 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 400.000000 | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | [17 empty] | Effluent filter was found partially clogged. The spray from spin emitters on Advantex manifold appeared weak. The emitters were hosed down and the recirculation pump intake screen was cleaned. The spray strength improved after cleaning these items. If intake screen of recirculation pump clogs quickly, again, the Advantex unit may need to be pumped out/refilled. There were 42 overrides of the recirculation pump in the last 30 days. The off time for the recirculation pump was changed from 12 to 11 minutes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/19/2023 | Jan 1 1900 12:21PM
10/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
01/02/2023 | Alternative | RoutineScheduled | 047-17-017 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1500 | septic | EZ Treat | Gravity | Gravity | Discharge |  |  | [] | [] | YES | None | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/27/2023 | 08:55 AM
04/06/2023 |  | RoutineScheduled | 93-184-5002 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Pump | Pressure | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Septic Tank Baffles","Level Sensor Operation","Disinfection","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/06/2023 | 12:00 AM
09/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  | 1500 |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 4:00PM
03/09/2023 |  | Routine/Scheduled | 147-17-0112 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Drainfields LLC | 1942001219 | Gene | Shanks | 2.000000 | 1650 | Aqua Klear |  | Pump | Pressure | Pad | Not Applicable | 125.000000 | ["Auxiliary Filter","Control Operation"] | ["Auxiliary Filter","Control Operation"] | N/A | Musty | Clear | [15 empty] | Timer enable float replaced. System is operating per design. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/09/2023 | Jan 1 1900 1:00PM
02/01/2023 | Alternative | Reportable Incident | 02-163-0175 | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | Control Operation | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Pumped pump tank empty - replaced failed logic controller in control panel - conducted routine service of treatment system. Processing tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - serviced discharge pump, float sensors - repaired control panel. Drip - headworks serviced. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/02/2023 | Dec 30 1899 9:30AM
07/19/2023 | Alternative | Routine/Scheduled | 103-STS-96414 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Purasys |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service - 180 day service inspection - sampling obtained. Primary septic tank - normal level Aeration Tank - sludge return operating - mixing present - submersible compressor serviced. Pump - float sensors, pump and controls operating. GeoMat Pad - no indication of surfacing. Samples obtained for BOD5 & TSS | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | 07:30 AM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance | SP-04-537 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Outstanding proposal for repairing lid. Recirc tank needs pump out. Air vent needs to be replaced. Will send proposal for all this work to be done. Water in septic tank is black due to medication being used at house. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
05/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] |  | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Upon arrival control panel was completely shut off. Found Aquarobic blower not working. Found force main in pump tank broken. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | 12:05 PM
10/11/2023 | Alternative | RoutineScheduled | 085-STS-33587 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1000 | EZ Treat |  | Pump | Pressure | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 12:00 AM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 10/31/2023 |  | 34.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample normal Pressure gauges replaced Primary tank pumped | This AOSS should now return to normal function after having provided the above state routine maintenance | 12/06/2023 | 03:05 PM
09/21/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/27/2023 | Dec 30 1899 8:35AM
06/15/2023 | Alternative | RoutineScheduled | 175-10-0375 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank | Delta DF- ATU to pump tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-10"sludge 2"scum/ ATU-4"sludge 4"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-22840/ Pump run time hours-2067/ Hand counts-87/ High counts-19/ Watermeter-070,890.4/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | alarm unplugged repaired Please have waterhose and water on to reach system for proper cleaning | This AOSS should now return to normal function after having provided the above state routine maintenance | 01/15/2024 | 10:39 AM
09/21/2023 | Alternative | RoutineScheduled | 07-197-A3 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 | ATU |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | Pungent | Cloudy | 6.000000 | 0.000000 |  |  | No aerator no tablets | [10 empty] | This system needs an aerator and tablets | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/25/2023 | 12:00 AM
09/18/2023 | Alternative | RoutineScheduled |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 09/18/2023 | Sample Chamber | 12.000000 | [5 empty] | Attached to this report |  | Septic Tank-4"sludge 3"scum/ Microfast-2"sludge / Pump Tank-0"sludge/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-134 ETM-8h 34m On-4m 2s Off-12h/ High-7/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/16/2023 |  | RoutineScheduled | 2011-143-0143 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Carrington Pump & Irrigation | 1942001121 | John | Carrington |  |  | Norweco |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Level Sensor Operation","Distribution Pump Operation","Effluent Screens","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation","Auxiliary Filter"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/16/2023 | 12:00 AM
07/12/2023 | Alternative | Reportable Incident Component Maintenance | 175-04-0460 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced contactor in control panel. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
07/03/2023 | Alternative | Routine/Scheduled | 228-14-0493 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/03/2023 | Dec 30 1899 8:30AM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/17/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-6"sludge 3"scum/ Microfast-4"sludge 0"scum/ Pump Tank-0"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-253 ETM-12h 23m/ Pump2-247 ETM-12h 2m On-2m 59s Off-12h Peak Off-9h 36m/ Peak-4/ High level-6/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/20/2023 | Alternative | Reportable Incident | 1982-143-0000 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | [] | [] | [17 empty] | Pumped Out | Replaced l280 pump and fixed pump line. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance | 182-19-0107 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
12/04/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/12/2024 | 04:00 PM
08/19/2023 | Alternative | Reportable Incident |  | Mathews | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | ["Attached Growth Medium","Control Operation","Distribution Pump Operation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | AOSS - initial visit - ALARM Found system fully flooded - needs service tech to visit and diagnose. Above ground EcoFlo fully overgrown and NOT accessible. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/21/2023 | 11:00 AM
09/29/2023 | Alternative | RoutineScheduled Component Maintenance | 175-12-0217 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
03/21/2023 |  | RoutineScheduled |  | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 03/21/2023 |  | 154.000000 | [5 empty] | Will be sent separately | Inspected | Replaced blower Pumped all tanks and added access Replaced blower panel Repaired buzzer | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/28/2023 | 02:17 PM
01/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
09/14/2023 | Alternative |  | 159-03-242 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | ["None"] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/14/2023 | 12:00 AM
07/19/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-91634 | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | 90-Day Inspection There appears to be effluent surfacing in the drip dispersal area. A follow-up visit is planned to investigate further before referring back to the system designer. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 08/01/2023 | 06:26 AM
09/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. High level float was wired to the overide float in the panel. Floats were set wrong. Fixed wiring in the panel and adjusted the floats to the proper height. System now has a functioning high level alarm. Two part microfast needs to be pumped due to sludge levels from the use of fabric softner. Homeowner will arrangements to have the tank pumped out. After pump out bathtub needs to be ran for 3 hours to refil the tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
05/06/2023 | Alternative | Reportable Incident | 136-16-0288 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | AOSS - Initial Visit - Alarm Event. Primary septic tank - overflowing due to clogged weir in Aeration Tank. Pumped empty for service and maintenance. Aeration tank - returned to normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | 09:15 AM
02/01/2023 |  | Routine/Scheduled | 550-STS-6598 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/01/2023 | Jan 1 1900 2:00PM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/16/2023 | Alternative | Routine/Scheduled | 157-05-310 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Primary septic tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump tank - float sensors, pump and controls operating. DBox - plastic - at grade - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/20/2023 | 08:00 AM
10/18/2023 | Alternative | RoutineScheduled | 06-113-243 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/18/2023 | 12:00 AM
04/24/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/05/2023 | Alternative | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 11500 | Biomicrobics Fast 3.0 |  | Pump | Pressure | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Trouble shooting pump tank goes into alarm randomly. Chamber was pumped by foutz. Found laots of towels and wipes. Tested pump and old floats and all test operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/30/2023 | 09:30 AM
01/16/2023 | Alternative | Initial Visit | 13-160-0144 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 | 1000 | Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | Septic | Discolored | [14 empty] | Inspected | - if blower alarm continues, recommend blower replacement - outlet/media not functioning properly, recommend further evaluation | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/16/2023 | 12:00 AM
02/21/2023 |  | RoutineScheduled | 107-13-0345 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/08/2023 | 12:00 AM
01/26/2023 |  | Routine/Scheduled | 800-03-0547 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | Jan 1 1900 12:26PM
12/21/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | Dec 30 1899 11:25AM
09/25/2023 | Alternative | RoutineScheduled Component Maintenance | 179-13-0051-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump" ,"SludgeScum Accumulation"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the Advantex RT unit with our staff present to remove sludge in the tank. Please contact our office when you would like for us to schedule this for you. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
04/12/2023 |  | RoutineScheduled | 175-18-0399 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 04:23 AM
01/10/2023 |  | RoutineScheduled | 195-Discharge-31227 Cornett Road | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/10/2023 | 12:00 AM
07/26/2023 | Alternative | RoutineScheduled Component Maintenance | 175-14-0447 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation" ,"SludgeScum Accumulation"] | ["Level Sensor Operation" ,"Distribution Pump Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Replaced non-functioning alarm horn in control panel, verified that latching alarm was working correctly. Advised owners that in latching alarm panels, the alarm had to be acknowledged (by pushing the silence switch) even though they had not heard the buzzer. Pump tank has excessive sludge. Owner made appointment with local pumper to get it pumped on 7/28. Blower running at 3.31 amps (max 3.6). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:19 PM
09/21/2023 | Alternative | RoutineScheduled |  | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Prince William | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 3000 | AX-20 | Micro-Fast | Pump | Gravity | Discharge | UV | 150.000000 | ["Disinfection","Attached Growth Medium","Distribution Pump Operation"] | ["SludgeScum Accumulation","Effluent Screens","Recirculation Pump"] | YES | Septic | Clear | [14 empty] | Pumped Out | No effluent was seen at discharge point. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/30/2023 | 12:00 AM
12/01/2023 | Alternative | Routine/Scheduled |  | Surry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Outlet tee appears to be intact. Not due for pump out. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pumps are functioning. Checked and confirmed discharge floats are functioning. Exercised gate valves and confirmed they were open. Discharge pumps are rated 17.7 amps @ 230 volts Pump 1 at Rest Voltage: 251.2 Pump 1 Amperage: 15.4 Pump 2 at Rest Voltage: 251.8 Pump 2 Amperage: 18.0 Pump 2 is pulling higher than normal amperage. It has exceeded Miller's 1 year warranty and is still within Orenco's 5 year warranty -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Pump 1 CT: 3579 Pump 1 ETM: 64 Hours Pump 2 CT: 3474 Pump 2 ETM: 63 Hours | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 9:03AM
08/10/2023 | Alternative | RoutineScheduled | 107-06-0118 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Trenches | Not Applicable |  | ["Septic Tank Baffles","Dispersal System Operation"] | ["Dispersal System Operation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | 12:00 AM
11/30/2023 | Alternative | Routine/Scheduled | 041-STS-257688 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/30/2023 | Dec 30 1899 3:34PM
02/27/2023 | Alternative | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced (5) Control floats. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/31/2023 | Dec 30 1899 12:26PM
04/24/2023 |  | Routine/Scheduled |  | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | UV | 600.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes and spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | Jan 1 1900 6:45AM
04/27/2023 |  | Routine/Scheduled |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Routine Service Primary septic tank - pumped empty - Installed new riser access Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - replaced support struts - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating - replaced control panel with new MVP DM controls. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | 07:30 AM
09/05/2023 | Alternative | RoutineScheduled | 12-197-A4 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | [12 empty] | None | Clear | 7.200000 | 5.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
07/19/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-1355 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | Dec 30 1899 2:30PM
10/16/2023 | Alternative | RoutineScheduled | 085-STS-34152 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:00 AM
12/28/2023 | Alternative |  | 17-192-155 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/28/2023 |  | 6.980000 |  |  | 2.300000 |  |  | Will be sent separately |  | BOD: 6.98 TSS: 2.30 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 12:00 AM
07/17/2023 | Alternative | Pump-Out Only |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 | [8 empty] | [] | [] | [17 empty] | Pumped Out | Need Peat Moss Replaced and Possible Pump Replacement | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/17/2023 | 12:00 AM
05/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
07/06/2023 | Alternative | RoutineScheduled | 181-08-0136 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 1.000000 | 1500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | Filters checked and cleaned. No apparent leaks in system or drain field area. Control panels functioning properly. System did not need to be pumped. Lid was properly secured | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/15/2023 | 09:55 AM
09/14/2023 | Alternative | RoutineScheduled Component Maintenance | 033-06-0161-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
07/10/2023 | Alternative | RoutineScheduled Component Maintenance | 099-13-0097-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Effluent Screens" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Peat showing its age but still OK for this year, evaluate next year for replacement. Pad site over grown needs to be maintained. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
10/23/2023 | Alternative |  | 099-15-0019-SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/24/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
12/11/2023 | Alternative |  | 08-113-163 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/11/2023 |  | 9.690000 |  |  | 1.300000 |  |  | Will be sent separately |  | BOD: 9.69 TSS: 1.30 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/11/2023 | 12:00 AM
04/13/2023 |  | RoutineScheduled | 101-04-0079 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Trenches | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/16/2023 | 12:00 AM
05/15/2023 |  | RoutineScheduled | 2051-98-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | YES | Musty | Clear | 6.900000 |  |  | 1.700000 |  | 06/01/2023 | Sample Chamber | 19.000000 |  |  | 10.200000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/11/2023 | 12:00 AM
08/14/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | 11:00 AM
05/09/2023 | Alternative | Routine/Scheduled | 128-05-127 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 12:45 PM
03/02/2023 |  | Initial Visit | 179-STS-91873 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | One high level alarm and 22 low level alarms showing for recirc tank. One high level showing in discharge tank. All "R" counts reset to zero. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
08/18/2023 | Alternative | RoutineScheduled | 09-197-A3 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Multiflo |  | Pump | Pressure | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/18/2023 | 12:00 AM
03/18/2023 |  | RoutineScheduled | 133 15 0056 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. Tested floats, pumps and alarm. Most likely the treatment unit will need to be pumped out next year. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 07:03 PM
09/26/2023 | Alternative | RoutineScheduled | 08-113-035 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 15 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/26/2023 | 12:00 AM
06/15/2023 | Alternative | RoutineScheduled | 085-STS-34235 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/14/2023 |  | Routine/Scheduled | 234-15-198 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | Jan 1 1900 11:55AM
08/04/2023 | Alternative | Pump-Out Only |  | Frederick | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Pending Review | EHD - Lord Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim |  |  | 1 | [6 empty] | [] | [] | NA | [16 empty] | Pumped Out | Pumped out Fuji tank hosed out | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 08/06/2023 | 04:55 PM
09/06/2023 | Alternative |  | 041-STS-259046 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 2250 | 1250 | 1000 | Pump | Pressure | Drip | UV |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens"] | YES | Pungent | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | 12:00 AM
01/18/2023 |  | RoutineScheduled | 06-183-254 | Russell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/17/2023 | 12:00 AM
02/15/2023 | Alternative | Routine/Scheduled | 04-174-0093 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/15/2023 | Dec 30 1899 1:53PM
10/12/2023 | Alternative | RoutineScheduled | 103-STS-95980 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/19/2023 | Alternative | RoutineScheduled | C11-180-0049 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Septic tank 1-2" scum layer and 18" sludge, 7' volume, septic does not need pumping, Recirculation zone 12" and discharge zone of advantex 12" This tank may need pumping out this fall. We can arrange with you. The biofilter was dirty and clogged , we cleaned it like new. Advantex System may needs pumping this fall. pulled pump and pump housing, cleaned both, large amount of scum and sludge in the treatment unit maybe time to pump it out this fall. All 6 Float switches test good - We flushed and brushed the spray manifold system until it ran clear, Ran system in test mode. Recirc pump run time 2363.3 hours and 92,758 Cycles and discharge pump run time 321.7 hours and 21,481 cycles. Alarm 4-28-23 and alert log 3-21-23 and many in april, all for filter clog alert. Reccomend to have us come each 6 months to clean filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | Jan 1 1900 9:30AM
01/03/2023 |  | RoutineScheduled | 133 08 0035 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Western Virginia Water Authority | 1942001145 | Michael | Doss | [9 empty] | ["None"] | ["None"] | YES | None | Clear | [5 empty] | 01/03/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2023 | 08:50 AM
08/17/2023 | Alternative | RoutineScheduled |  | Cumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1500 | Singular |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Effluent Screens","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Cloudy | [14 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/17/2023 | 12:00 AM
09/12/2023 | Alternative | RoutineScheduled | 08-163-0030 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 6.000000 |  | Puraflo |  | Pump | Gravity |  |  |  | [] | ["Attached Growth Medium","Level Sensor Operation","Distribution Pump Operation","Auxiliary Filter"] |  | Musty | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | 12:00 AM
04/24/2023 |  | RoutineScheduled | 133 07 0080 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 2000 | Biomicrobics Fast |  | Pump | Pressure | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Routine yearly inspection, Owner has grease traps pumped regularly -Septic Tank under 1" scum and 6" sludge. Fast unit 12" sludge, Fast side port 12" sludge, Pump tank 6" sludge, All levels look great and no pumping is needed at this time. Alarm and both pump appear operational, water level is at correct level. Owner reported no recent alarm. Fast blower was operational and was just replaced by the owner, Cleaned Blower air filter. system is operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
08/08/2023 | Alternative | Routine/Scheduled | 093-16-0201 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 2.000000 | [13 empty] | Replaced aerator and diffuser | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | Dec 30 1899 11:23AM
02/01/2023 |  | RoutineScheduled | 177-06-0594-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Recirc valve was clogged up, cleaned. Inlet pipe has settled a little but it hasn't get clogged up. Will keep an eye on it. Treatment looks better than last year. Left copy of Do's and don'ts. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
07/18/2023 | Alternative | RoutineScheduled | 14-100-0213 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | AQUASAFE |  | Pump | Pressure | Mound | UV | 600.000000 | [] | [] | YES | [17 empty] | EVERYTHING WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | 12:00 AM
02/02/2023 |  | Follow-Up | 179-09-0106-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Added access riser on septic tank inlet. Sealed pump tank wedge lid. Installed proper float tree. Dug up header line #4, line was full of sludge and roots. Jetted and now functional. Added root destroyer to line 4. Homeowner had tanks pumped out last Wednesday. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
05/31/2023 | Alternative | RoutineScheduled | 2017-143-0206 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/16/2023 |  | RoutineScheduled | 175-05-0889 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  | ["SludgeScum Accumulation"] | NO | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
02/17/2023 |  | Reportable Incident |  | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Aqua Klear |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | [15 empty] | Inspected | Called due to owner finding blower panel alarming, it was producing air but pulling half of the rated amount and looked to have a bad diaphram in the motor. Ordered a new blower motor and replaced the alarm box. The old unit had a bad pressure gauge switch, light and tweeter alarm. System if now functional. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/01/2023 | 09:30 AM
07/18/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | Dec 30 1899 2:02PM
09/20/2023 | Alternative |  | 033-18-0126-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
03/01/2023 | Alternative | Routine/Scheduled | 073-STS-101944 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Biofilter Replacement - Repair VDH Permit 136-23-005 02/28/2023 - pumped septic tank and pump basin for storage. 03/01/2023 - Replaced biofilter media with new 03/06/2023 - installed new 500g pump chamber. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/09/2023 | 07:30 AM
03/02/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.900000 |  |  | 0.600000 |  | 03/02/2023 |  | 4.000000 |  |  | 13.200000 |  |  |  |  | Sludge Level high, advised client to have system pumped. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | 03:00 PM
08/31/2023 | Alternative | Routine/Scheduled |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level Processing tank - RSV, recirc pump and effluent screen serviced. Treatment Module - media drapes & spray grid serviced. DBox - not located. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | Dec 30 1899 11:30AM
05/18/2023 |  | RoutineScheduled | 101-11-0031 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Trenches | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | 12:00 AM
01/27/2023 |  | RoutineScheduled | 099-14-0063-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
12/01/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-326 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
04/17/2023 | Alternative | Routine/Scheduled | C800-14-0073 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Aqua Klear |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | Dec 30 1899 1:52PM
08/15/2023 | Alternative | RoutineScheduled | 09-177-1091 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | ECOPURE |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Distribution Pump Operation","Level Sensor Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 12:00 AM
09/05/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | BioWheel |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | August 2023 monthly report. Total flow for month of August 2023 - 114,428 gallons. Average daily flow- 3,691 gallons per day. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | 07:03 PM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, UC Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/03/2023 |  | Routine/Scheduled |  | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | UV | 600.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Processing Tank - recirc - recirc pump, media drapes, spray grid serviced. UV Disinfection - bulb and housing serviced. Processing Tank - Discharge - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | Jan 1 1900 6:30AM
03/15/2023 |  | RoutineScheduled | 05-125-073 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | 12:00 AM
02/28/2023 |  | Routine/Scheduled | 228-04-0674 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Ecoflo |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/28/2023 | Jan 1 1900 12:35PM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was not functioning. When replacing, recommend lifting the housing. The control panel was having problems and did not appear to be cycling correctly. Parts have been ordered for replacement. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"SludgeScum Accumulation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Replaced UV Bulb while on site for inspection. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/11/2023 | Dec 30 1899 11:24AM
03/23/2023 | Alternative | Routine/Scheduled | 157-13-0139 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/23/2023 | 12:30 PM
02/20/2023 |  | RoutineScheduled | {FIPSCode}-STS-1192 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation","Septic Tank Baffles"] | YES | Musty | Clear | [15 empty] | 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/20/2023 | 12:00 AM
09/19/2023 | Alternative | Routine/Scheduled | 03-137-0120 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out -Recirculation Tank: Water level normal. Flushed and cleaned recirculation pump. Tested and confirmed that recirculation pump is operating properly. Tested and confirmed that recirculation float sensors are operating properly. Cleaned effluent screen. Recirculation pump has exceeded life expectancy. Recirculation pump plumbing has exceeded life expectancy. Recirculation floats have exceeded life expectancy. Riser lid is deteriorating which can lead to a safety risk. -RSV: Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly. RSV assembly held together with a temporary repair. -Discharge/Pump Tank: Water level normal. Tested and confirmed that discharge pump is operating properly. Tested and confirmed that discharge float sensors are operating properly. Pump plumbing has exceeded life expectancy and is inaccessible. Floats have exceeded life expectancy and are not properly secured. Found signs of groundwater infiltration around base of riser. Unable to determine pump model and age. -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Checked and confirmed spray height is good. Media lid safety support struts have failed. Media lid is deteriorating -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Drain Field: Found no signs of surfacing on dispersal field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/06/2023 | Dec 30 1899 12:47PM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-03-58 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite to inspect sysyem could not give a contract due to system needing a peat change. Proposal to be sent for a peat change. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
07/23/2023 | Alternative | RoutineScheduled | 96-197-A2 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | YY Services LLC | 1965006418 | Brian | Stewart | 2.000000 | 1000 |  |  | Gravity | Gravity | Discharge | Chlorination | 150.000000 | ["Disinfection","BlowerCompressorAerator Operation"] | ["Disinfection","BlowerCompressorAerator Operation"] | NA | None | Clear |  | 1.000000 |  | 3.000000 | Effluent Ph 7.2 Effluent DO 7.7 | 07/14/2023 | Sample Tap | 6.780000 |  |  | 8.900000 |  |  | Will be sent separately | Pumped Out | EMI BOD5 and TSS results on hand if needed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/14/2023 | Dec 30 1899 12:05PM
11/03/2023 | Alternative | Routine, Scheduled | 175-08-0286 | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | POINDEXTER, WILLIAM D | 1934000380 | WILLIAM | POINDEXTER | 1.000000 |  | Septic Tank Only | Orenco Advantex | Pump | Distribution Box | Aggregate Trench | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2011 | 12:59 PM
10/19/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 12:00 AM
01/05/2023 |  | RoutineScheduled | 177-STS-90104 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Septic Tank Baffles" ,"Recirculation Pump" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | NA | None | Clear | [5 empty] | 01/05/2023 |  | 7.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. 41 psi. Discharge: HL 17, ETM Om. Peak cts 0, Etm 0m. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
04/10/2023 |  | RoutineScheduled | 177-08-0219-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | There are ants in the first Puraflo module. We recommend treating the area around all modules for ants. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance | 179-10-0163-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance | 175-18-0010 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Microfast needs pumping and repair blower airline. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 08/29/2023 | 03:58 AM
04/28/2023 | Alternative | RoutineScheduled | 031-STS-24108 | Campbell | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 300 | Micro-Fast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | Sludge level-4-5" Scum layer on top- 16" Sludge layer on bottom- Treatment has no aeration and high water level- Blower operational- Cleaned blower airfilter. It was moderatly dirty/dusty. pump tank 6" sludge- Effluent discharge pump and alarm both operational and normal level. Arranged for emergency pump out, Found a blockage from 4 in Knockout had come to block the sample port of 4in pipe by chance and entire system did not flow. Installer was able to remove the blockage and the system should return to normal ioperation. Mound drainfield looks good, Owner will have installed come back to work and inprove the runoff and drainage to reduce any infiltration from rain. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/30/2023 | 09:30 AM
11/03/2023 | Alternative | Follow-Up Component Maintenance | SP-01-453 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Installed inlet and outlet risers on septic tank. Replaced alarm horn. Replaced broken plastic tee for backwash valve #1 with brass tee. Sealed pump tank riser. Sealed conduit penetration on pump tank riser. Added effluent filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
10/18/2023 | Alternative | Routine/Scheduled | 12-163-0005 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level Has no solids with 4" of sludge Customer replaced riser himself -Aeration: At normal level Less than 1" of suspended solids Pulled and cleaned aspirator Pulled and cleaned filter and vault Customer replaced risers himself -Control Panel: Panel replaced last year Working properly Aspirator pulling 4.55amps -Distribution Box: Box at grade At normal level All lines balanced -Drain Field: Showing no signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | Dec 30 1899 11:38AM
01/18/2023 |  | RoutineScheduled | DISCHARGE | Montgomery | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - New River | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 3 Chlorine 5 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/18/2023 | 12:00 AM
04/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/20/2023 | Dec 30 1899 5:20PM
08/31/2023 | Alternative | RoutineScheduled | 104-02-0401 | Amherst | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Effluent filter installed or maintained | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 600 | BioMicrobics Micro Fast 0.5 |  | Pump | Pressure | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | NA | Musty | [15 empty] | Inspected | Septic Recirc Zone 2" scum 20" Sludge- Discharge zone 24" sludge, Pump Tank basin 4" sludge trace- Cleaned blower air filter -Cleaned spin filter- Pump counter 8119 CYCLE 2023 6880 CYCLES 2022 5087 2021 =1239 CYCLES THIS YEAR VS 1793 pump cycles PRIOR YEAR - Pump timer 1183.96 HRS vs 1045.05 in 2022 and 833.30Hrs in 2021. 138.91 hours pumped this year vs about 212 hours pump year- zoner valve box is worn and may need replacement but does not appear to leak. Drain field appears dry. Good aeration was observed in treatment tank. treatment System may need pumped out next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/31/2023 | 09:30 PM
10/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Only one spray head on the EZ treat was functioning. Flushed lines and replaced spray heads. EZ treat should return to proper function. There are roots growing in around the inlet pipe of the clarifying/EZ treat/DF pump tank. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
10/31/2023 | Alternative | RoutineScheduled | 11-113-169 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 8 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/31/2023 | 12:00 AM
09/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Pump | Pressure | Drip | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/05/2023 |  | RoutineScheduled | 124-STS-2379 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Virginia Beach | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 2000 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/01/2023 | Alternative | Initial Visit | 800-STS-15285 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to a pump issue. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the diffuser and the filter in the Clearstream. Changed the filter in the aerator. The timer is set to 49 seconds every 2 hrs 23 mins. Did not take labs. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | Dec 30 1899 12:00PM
12/07/2023 | Alternative | Routine/Scheduled | 196-00-439 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Puraflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/07/2023 | 04:45 AM
05/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Inspection of septic system behind the house. The pvc sewer line was camera snaked and was clear. The septic tank lid was dug up it was 9" under the surface. The tank was pumped out and inspected. There is no inlet T and the pipe coming into the tank isn't sealed at tank wall. The conveyance line was camera snaked. The 4 port concrete splitter box was dug up it was 2 feet below the surface. It is badly deuterated and will need replaced. All 3 conveyance lines coming out of splitter will need replaced. All 3 6 port concrete d-boxes were dug up all were 2 feet below the surface. All 3 are badly deuterated and will need replaced. Also all header lines were camera snaked 6 lines are either crushed or full of roots and will need replaced as needed. At time of inspection the septic system was not in working condition. This inspection does not guarantee the life of any component. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
06/09/2023 | Alternative | Routine/Scheduled | 08-160-0052 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable | 234.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/09/2023 | 12:00 PM
09/07/2023 | Alternative | Reportable Incident | 093-19-0006 | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. Replaced the UV ballast. The septic tank needs to be pumped out and pump the trash out of the Clearstream when doing so. The timer is set to 1.5 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/07/2023 | Dec 30 1899 2:00PM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/24/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/05/2023 | Alternative | RoutineScheduled | 154-13-0121 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend replacing the EZ Set Lid on the Septic Tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance | 182-05-0336 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 06/19/2023 |  | 14.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
01/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | Best 1 | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
06/16/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Solenoid was replaced and the system appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/26/2023 | Alternative | RoutineScheduled | 14-100-0231 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Bundick | Pump | 1.000000 | 500 | Septic Tank | Areo-Flo ATU | Gravity | Pressure | Pad | UV | 450.000000 | ["None"] | ["None"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/25/2023 | 04:20 PM
01/24/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
11/03/2023 | Alternative | Routine/Scheduled | 2019-143-0005 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 550 | Fuji |  | Pump | Pressure | Drip | UV | 350.000000 | SludgeScum Accumulation | SludgeScum Accumulation | N/A | [16 empty] | Pumped Out | Pumped out trash tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/03/2023 | 01:30 PM
05/24/2023 |  | RoutineScheduled | 175-14-0221 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Annual inspection. Owner said that they changed up some of the laundry products they were using, but effluent is still cloudy and at an elevated level in the tank. Recommend chemical cleaning of the media followed by a complete pump-out. Owner should continue to investigate household cleaners and stop using those that contain quaternary ammonium compounds as they are devastating to onsite wastewater treatment. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
05/25/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/02/2023 | Dec 30 1899 2:00PM
04/18/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The Septic and pump tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
10/31/2023 | Alternative |  |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 RT |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | 12:00 AM
03/31/2023 |  | RoutineScheduled | 179-15-0200-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Blower 2.85. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
11/03/2023 | Alternative | Routine/Scheduled |  | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/03/2023 | Dec 30 1899 11:31AM
08/08/2023 | Alternative | RoutineScheduled | 103-STS-96017 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned st and atu filter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/12/2023 | Alternative | RoutineScheduled | 2012-143-0140 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/29/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.130000 | [14 empty] | Blower was not operational. Replaced blower on 12/11/23 | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/13/2023 | 02:10 PM
11/14/2023 | Alternative | Reportable Incident |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | Effluent Screens | YES | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/30/2024 | 12:15 PM
10/24/2023 | Alternative | RoutineScheduled Component Maintenance | 182-16-0020 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
07/12/2023 | Alternative | Routine/Scheduled | 133-STS-104421 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 6.000000 | 5450 | Advanced Septic |  | Pump | Pressure | Pad |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 20.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | 04:54 PM
04/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
04/18/2023 |  | RoutineScheduled | 099-STS-89584 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Control Operation" ,"Disinfection" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Control Operation" ,"Disinfection" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. 2 air release valves missing valve cover lids, recommend putting new ones in. Left note to customer about being careful while mowing drip field, they were very close to breaking air release valves. DISCHARGE: HL 6, ETM 0M, PEAK 8, ETM 12H41M. Pump tank has a lot of steins on walls, but we hose tested n no water came in on those places so will keep an eye on that. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
06/22/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 6.000000 |  | Septic Tank | Septic Tank #2 | Pump | Pressure | Pad | Not Applicable |  | ["SludgeScum Accumulation"] | [] | YES | [17 empty] | Septic Tank #1-4"sludge 4"scum (REQUIRE PUMP OUT DUE TO GREASE MIGRATING TO SEPTIC TANK #2) Septic Tank #2-0"sludge 2"scum/ EZ-Treat #1-3"sludge/ Recirc #2-3"sludge/ Recirc #3-3"sludge/ Pump Tank to LPD Pad-2"sludge/ Recirc Counts: Pump 1- 0014738 ETM-0022137/ Pump 2- 0017061 ETM-0022042/ Discharge Pumps Counts: Pump1- 745 ETM-152h 50m/ Pump2-707 ETM-145h 23m/ Peak-20/ High-18/ Replaced manifold on EZ-Treat Module #2/ No breakout or spongy areas on the LPD Pad site and dosing properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/08/2023 | Alternative | RoutineScheduled | SD-11-392 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Septic tank | PuraFlo | Pump | Gravity | Trenches | Not Applicable | 52.300000 | ["SludgeScum Accumulation","Effluent Screens","Other"] | ["SludgeScum Accumulation","Effluent Screens"] | YES | Septic | Cloudy | [14 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 03:00 PM
02/14/2023 |  | RoutineScheduled | 2006-143-0326 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1500 | MicroFAST |  | Pump | Pressure | Drip |  |  | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/11/2023 | 12:00 AM
11/03/2023 | Alternative | Routine/Scheduled | 2010-143-0125 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 400 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 250.000000 | SludgeScum Accumulation | SludgeScum Accumulation | NO | [16 empty] | Pumped Out | Pumped out trash chamber | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/03/2023 | 12:32 PM
03/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/24/2023 | Alternative | RoutineScheduled | 165-STS-334024 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 05/24/2023 |  | 8.000000 | [5 empty] | Will be sent separately | Inspected | Lab Sample Normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/21/2023 | 03:35 PM
11/10/2023 | Alternative | RoutineScheduled | SD-05-217 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2000 | septic | BEST 1 | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/19/2023 | 08:45 AM
03/08/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | filler clog | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
09/02/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | YES | Septic | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 12:00 AM
03/16/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2024 | Dec 30 1899 11:49AM
01/27/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Lord Fairfax | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Omron timer's display was irregular and could not be reset. Also, the 1 and 2 switches would not manually activate the pump or blower. Replaced, programmed, and tested a new Omron timer. Replaced the air filter. Repaired fiberglass damage to the dosing tank manway. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
12/08/2023 | Alternative | Follow-Up | 165-STS-339630 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 RT |  |  | Pressure | Drip | Not Applicable |  | [] | [] | [18 empty] | follow up | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/08/2023 | 12:00 AM
10/19/2023 | Alternative |  | 182-16-0133 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | None | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 12:00 AM
07/29/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced zoner. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
11/02/2023 | Alternative | Routine/Scheduled | 800-13-0098 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | Dec 30 1899 9:26AM
03/07/2023 |  | RoutineScheduled | 175-10-0047 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank / ATU | Pump Tank | Pump | Gravity | Discharge | UV |  | ["Disinfection","BlowerCompressorAerator Operation"] | ["Disinfection","BlowerCompressorAerator Operation"] | NA |  |  | 7.100000 |  |  |  | E.coli-488/100mL | 03/07/2023 | Sample Chamber | 2.000000 |  |  | 44.000000 |  |  |  |  | Septic-2"sludge 0"scum/ ATU-0"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-8385 ETM-664h 54m On-4m 48s Off-4h 46s / High-79 / UV-Light is faulty and requires replacement/ Lid on the sand filter requires replacement and completed on 3/31/2023/ Sand in the sand filter was turned and in good condition, no ponding. UV-Light repair completed on 3/17/2023 and functioning properly at this time. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
08/16/2023 | Alternative | RoutineScheduled | 119-STS-95142 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001302 | Charles | Langford | 2.000000 | 1000 |  |  | Pump | Pressure |  |  |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump 1 of 2 is not functioning at this time. Homeowner is reaching out to get pump replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
05/24/2023 | Alternative | Routine/Scheduled | 151-04-094 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced Pump Basin - float sensors, pump and controls operating. Biofilter - peatmoss in good condition - raked / turned DBox - plastic - at grade and intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 11:00 AM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, UC Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/15/2023 | Alternative | RoutineScheduled | 117-STS-15216 | Mecklenburg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Southside | Ratcliff construction inc | 1944001614 | Steve | Ratcliff | 1.000000 | 1000 | 1 | 800 | Gravity | Gravity | Discharge | UV |  | ["None"] | ["None"] | NA | None | Clear |  |  | 1.000000 |  |  | 02/15/2023 | Sample Tap | 2.000000 |  |  | 1.000000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | 07:03 PM
01/09/2023 |  | Routine/Scheduled | 550-STS-6335 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | Jan 1 1900 10:30AM
07/12/2023 | Alternative | Routine/Scheduled | 175-05-0063 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | Dec 30 1899 8:30AM
03/10/2023 |  | RoutineScheduled | 099-STS-89474 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
06/02/2023 | Alternative | RoutineScheduled | 181-05-0406 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | Septic Tank Only | AdvantexAX20 | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. Both pumps were pulled and sprayed off. The textile sheets were sprayed off. The laterals in the treatment unit was cleaned. The pressure was adjusted on the treatment unit. The controls were operating as designed. There were no visible leaks in the drip field. There was return effluent returning to the pump tank so the drip field was operating as designed. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/06/2023 | 11:30 PM
02/23/2023 | Alternative | RoutineScheduled | 109-STS-32517 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/25/2023 | 12:00 AM
08/04/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.620000 |  |  | 0.600000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/15/2023 | 12:00 AM
09/05/2023 | Alternative | RoutineScheduled Component Maintenance | 177-09-0024-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend replacing both lids on the septic tank. We also recommend treating the area around the Puraflo modules for ants. Roots are starting to grow into the Puraflo modules. This may make it difficult to service the peat at some point in the future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
05/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/02/2023 | Alternative | RoutineScheduled | 12-142-0135 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/11/2023 |  | RoutineScheduled | 03-100-1092 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | [] | [] | YES | [17 empty] | Everything working as it should. Raked peat. Peat looks good in all 4 pods. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/12/2023 | 12:55 PM
03/27/2023 | Alternative | RoutineScheduled | 16-184-5001 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/27/2023 | 12:00 AM
05/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/25/2023 | Alternative |  | 195-Discharge-29122 Jeb Syuart Hwy | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/25/2023 |  | 5.270000 |  |  | 1.200000 |  |  | Will be sent separately |  | BOD: 5.27 TSS: 1.20 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/25/2023 | 12:00 AM
06/05/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-87861 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 4.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation" ,"BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | ["Level Sensor Operation" ,"Control Operation" ,"BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Peak float was stock close in grinder pump tank, replaced. Peak counts 210300. Hl 93771. System barely out of high level due to a very busy weekend. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
01/03/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1500 | Septic | Puraflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/30/2023 | Alternative |  |  | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 12:00 AM
10/17/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0144-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Small roots on wedge lids but no infiltration. Pump slowing down, will have to be upgraded when fails. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
04/27/2023 |  | RoutineScheduled | 2011-143-0137 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C & E Mechanical Corporation | 1942001339 | Louis | Timberlake | 1.000000 | 1000 | PremierTech EcoFlo |  | Pump | Pressure | Trenches | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation","Level Sensor Operation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [6 empty] | Recommend pumping in 3 to 4 years | [9 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 02:30 PM
12/05/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2024 | Dec 30 1899 12:23PM
05/22/2023 | Alternative | Routine/Scheduled | 08-174-0104 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Microfast |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/22/2023 | Dec 30 1899 8:50AM
04/24/2023 |  | Routine/Scheduled |  | Lancaster | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - effluent screen broken - serviced - root intrusion in tank. Biofilter - fiberglass - has fracture allowing infiltration - peatmoss spent, compacted - root intrusion - tipping bucket broken. Pump Basin - plastic - bulging present - float sensors, pump and controls operating. DBox - plastic - slight deformity present NOTE - Inspection Notes dating back to 2020 have noted these issues. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/25/2023 | 07:30 AM
08/07/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None |  | 7.210000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | 11:15 AM
09/20/2023 | Alternative | Reportable Incident | 128.07.118 | Essex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [16 empty] | Pumped Out | 9/20 Pump Out: * pumped flooded micro fast system * pumped 1250 gallons 9/21 Consultation: - Came out for a consultation. Found no power to discharge pump breaker or microfast blower. Found breaker off inside the house. Found floats to be internally failing. Made recommendations and customer approved 9/21 Repair: -Installation of a water-resistant SB4 Junction Box inside a Riser includes Conduit and Grommet Kit -Installation of 3 Floats -Tested all components upon completion and everything is working properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/06/2023 | 03:39 PM
05/04/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Puraflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/04/2023 | Dec 30 1899 1:03PM
09/13/2023 | Alternative | RoutineScheduled Component Maintenance | 179-09-0194-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | UV |  | ["Disinfection" ,"BlowerCompressorAerator Operation"] | ["Disinfection" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
02/20/2023 | Alternative | Pump-Out Only | -STS-13556 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner |  |  | Microfast | [6 empty] | [] | [] | [17 empty] | Pumped Out | Pumping & Cleaning Septic Tank (1000 gallons) JOB SCOPE: Pumped/cleaned septic tank; septic system is functioning at this time but not as designed as there are components that are recommended to be repaired/replaced. - media needs to be repaired/upgraded - customer does not want to proceed with annual maintenance at this time | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 02/22/2023 | 12:00 AM
09/13/2023 | Alternative | Reportable Incident | 151-18-0089 | Lancaster | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [16 empty] | Pumped Out | 9/13/23 Truck 605 * Arrived for Pump out of Aeration Tank * Pumped 750 Gallons * Cleaned Tank out * Refilled Tank | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/04/2023 | 02:35 PM
04/06/2023 | Alternative | Initial Visit | 800-STS-14575 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the UV ballast. Did not take the samples due to the UV not working on arrival. The timer is set to 2 minutes every 1 hour. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/06/2023 | Dec 30 1899 1:45PM
11/14/2023 | Alternative | RoutineScheduled Component Maintenance | 099-STS-87264 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The electrical conduit has pulled out of the junction box. We recommend removing the junction box off of the wall, adding a new section of conduit, and remounting the junction box. We will need someone home to turn power off and turn it back on | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
08/08/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Pending Review | EHD - West Piedmont | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | investigating wet spot nbear the treatment unit. After testing and digging up a huge area around the tank and camering the septic lines we found no leaks from the septic system. We did find it appears to be wet from the heavy wet spring and summer and 3 hours of lawn irrigation flodding the shaded septic area along a narrow path and side of the home. Reccomend to reduce or eliminate this irrigation zone. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | 09:30 AM
10/12/2023 | Alternative | Routine/Scheduled | 093-18-0138 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Outlet tee appears to be intact. No riser access. Due for pump out -Discharge/Pump Tank: Water level high. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Flushed and cleaned vortex filter. Checked and confirmed UV system is functioning properly. -Aeration: Water level high. Flushed and cleaned weir. Flushed and cleaned diffuser. Checked and confirmed high level alarm float is functioning properly. Due for pump out. Refill is required for proper operation and to prevent damage to components. -Air Pump/Blower: Checked and confirmed aerator is functioning properly. Flushed and cleaned aerator air intake filter. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarms are functioning properly. Checked and confirmed visual alarms are functioning properly. -Drip Field: Homeowner added top soil about 3 weeks ago. Soil is still soft. Noted some spots where surfacing is still occurring which may be result of the soil being soft. Checked inspection ports and water level is about 12" below grade. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/27/2023 | Dec 30 1899 2:27PM
10/06/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-24251 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.500000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
04/27/2023 |  | RoutineScheduled | 154-16-0006 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco | Norweco | Pump | Pressure | Mound | Not Applicable | 1000.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/04/2023 | 12:00 AM
05/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
09/12/2023 | Alternative | RoutineScheduled | 175-97-0239 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Pressure | Trenches | Not Applicable |  | ["Other"] | ["Other"] | YES | [17 empty] | Septic Tank-4"sludge 2"scum/ Pump Tank-2"sludge/ No pump out needed at this time/ Controls box alarm buzzer replaced/ Controls, pump, floats and alarms now functioning properly/ No counts on the control box/ Found the pump tank junction requires replacement also repair needed on the concrete riser, LPD globe valve handles need replacement/ Repairs to be done at a later date/ No breakout or spongy areas on the LPD Drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
04/17/2023 |  | Routine/Scheduled | 234-17-0008 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | Jan 1 1900 10:40AM
12/06/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | YES | Septic | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 12:00 AM
01/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2023 | Dec 30 1899 8:47AM
08/08/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 |  | LPD |  | Pump | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/26/2023 | 12:00 AM
01/19/2023 |  | Reportable Incident |  | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Three Rivers | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Alarm Event - no power to system - Electrician Required. Pumped septic tank empty for storage - | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/23/2023 | 07:30 AM
05/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/23/2023 | 09:32 AM
02/22/2023 | Alternative | Routine/Scheduled | 093-16-0014 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 4.000000 | [7 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 3 minutes every 2 hours. Took 5 year BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | Dec 30 1899 10:30AM
07/07/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20463 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
02/24/2023 |  | RoutineScheduled | 179-06-0016-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Disinfection" ,"Dispersal System Operation" ,"Level Sensor Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for rountine inspection and system was in alarm due to field flush diaphragm being clogged cause system to constantly flush. Hvac equipment needs to be removed from dripfield. Drip rate and field flush has dropped . proposal to be sent to bleach flush drip tubing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
10/23/2023 | Alternative | RoutineScheduled | 09-197-A4 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
07/27/2023 | Alternative | Routine/Scheduled | 06-160-0297 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 113.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | 12:00 PM
09/15/2023 | Alternative | RoutineScheduled Component Maintenance | 196-07-196 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Three Rivers | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Effluent Screens"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
03/16/2023 |  | Routine/Scheduled | {FIPSCode}-STS-3500 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/16/2023 | Jan 1 1900 2:40PM
06/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 06/29/2023 |  | 51.000000 | [5 empty] | Will be sent separately | Inspected | Replaced zone valve and valve box cover | This AOSS should now return to normal function after having provided the above state routine maintenance | 08/23/2023 | 06:57 AM
09/05/2023 | Alternative | Routine/Scheduled | 234-14-405 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | Dec 30 1899 9:15AM
10/10/2023 | Alternative | RoutineScheduled | 087-STS-6676 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 1.000000 |  | Bio Gator |  | Gravity | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation"] |  | Musty | Cloudy | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/10/2023 | 12:00 AM
05/23/2023 |  |  | 033-17-0189-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
09/20/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | MicroFast needs pumping. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | Dec 30 1899 12:58PM
08/02/2023 | Alternative | Routine/Scheduled | 109-STS-31178 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 200.000000 | Dispersal System Operation | Dispersal System Operation | NO | [7 empty] | 08/02/2023 | Pump Chamber | 2.000000 | [5 empty] | Will be sent separately |  | Sample taken. Board reset | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/14/2023 | 11:22 AM
08/09/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
12/08/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-89749 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Auxiliary Filter"] | ["Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Auxiliary Filter"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
06/16/2023 | Alternative | Routine/Scheduled | 149-STS-10585 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/16/2023 | Dec 30 1899 2:41PM
04/03/2023 |  | Pump-Out Only |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 10:03 AM
09/06/2023 | Alternative | RoutineScheduled | 181-13-0059 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | Sand Mound | Pump | Gravity | Mound | Not Applicable |  | ["None"] | ["None"] | NA | [7 empty] | 09/06/2023 | Sample Chamber | 9.900000 | [5 empty] | Attached to this report |  | The system did not need to be pumped. The effluent filter was pulled and cleaned. The controls were operating as designed. There were no visible leaks in the sand mound. The BOD was well in the permitted limits. the TSS was not drawn due to the sample port being designed to small. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/26/2023 | 04:10 PM
09/06/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | UV |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | 7.800000 | 14.900000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/15/2023 | Dec 30 1899 2:41PM
08/09/2023 | Alternative | RoutineScheduled Component Maintenance | SP-05-708 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | Broken conduit will be patched by the homeowner. One of the three RSV nipples is missing. We recommend pumping the Advantex tank due to sludge accumulation in the tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
06/08/2023 |  | RoutineScheduled | 175-17-0411 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Microfast unit needs pumping. UV unit needs replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | 12:05 PM
08/22/2023 | Alternative | Routine/Scheduled |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced - recommend pumpout of processing tank. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | 07:00 AM
01/18/2023 | Alternative |  | 150-18-0150 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | 12:00 AM
01/16/2023 | Alternative | Routine/Scheduled | 136-18-0060 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 2 minutes every 1 hour. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | 10:30 AM
12/19/2023 | Alternative | Routine/Scheduled | 041-STS-261455 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 750 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | Dec 30 1899 11:30AM
03/28/2023 | Alternative | Routine/Scheduled | 136-99-0350 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | AOSS - Initial Visit - Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Biofilter - peatmoss in extreme poor condition - requires replacement. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 10:30 AM
03/22/2023 | Alternative | Routine/Scheduled | 166-18-176 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash Tank - normal level. Aeration Tank - normal level - mixing present - compressor serviced. PUmp Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/23/2023 | 08:00 AM
03/28/2023 |  |  | 177-08-0237-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
02/17/2023 |  | Routine/Scheduled | 17-137-0126 | Goochland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Multiflo ATU |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/17/2023 | Jan 1 1900 4:13PM
06/03/2023 | Alternative | RoutineScheduled | 109-10-0439 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 14" of accumulated solids in septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. Sprayed off treatment unit "sheets". Cleaned recirculation pump basket filter. 12" of solids in recirculation portion of treatment unit. 10" of solids in discharge portion of treatment unit. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 07:03 PM
05/16/2023 |  | RoutineScheduled | SWP-04-352 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Media showing its age maybe 2 more years left, evaluate next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
04/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Best 1 gravity septic system | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
04/25/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
02/07/2023 |  | Routine/Scheduled | 810-STS-4065 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  |  | Pressure |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/07/2023 | Jan 1 1900 10:00AM
12/01/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 01:40 PM
12/19/2023 | Alternative | Routine/Scheduled | 041-STS-261275 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 750 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | Dec 30 1899 9:30AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/16/2023 | Alternative | RoutineScheduled Component Maintenance | 107-16-0219 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 10/16/2023 |  | 124.000000 | [5 empty] | Will be sent separately | Inspected | Replaced alarm float | This AOSS should now return to normal function after having provided the above state routine maintenance | 11/22/2023 | 09:18 AM
12/28/2023 | Alternative | Reportable Incident Component Maintenance | 177-08-0240-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to failed alarm float sending a false alarm. Replaced failed float. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | 09:40 AM
05/02/2023 |  | RoutineScheduled | SWP-03-519 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity |  | Not Applicable |  | ["Attached Growth Medium" ,"Disinfection" ,"Effluent Screens" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Disinfection" ,"Effluent Screens"] | YES | Musty | Clear |  | 9.750000 |  |  |  | 05/02/2023 | Sample Chamber | 4.000000 |  | 1.000000 | 2.300000 |  |  | Will be sent separately | Inspected | Added 1" union to EZ Treat pump | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
08/12/2023 | Alternative | RoutineScheduled |  | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2000 | septic | advantex | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | 08:00 AM
01/20/2023 | Alternative | Reportable Incident | 171-11-0041 | Pittsylvania | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20-RT |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Control Operation"] | ["Effluent Screens","Control Operation"] | NA | [16 empty] | Inspected | RTU122504 - Recirc Pump is PF0300311, Dischagre pump operational (pf200511), all floats tested operational. Meter readings- Recirc pump - 1534 Min- old reading 1402 Min and 69,135 Cycles old reading 43,637 Cycles - Discharge Pump 1657.5 min old reading 1201 Min and 50023 Cycles old reading last year 43251 Cycles. Today we repaired the Drip filter headworks box allowing for the filter to be accessed and cleaned, backwashed and flushed the filter. Repaired the drain line entering the septic tank which hads a significant infiltration leak of water entering the pump tank.. Alarm cleared after service and unit returned to normal operation. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/31/2023 | 09:30 AM
06/19/2023 | Alternative | RoutineScheduled | 047-17-083 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
10/30/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/30/2023 | Dec 30 1899 9:00AM
05/09/2023 |  | Pump-Out Only | 234-13-191 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/09/2023 | Jan 1 1900 9:00AM
12/27/2023 | Alternative | RoutineScheduled | 155-STS-11608 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | 1.000000 | 1000 | MICROFAST |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] |  | Septic | Cloudy | [5 empty] | 12/27/2023 | Sample Tap | [6 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 12:00 AM
05/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/06/2023 | Alternative |  | 195-Discharge-21118 Grassy Ridge Road | Washington | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 4 - Blue Crystal tablets installed 8 - Bio Max tablets installed Replaced timer | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 09/06/2023 | 12:00 AM
10/04/2023 | Alternative | Reportable Incident | 228-13-0174 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. Replaced the buzzer. The septic tank needs additional risers on it to be properly inspected in the future. The timer is set to 2 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/04/2023 | Dec 30 1899 9:30AM
02/15/2023 |  |  | 099-06-0347-SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
05/01/2023 |  | Routine/Scheduled | 228-17-0185 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | Jan 1 1900 11:00AM
04/07/2023 |  | RoutineScheduled | 179-15-0220-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
03/10/2023 |  | Initial Visit |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip |  |  | ["Attached Growth Medium","Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | [18 empty] | livestock on system. Not recommended | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
12/23/2023 | Alternative | RoutineScheduled | 133 10 0206 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 2000 | EZ Treat |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Fourth quarter 2023 inspection. Cleaned recirculation tank filter. Tested floats, pumps and alarm. Spray heads spraying very good. Restaurant is on a regular grease trap pump out schedule. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/05/2024 | 07:03 PM
07/31/2023 | Alternative | RoutineScheduled Component Maintenance | 177-10-0273-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
12/27/2023 | Alternative |  | 182-99-0577 (LEGACY SPRAY ALT. SYSTEM) | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Sand |  |  | Pressure | Discharge | Not Applicable |  | ["None"] | [] | [19 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/09/2024 | 12:00 AM
08/16/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-92271 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [5 empty] | 08/16/2023 |  | 12.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Septic tank inlet riser is missing a small section of top lip, will need replace if it gets hit again. HL-8, LL-17, OVERRIDE-2. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
05/16/2023 | Alternative | Routine/Scheduled | S 800-17-0099 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Biofilter - peatmoss in fair condition - raked / turned. Pump Basin - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | Dec 30 1899 8:45AM
04/22/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | Musty | [14 empty] | Will be sent separately | Inspected | Follow-up visit. Replaced the blower running (green) indicator light assembly that was identified as non-functioning during the January inspection. Air pre-filter cleaned as preventative maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 06:43 AM
05/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
03/24/2023 |  |  | 145-STS-257581 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 1.000000 | 1962 | 1962 |  | Pump | Gravity | Trenches | UV |  | [] | ["Control Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles"] | YES | None | Clear | 7.000000 |  | 7.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/24/2023 | Jan 1 1900 1:30PM
12/05/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Rejected | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | FAST |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 4 - Blue Crystal Tablets Installed 10 - Bio Max Tablets Installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/05/2023 | 12:00 AM
07/08/2023 | Alternative | RoutineScheduled | SD-15-64 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1500 | septic | Puraflo | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | 08:40 AM
06/14/2023 | Alternative | RoutineScheduled Component Maintenance | 154-08-0055 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend replacing the filter for the air pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
11/20/2023 | Alternative | Follow-Up | 07-160-0147 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | [9 empty] | [] | [] | [18 empty] | 10/12/23 Service Visit - arrived on site to replace effluent pump and found pump to be functional - recommend installation of new alarm box. 11/20/23 Installation of New Alarm Box - installed new alarm box, everything is now functioning properly. - recommend that the alarm box be placed on an independent receptacle and have its own breaker | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/29/2023 | 12:00 AM
08/02/2023 | Alternative | Routine/Scheduled |  | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | EZ Treat Sandfilter |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles"] | YES | [16 empty] | Pumped Out | Routine pumpout as recommended during last service event. Pumped septic tank empty - serviced. Pumped processing tank empty - serviced - refilled with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/03/2023 | Dec 30 1899 6:45AM
03/29/2023 |  |  | 19-172-0185A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 1.000000 | 1962 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","SludgeScum Accumulation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles"] | YES | Pungent | Discolored | 7.000000 |  | 6.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | Jan 1 1900 2:30PM
11/17/2023 | Alternative | Follow-Up Component Maintenance | 179-STS-92341 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Sealed all risers on tanks. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 02/13/2024 | 11:49 AM
09/11/2023 | Alternative | Reportable Incident | 550-STS-6526 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Owner called due to an alarm. Replaced the UV light bulb. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/11/2023 | Dec 30 1899 12:00PM
12/11/2023 | Alternative | Reportable Incident Component Maintenance | 099-18-0080 SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles"] | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Complaint inspection. System was on high level due to bad pump, replaced old n98 pump with new champion cpe3 and new pump does 64.1 gallons per minute so run time stays the same to get rid of full dose. HL-11, LL-21, OVERRIDE-4. Microfast media not on high level anymore customer added a gallon of concentrated bleach and took care of filamentus bacteria, Treatment is crystal clear. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
07/17/2023 | Alternative | RoutineScheduled | 13-120-0184A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | NA | [17 empty] | Replaced on/off float switch and repaired pump line. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | 12:00 AM
09/25/2023 | Alternative |  | 166-13-214 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
03/30/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/19/2023 | Alternative | Routine/Scheduled | 041-STS-261304 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 600 |  |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | Dec 30 1899 9:00AM
11/15/2023 | Alternative | Routine/Scheduled | 166-14-150 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level No solids with 4" of sludge Pulled and cleaned filter -Discharge/Pump Tank: At normal level Pump and floats working properly -Peat Moss: Tipping bucket working Peat still in decent shape Racked out holes -Control Panel: Outside is showing aging but inside is clean Working properly All visual and audible alarms working Discharge pump pulling 6.64amps -Distribution Box: At normal level All lines taking water properly No signs of cracks or bulging -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | 01:15 PM
01/13/2023 |  | RoutineScheduled | 177-STS-90221 | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | ["Effluent Screens" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | YES | [15 empty] | Will be sent separately | Inspected | There is effluent surfacing at the end of the drainfield lines. We are providing a copy of this report to the builder & system designer so they will be aware of this issue. Health Dept: Reached out to Ed Scott with Ecoseptix. He stated he sent the report to OSE/builder and has not heard back. On 3/7/23, MW reached out to OSE, Rodney Whittaker, to see if anything has been done and/or plans. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/02/2023 | 07:17 AM
06/02/2023 | Alternative | Pump-Out Only | 02-120-0593AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 750.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Supervised pumpout of primary septic tank and processing tank. Installed access riser on septic tank Re-sealed risers on processing tank Refilled processing tank with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/07/2023 | Dec 30 1899 12:15PM
11/01/2023 | Alternative | Routine/Scheduled | 09-120-0347R | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level Has 3" of solids with 10" of sludge Should be pumped soon Riser section is broken, customer keeps tape on it -Discharge/Pump Tank: At normal level Pump and floats working properly -Aeration: Aeration at normal level Tank is almost completely full of sludge and needs to be pumped and refilled. -Air Pump/Blower: Working properly Pulled and cleaned filter -Control Panel: Visual and audible alarms working Discharge pump pulling 9.40amps -Distribution Box: At grade At normal level -Drain Field: Showing no signs of surfacing or blowouts | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | Dec 30 1899 10:28AM
05/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2024 | 12:23 PM
02/23/2023 |  | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [6 empty] | Level Sensor Operation | Level Sensor Operation | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/23/2023 | 10:43 AM
09/19/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Cloverleaf Environmental Consulting, Inc | 1942001135 | Robert | Charnley |  |  | Advantex |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Level Sensor Operation","Recirculation Pump"] | ["Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
01/24/2023 | Alternative | Routine/Scheduled | 151-04-043 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1500 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 75.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 03:35 PM
08/23/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-126 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
05/15/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Whitewater |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Called due to an alarm- Replaced Clogged spin filter, reglued pump pipe stem which had separated after pulling pump and cleaning the intlet screen.Pump reading 947,500 versus 947,350 last visit a month ago- | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
10/10/2023 | Alternative | RoutineScheduled | 166-13-097 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Elite Onsite | 1942001726 | Drew | Saunders | 2.000000 | 2000 | 1500 | 500 | Pump | Pressure | Drip | Not Applicable | 325.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/10/2023 | 03:30 PM
03/27/2023 | Alternative | Routine/Scheduled | 166-05-804 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Ecoflo |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/27/2023 | 04:00 PM
04/18/2023 | Alternative | RoutineScheduled | 061-STS-22555 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/12/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Service call : Replaced Gast Blower / Now functioning properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
02/03/2023 |  | RoutineScheduled | SWP-04-355 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 1-6 | 0-0 0-1 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [5 empty] | 12.000000 | [11 empty] | Inspected | peat moss is degrading will send a proposal to home owners for replacement | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | 02:00 PM
06/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
11/01/2023 | Alternative | RoutineScheduled Component Maintenance | 175-19-0168 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
09/13/2023 | Alternative | RoutineScheduled | 14-197-A3 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 |  | ATU |  | Pump | Gravity | Discharge | Chlorination |  |  |  |  | Sulphitic | Clear | 5.500000 | 2.000000 |  | 0.000000 | NO tablets | [10 empty] | Odor yes and no tablets | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
06/08/2023 | Alternative |  | 18-197-A1 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 06/08/2023 |  | 4.620000 | [5 empty] | Will be sent separately |  | BOD: 4.62 TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | 12:00 AM
11/27/2023 | Alternative | RoutineScheduled | 115-14-0009 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Auxiliary Filter"] | ["Distribution Pump Operation","Effluent Screens"] | NA | Musty | [15 empty] | Inspected | Sludge levels-Scum layer 1-2" in. and 10-12" sludge in upper Septic tank #1- Heavy plant matter noted. -Septic zone/recirc minimal scum and 4-6" Sludge and 16" Sludge in Discharge zone of tank. Pump tank fine sludge. System was pumped 3 years ago and may need pumping this year. Upper tank effluent screen was clogged and we cleaned. The bio filter was very dirty but had not fully clogged. Both Pumps are operational. sprayed off media and manifold, Pulled and cleaned RSV. floats all responding. Ran system in test mode to flush it. Drainfield has been cut over and the drip drainfield was ok. Recirc pump 3447.2 Hours and 79,588 cycles. The discharge pump has 1716 hours and 73,607 cycles. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
01/23/2023 | Alternative | Reportable Incident | 115-STS-101722 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 300.000000 | ["Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | COSS - Maintenance - GMP2018-02 - VDH HDID 157-22-0141 Pumped empty, crushed and backfilled existing 750g septic tank. Installed new 4" PVC sewer line. Installed new 1000g concrete mid-seam septic tank with effluent screen and access riser. Installed new 4" PVC conveyance line. Installed new 8 port concrete DBox & Header lines. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/24/2023 | 07:00 AM
10/21/2023 | Alternative | Reportable Incident | 136-06-0396 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm Call: Underground put in plumbing backwards so pump wasn't moving water Wired panel up wrong so pump wouldn't come on automatically On off float went bad due to the wrong wiring - all components fixed and working as should | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 02:02 PM
02/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | YES | [17 empty] | Septic Tank-6"sludge 1"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ LPD Pump drawdown- 4" in 1 minute/ On-2m Off-12h/ Controls, pumps, floats and alarms functioning properly/ No breakout or spongy areas on the LPD Drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/24/2023 | Alternative |  | 139-03-0057 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Joanna & Mike | McDonough | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance | 107-06-0627 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
03/11/2023 |  | Routine/Scheduled | 127-STS-34041 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 1250 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/11/2023 | Jan 1 1900 11:00AM
02/11/2023 |  | RoutineScheduled | 2069-02-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination | 500.000000 | ["Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | NO | Musty | Clear | 7.300000 |  |  | 1.500000 |  | 02/13/2023 | Sample Chamber | 6.000000 |  |  | 8.500000 | [5 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/23/2023 | 12:00 AM
09/27/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
06/30/2023 | Alternative | Routine/Scheduled | 12-120-0113A | Chesterfield | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Rejected | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Trash Tank - normal level - recommend pumpout Aeration Tank - Aspirator tip broken - no mixing present! Clarifier - effluent screen serviced. Pump Tank float sensors, pump and controls operating. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/05/2023 | Dec 30 1899 9:00AM
02/08/2023 |  | RoutineScheduled | 033-STS-90511 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Owner called with an alarm. Reconnected recirc pump union and replaced float under warranty. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
04/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/10/2023 | 11:17 AM
01/23/2023 |  |  | SR-05-351 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
05/19/2023 |  | Reportable Incident | 2015-143-0169 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Owner called due to an alarm - replaced the UV light bulb. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/19/2023 | 12:00 PM
12/20/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Henrico | Drainfields LLC | 1942001219 | Gene | Shanks | 2.000000 | 1250 |  |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 10:00 AM
04/27/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/22/2023 | 11:15 AM
10/09/2023 | Alternative | Routine/Scheduled | 166-16-009 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Found at normal level, 3in of sludge and less than 1in of solids. Pulled and cleaned filter. Riser was installed with spray foam, riser showing signs of leaking. -Discharge/Pump Tank: Found at normal level, tested floats and pump. All working as they should. Pump and floats are aged. -Peat Moss: Tipping bucket and trays are in working order. Raked out peat on both sides. Peat is broken down and compacted. Recommend peat change -Control Panel: 120 volts audio and visual alarms working as they should. Buzzer is working just not as loud. -Distribution Box: Customer declined digging up dbox this year. Will need to inspect next year -Drain Field: No signs of surfacing in drainfield area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 01:24 PM
03/14/2023 |  | Routine/Scheduled | 15-120-0396AR | Chesterfield | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesterfield | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1250 | Multiflo ATU |  | Pump | Pressure | Drip | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [17 empty] | Compressor was found working. Alarm for control panel was not working. Audible alarms for discharge and flow equalization pump systems were found disconnected. The access risers for the septic, flow equalization, and discharge tanks were tested for leaks and leaks were observed in all of them. The cord grips on the flow equalization electric splice box were broken. The compressor needs to be replaced. The risers need to be sealed. The audible alarm for the compressor needs to be repaired or replaced. The cord grips need to be replaced. Water records should be shared with ODO, Inc. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/15/2023 | Jan 1 1900 8:02AM
02/01/2023 | Alternative | Pump-Out Only | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 | 500 | 1000 |  | Pump | Pressure | Drip | Not Applicable |  | ["SludgeScum Accumulation"] | [] | NA | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | Dec 30 1899 1:30PM
11/02/2023 | Alternative | RoutineScheduled | 185-STS-17515 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | ADVANTEX |  | Pump | Pressure | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","Disinfection","Distribution Pump Operation","Recirculation Pump","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Disinfection","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 4 - Blue Crystal tablets installed 12 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/02/2023 | 12:00 AM
02/22/2023 |  | Routine/Scheduled | 087-STS-6589 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/22/2023 | 02:29 PM
05/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
02/08/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | Jan 1 1900 10:55AM
05/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend replacing UV bulb. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/23/2023 |  | RoutineScheduled | 12-100-0319 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 18.000000 | 1,000 GALLON PER RESIDENCE | PURAFLO |  | Pump | Pressure | Pad | Not Applicable | 2375.000000 | [] | [] | YES | [17 empty] | EVERYTHING WORKING AT PUMP STATION . PEAT LOOKS GOOD AND EVEN WITH MANIFOLD. PUMPED SEPTIC AT FOLLOWING ADDRESSES: 8289 SEA BREEZE 8284 SEA BREEZE 8262 SEAGULL 8258 SEAGULL 8271 SEA BREEZE | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/08/2023 | 12:00 AM
04/01/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/09/2023 | 12:00 AM
05/08/2023 |  | Routine/Scheduled | 550-STS-6400 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | Jan 1 1900 2:35PM
09/07/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Bio Barrier | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
09/25/2023 | Alternative | RoutineScheduled Component Maintenance | SWT-04-497 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"SludgeScum Accumulation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend scraping the Advantex sheets and pumping the Advantex tank and pumping the tank after the sheets are scraped. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
03/28/2023 |  | RoutineScheduled | 185-STS-17513 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Disinfection","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/28/2023 | 12:00 AM
04/05/2023 |  | Reportable Incident |  | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Hydro-Action ATU |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | AOSS - Initial Visit Septic tank pumped 04/01 - owner did not realize has an AOSS! Effluent screen serviced. Aeration tank - normal level - aeration compressor failed - replaced and put back into operation. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/06/2023 | 08:30 AM
08/15/2023 | Alternative | Reportable Incident | 108-05-0043 | Bath | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 750 | Septic Tank Only | Delta Whitewater | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NO | [17 empty] | The system did not need to be pumped. The blower had quit working so a new blower was installed. and the system is working as designed. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/28/2023 | 02:25 PM
04/24/2023 |  | Reportable Incident | 228-13-0534 A | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Replaced the P-20 pump (new serial # 2207-139423). Meet with the pumping company - pumped out the Clearstream tank and pumped out the septic tank. The timer is set to 6 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/24/2023 | Jan 1 1900 12:15PM
10/23/2023 | Alternative |  | 04-197-A4 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination | [22 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
06/13/2023 | Alternative | RoutineScheduled Component Maintenance | 061-STS-23024 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001236 | Stuart | Lynn |  |  | Whitewater ATU | Whitewater ATU | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | ["BlowerCompressorAerator Operation"] | NA | None | Clear | [5 empty] | 06/12/2023 | Pump Chamber | 7.000000 |  |  | 3.000000 | 5.000000 |  | Will be sent separately | Inspected | Routine service and filters cleaned flow meter replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | 01:58 PM
05/01/2023 | Alternative | Routine/Scheduled | 151-05-109 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 2000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - recommend pump out. Secondary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Biofilter Modules - (5) - Peatmoss in poor condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | 07:00 AM
10/19/2023 | Alternative | RoutineScheduled | 121-STS-12047 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000 | Whitewater |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 12:00 AM
10/04/2023 | Alternative | RoutineScheduled | 019-STS-24753 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank Pumped | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Advantex AX25 RT |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Both Septic tank were pumped out by Foutz Septic. Recommend to refill plastic tank with water soon after pump out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | 09:30 AM
10/13/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | 12:00 AM
06/28/2023 | Alternative | Routine/Scheduled | 166-07-226 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. BioFilter - peatmoss spent - requires replacing - raked best able Pump Tank - float sensors, pump and controls operating. DBox - plastic - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/29/2023 | 07:30 AM
11/14/2023 | Alternative | RoutineScheduled | 139-04-0281 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | ["Attached Growth Medium","Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | 12:00 AM
12/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2024 | 11:49 AM
01/24/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.810000 |  |  |  |  | 01/24/2023 |  | 104.000000 |  |  | 25.700000 |  |  |  |  | Blower is bad, and system needs pumped. Will resample after both are done. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 02/14/2023 | 08:00 AM
08/31/2023 | Alternative | Initial Visit |  | Petersburg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Crater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Visit - Alarm Event Found discharge pump plumbing broken at flow inducer - repaired. Trash Tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating - repaired. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | Dec 30 1899 11:30AM
05/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The lids were not screwed in. Hardware was replaced at the time of inspection. Blower was replaced by others. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/01/2023 |  | RoutineScheduled | 16-165-0130 | Northampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Bundick | Pump | 7.000000 | 19,600 | Septic Tank | Ez TreatSand-Filter | Gravity | Pressure | Trenches | Not Applicable | 6000.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/01/2023 | 10:35 AM
01/04/2023 |  | RoutineScheduled | 179-11-0167-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We did not service the discharge pump because the pump line has settled inside the tank. We recommend repairing this plumbing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
11/15/2023 | Alternative | Routine/Scheduled | 15-142-0167 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 300.000000 | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | Dec 30 1899 3:05PM
10/18/2023 | Alternative | RoutineScheduled Component Maintenance | 179-07-0293-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Replaced 3 control floats while on site. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
12/07/2023 | Alternative | RoutineScheduled | 98-184-5001 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
12/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 12/28/2023 |  | 17.000000 | [5 empty] | Will be sent separately | Inspected | remove thorn bush lab sample normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
12/01/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-81937 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Clearstream |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/29/2023 | 12:00 AM
05/23/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump was replaced and the system appears to be functioning as designed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/23/2023 | Alternative |  | 033-06-0275-SR | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/04/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Routine Annual | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/04/2023 | 12:00 AM
01/25/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
06/07/2023 | Alternative | Pump-Out Only | 07-160-0158 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | 12:00 AM
04/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/18/2023 | Alternative | Follow-Up | 103-STS-96394 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | replaced failed aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/01/2023 |  | RoutineScheduled | 099-07-0105-SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend pumping the pump tank due to sludge levels in the tank. The Advantex tank will likely need pumping next year so we recommend pumping it now also. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
06/09/2023 | Alternative | Reportable Incident Component Maintenance | 099-15-0094 SR | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Complaint inspection. Low level alar due to bad timer enabler float, replaced float. added water to get water level back to normal. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
06/12/2023 | Alternative |  | 2008-143-0176 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1750 | 1000 | 750 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | Pungent | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 12:00 AM
02/13/2023 |  | RoutineScheduled | 17-113-088 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/13/2023 | 12:00 AM
09/01/2023 | Alternative | RoutineScheduled | 10-118-0034 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1500 | Clearstream |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/19/2023 | 12:00 AM
11/13/2023 | Alternative | RoutineScheduled | 107-18-0198 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
03/11/2023 |  | RoutineScheduled | 133 05 0919 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 14" of accumulated solids in septic tank. Cleaned recirculation pump basket filter. Flushed treatment unit spray manifold. Washed off treatment unit sheets. Tested floats, pump and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/12/2023 | 07:03 PM
08/22/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-12560 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic |  | Pump | Pressure | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | YES | [17 empty] | 4' Liquid depth, 0 scum, 6" of loose sludge in ST. Alarm, floats, and pump work, Field is dry. LPD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/22/2023 | 10:00 AM
01/09/2023 |  | Routine/Scheduled | 234-15-113 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | Jan 1 1900 12:30PM
05/26/2023 | Alternative | Reportable Incident Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed E189/230v effluent pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
10/24/2023 | Alternative | Reportable Incident | 099-06-0278-SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Other"] | ["Other"] | [17 empty] | Inspected | repaired broken drip tubbing. will monitor in the future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/24/2023 | 10:00 AM
01/27/2023 |  | RoutineScheduled | 099-14-0031-SR | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Ecoflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Removed trees from mound. Added Root Destroyed to pod. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
01/31/2023 |  | RoutineScheduled | SWT-05-533 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["SludgeScum Accumulation" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the Septic Tank and the Aerobic Treatment Unit due to scum & sludge accumulation in the tanks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
06/14/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1300 | Norweco Drip |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | ["None"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | 12:00 AM
03/06/2023 |  | RoutineScheduled | 182-15-0061 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/08/2023 | 12:00 AM
10/18/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | UV |  | ["Disinfection" ,"Effluent Screens"] | ["Disinfection" ,"Effluent Screens"] | YES | Musty | Clear | 7.200000 | 16.100000 | [11 empty] | Will be sent separately | Inspected | Replace UV bulb & glass housing while on site. | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 11/15/2023 | Dec 30 1899 2:02PM
02/27/2023 |  | RoutineScheduled | 03-165-0416 | Northampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1000 | Septic Tank | Ecoflo | Gravity | Pressure | Pad | Not Applicable | 450.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/27/2023 | 12:20 PM
09/11/2023 | Alternative | Routine/Scheduled | 17-142-0062 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | - Septic Tank: Water level normal. Inlet tee appears to be intact. Outlet tee appears to be intact. No riser access. Not due for pump out. - Trash Tank: Water level normal. Inlet tee appears to be intact. Due for pump out. - Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. - Aeration: Water level normal. Flushed and cleaned weir. Flushed and cleaned diffuser. Checked and confirmed high level alarm float is functioning properly. Due for pump out. - Air Pump/Blower: Checked and confirmed aerator is functioning properly. Flushed and cleaned aerator air intake filter. Aerator is 6 years old - Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. - Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact. Removed minor root infiltration Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | Dec 30 1899 10:36AM
07/06/2023 | Alternative | Routine/Scheduled | 234-17-460 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | [14 empty] | Pumped Out | Replaced aerator, diffuser and UV Bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/13/2023 | Dec 30 1899 9:30AM
07/18/2023 | Alternative | RoutineScheduled | SD-10-99 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | septic/trash | ATU | Gravity | Gravity | Discharge | Chlorination |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/02/2023 | 08:20 AM
10/09/2023 | Alternative | Routine/Scheduled | 157-11-0040 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream tank, cleaned the mesh screen in the spinfilter, and cleaned the filter in the septic tank. Changed the diffuser in the Clearstream and changed the filter in the aerator. Could not locate the valve boxes. The timer is set to 4 minutes every 1 hour. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | 08:00 AM
09/14/2023 | Alternative | Routine/Scheduled | 800-STS-14046 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream and cleaned the filter in the septic. Changed the filter in the aerator. The timer is set to 1 minute 45 seconds every 3 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/14/2023 | Dec 30 1899 10:00AM
04/19/2023 |  | Routine/Scheduled | 127-STS-34077 | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 3.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/19/2023 | Jan 1 1900 2:50PM
12/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 12/29/2023 |  | 194.000000 | [5 empty] | Will be sent separately | Inspected | fixed air supply | This AOSS should now return to normal function after having provided the above state routine maintenance | 01/15/2024 | 10:39 AM
05/16/2023 |  | RoutineScheduled | 175-11-0021 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
02/06/2023 |  | RoutineScheduled |  | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Rappahannock-Rapidan | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | blower panel not operating and needs replacement for passing inspection | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
02/20/2023 | Alternative | Routine/Scheduled | 166-05-668 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Biofilter - peatmoss in good condition - raked / turned. PUmp Basin - float sensors, pump and controls operating. DBox - plastic - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/21/2023 | 08:30 AM
07/10/2023 | Alternative | RoutineScheduled | 196-09-094 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/18/2023 | Alternative | Reportable Incident | 109-06-0799 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Acres of Virginia, Inc. |  | Melvin | Collins | 1.000000 | 500 | Multi flo |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
09/09/2023 | Alternative | Routine/Scheduled | 800-STS-13751 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | Dec 30 1899 8:15AM
05/04/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
02/07/2023 | Alternative | Routine/Scheduled | 136-12-0016 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Delta Environmental Products, UC Series |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration Tank - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced - several "wet" areas found in drip field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/09/2023 | 07:15 AM
11/21/2023 | Alternative | RoutineScheduled | 153-STS-20505 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank | Norweco ATU to Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [7 empty] | 11/21/2023 | Sample Chamber | 110.000000 | [5 empty] | Attached to this report |  | Septic Tank-3"sludge 4"scum/ ATU-0"sludge/ Pump Tank-0"sludge/ No pump out required/ Aerator functioning properly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-472 ETM-16h 33m/ High-4/ Recommend pumping out the septic tank and the ATU due to the BOD sample results. No breakout or spongy areas on the drainfield | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
10/13/2023 | Alternative | Reportable Incident | 136-03-103 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [16 empty] | Pumped Out | Pump out: - pumped out septic for peat change next week Peat Change (10/16): Replacement of Ecoflo Biofilter - includes: - Purchase & delivery of new Biofilter (specialty peat moss) - Pumping of Septic Tank - Removal of existing Biofilter using a specialty Vacuum Truck - Disposal of existing Biofilter - Installation of the new Biofilter | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/27/2023 | 03:04 PM
07/24/2023 | Alternative | Reportable Incident | 177-13-0064-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | [17 empty] | Inspected | replaced pump | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | 12:00 PM
10/16/2023 | Alternative | RoutineScheduled | 05-197-A8 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.500000 | 7.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
01/06/2023 | Alternative | Routine/Scheduled | 157-10-0230 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Trash Tank - normal level Aeration tank - normal level - mixing present - aspirator serviced. Clarifier - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 09:30 AM
08/15/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Clearstream |  | Gravity | Gravity | Trenches | UV | 200.000000 | ["Disinfection","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 12:00 AM
07/07/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20308 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NO | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
09/25/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | Dec 30 1899 10:15AM
01/26/2023 |  | Routine/Scheduled | 800-08-0233 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | Jan 1 1900 10:31AM
10/13/2023 | Alternative | Follow-Up Component Maintenance | 196-05-729 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Three Rivers | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Clearstream | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed new air pump and pressure switch | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
05/16/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/26/2023 | Alternative | Routine/Scheduled | 05-174-0150 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. Biofilter - minor ponding - peatmoss in fair condition - raked / turned. DBox - needs to be resealed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | Dec 30 1899 12:00PM
12/28/2023 | Alternative | RoutineScheduled Component Maintenance | 177-16-0392-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2024 | 07:56 AM
11/20/2023 | Alternative | RoutineScheduled | 001-STS-91774 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [8 empty] | 11/20/2023 | [9 empty] | cleaned filters, changed diffusers. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Delta Environmental Products, DF Series | Delta Environmental Products, DF Series | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Looking away from building - Aerator on left kept blowing fuses and would not run. Was not running upon arrival Aerator on right was running but it does not seem like the air was making it into the treatment unit. It was left off to not burn the motor with back pressure. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
04/26/2023 |  | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | EcoPod |  | Pump | Pressure | Drip |  | 600.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/28/2023 | 10:36 AM
05/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The header line appears to be nitrified and probed out slightly wet. Recommend uncovering distribution box and checking header line connections. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/29/2023 | Alternative | RoutineScheduled Component Maintenance | 177-12-0071-SR | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation"] | ["Level Sensor Operation" ,"Control Operation"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Annual inspection. Both sand filters had standing water up to the overflow pipes due to clogged sand. As such, the filters were not providing any treatment. Got a little bit of drainage by augering the sand. Will send another repair proposal to replace the top foot of sand. 2-20-24: Email from Dominion Septic (Brittney Perkins): "We have sent another proposal to 8005 Southwoods on January 9th and are waiting on their authorization. Option 1: Replace approximately top 12" of clogged media in both sand filters with proper sand. Need dry conditions for small loader tractor to navigate yard. Option 2: Replace approximately 24" of clogged media in both sand filters with proper sand. Need dry conditions for small loader tractor to navigate yard." - MWEBB | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 01/02/2024 | 07:39 AM
03/15/2023 |  | Routine/Scheduled | 550-STS-6850 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | EZ Treat Sandfilter |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | Jan 1 1900 9:00AM
05/02/2023 |  | Routine/Scheduled | 2008-143-0008 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex | Orenco Advantex | Pump | Pressure | Drip | Not Applicable | 750.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Modules (2) - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/03/2023 | 07:00 AM
01/30/2023 |  | RoutineScheduled | 16-183-006 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Fast |  | Gravity | Gravity | Discharge | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/30/2023 | 12:00 AM
07/11/2023 | Alternative | RoutineScheduled |  | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Whitewater |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | NA | [16 empty] | Inspected | Septic Tank Sludge- No accsess lid to check- Treatment unit No Scum layer and 6" sludge - Blower is good and alarm is good, the alarm T Barb was missing from the outlet and the owner replaced this, System alarm is now functional and treatment tank does not need pumping out. However contents of septic tank have not been checked. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/30/2023 | 09:30 AM
06/05/2023 | Alternative | RoutineScheduled | SD-13-57 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation","Attached Growth Medium"] | ["SludgeScum Accumulation","Attached Growth Medium"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 04:55 PM
11/10/2023 | Alternative | Routine/Scheduled |  | Greensville | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Pressure | Mound | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/10/2023 | Dec 30 1899 2:55PM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance | 179-12-0336-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Pump tank needs to be pumped out due to sludge levels. Field solenoid had a wire break off and system was not flushing. Replaced solenoid. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
10/19/2023 | Alternative | RoutineScheduled | 04-160-0052 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner |  |  | Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | Septic | [15 empty] | Pumped Out | - everything appears to be functional but recommend riser be installed on septic tank so full inspection can be completed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 12:00 AM
09/28/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Routine Annual and pumping, nothing to report | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/27/2023 |  | RoutineScheduled | 175-13-0487 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Control Operation" ,"Distribution Pump Operation"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Annual inspection. High level count at 92. Wet, rusty stains at midjoint, inlet end of pump tank are indicators of groundwater infiltration. Needs resealed. Return ARV for zone 3 had a steady dribble. Recommend replace with new Geoflow ARV with schrader valve. Alarm horn in control panel is burnt out, owner aware. Recommend pump out of septic tank based on time since last pumping. Recommend adding risers and lids to grade to at least one end of the septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
07/03/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-1098 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear |  | 4.000000 | [13 empty] | z | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/03/2023 | Dec 30 1899 12:50PM
03/27/2023 |  | Reportable Incident | 228-16-0323 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/27/2023 | Jan 1 1900 9:00AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/16/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | Dec 30 1899 2:21PM
01/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Blower RUNNING light (green) was shorted out, assembly replaced. Air filter replaced. Very minor root penetration observed at the access manway seal. No evidence of allowing infiltration, will continue to monitor. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
08/29/2023 | Alternative | RoutineScheduled | 047-16-224 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1250 | septic | EZ Treat | Gravity | Pressure | Discharge | UV |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.200000 |  |  |  |  | 08/29/2023 | Sample Chamber | 2.000000 |  | 1.000000 | 2.000000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/30/2023 | 08:50 AM
09/01/2023 | Alternative | RoutineScheduled | 04-183-182 | Russell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 - Blue Crystal tablets installed 14 - Bio Max tablets installed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/01/2023 | 12:00 AM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/08/2023 | Alternative | RoutineScheduled | 087-STS-6687 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1000 | EZ Treat |  | Pump | Pressure | Drip |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/21/2023 | 12:00 AM
08/01/2023 | Alternative | Routine/Scheduled |  | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. U.V. Disinfection - Bulb replaced, housing serviced. Pump Tank - float sensors replaced - pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | Dec 30 1899 8:00AM
05/31/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-47 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"SludgeScum Accumulation" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the Advantex Tank due to sludge accumulation in the tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
02/03/2023 |  | RoutineScheduled | 03-137-0200 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | All In Septic Services | 1942001442 | Dennis | Mitchell | 3.000000 | 2000 | ECO-Flow |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Auxiliary Filter","Attached Growth Medium"] | NA | Musty | Clear | [14 empty] | Inspected | Septic Sludge/Scum Accumulation - 6" Pump Station Sludge Scum Accumulation - 3" Peat Moss Level Low - Starting To Pond - Peat Rakes Out, will need replaced shorlty | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | 12:00 AM
09/28/2023 | Alternative | RoutineScheduled | SWP-04-576 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 0-6 0-8 | 0-0 | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear |  |  | 9.000000 | [11 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/28/2023 | 12:00 PM
03/07/2023 |  | Pump-Out Only | 10-142-0276 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | EcoPod |  | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/17/2023 | Jan 1 1900 9:34AM
02/27/2023 |  | Follow-Up | {FIPSCode}-STS-1293 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Control Operation","Disinfection"] | ["Control Operation","Disinfection"] | N/A | [17 empty] | Replaced UV control panel | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/27/2023 | Jan 1 1900 10:00AM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
06/19/2023 | Alternative | RoutineScheduled | VAG408472 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal | [6 empty] | Discharge | UV |  | ["None"] | [] | [19 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/19/2023 | 12:00 AM
03/10/2023 |  | RoutineScheduled |  | Shenandoah | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/13/2023 | 06:55 AM
07/31/2023 | Alternative | RoutineScheduled Component Maintenance | 047-STS-21912 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Wipes and grease accumulating in septic tank. Septic filter was clogged up, cleaned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:19 PM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/21/2023 | Alternative |  | 101-16-0452 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | John/Laina | McGurn/ Hanchak | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/07/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Recirculation Pump","Distribution Pump Operation"] | ["Attached Growth Medium","Control Operation","Recirculation Pump","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/02/2023 |  |  | {FIPSCode}-STS-31828 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Norweco | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/08/2023 | 12:00 AM
03/27/2023 |  |  | 099-17-0013 VUSA | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions | 2705163102 | Michele | Ware | 2.000000 |  | Puraflo |  | Pump |  | Pad |  |  | [] | ["Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/12/2023 | 12:00 AM
06/27/2023 | Alternative | Routine/Scheduled | 145-STS-259910 | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/27/2023 | Dec 30 1899 3:24PM
09/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | filter clog cleared | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
11/01/2023 | Alternative | RoutineScheduled | 157-11-0118 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | checked sludge, cleaned filters, system check okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/12/2023 | Alternative |  | 124-STS-2379 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Blue Ridge | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | There is a suspect area just before the drainfield. It looks like it could be an issue with the force main. Informed homeowner and gave recommendations for further investigation. Will update as more information is available. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
08/23/2023 | Alternative | Routine/Scheduled | 18-172-0019A | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Needs to be pumped | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/23/2023 | Dec 30 1899 2:59PM
04/18/2023 |  | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | rsv clog cleaned | This AOSS should now return to normal function after having provided the above state routine maintenance | 05/22/2023 | 11:15 AM
03/09/2023 |  | RoutineScheduled | SP-05-335 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Peat moss has gotten light use since its installation in 2006 and is still in decent shape. Owner has cut down and removed bushes that were next to the pods. Pump not as fast as it used to be, probably due to age. Owner will have it replaced at same time as the peat. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
06/14/2023 | Alternative | Routine/Scheduled | 234-13-110 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | Dec 30 1899 1:20PM
10/24/2023 | Alternative | Follow-Up Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced Puraflo peat in 3 modules. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | Dec 30 1899 2:02PM
10/16/2023 | Alternative |  |  | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1000 | 750 | 250 | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Disinfection","SludgeScum Accumulation"] | YES | Pungent | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | Dec 30 1899 9:30AM
03/29/2023 |  | RoutineScheduled |  | Greene | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Blue Ridge | SES Mid Atlantic, LLC | 1942001682 | Frank | Hogan |  |  | Whitewater ATU | Whitewater ATU | Gravity | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] |  | NA | Musty | Clear | [5 empty] | 03/29/2023 | Pump Chamber | 67.000000 |  |  | 19.000000 | 43.000000 |  | Will be sent separately | Inspected | 2 rothgeb - Robert Rothgeb - Mar 24, 2023 42:17 PM Recirc Pumps 2 and 3 out need replaced ordrered fro m vcama rothgeb - Robert Rothgeb - Mar 19, 2023 2:17 PM Standardized D.O. meter : 9.24 mg/l at 18.8 degrees C. Standard 9.32 mg/l. D.O. / Temperature 1121 - Dosing Tank : 12.40 mg/l at 13.2 degrees C 1123 - Polishing Tank : 12.60 mg/l at 12.9 degrees C 1125 - Anoxic Tank : 12.60 mg/l at 12.9 degrees C 1127 - ECOPOD Tank #1 : 12.74 mg/l at 12.7 degrees C 1129 - ECOPOD Tank #2 : 12.81 mg/l at 12.6 degrees C 1131 - ECOPOD Tank #3 : 12:73 mg/l at 12.7 degrees C 1133 - INF Tank : 12,88 mg/l at 12.5 degrees C 1156 - Standardized pH meter : 7.05 at 19.2 degrees C pH / Temperature Ammonia Nitrate Nitrite Alkalinity 1203 - Dosing Tank : 7.70 at 13.3 degrees C > 6 ppm 75 ppm 7.5 ppm 223 ppm 1205 - ECOPOD Tank #1 : 7.91 at 13.3 degrees C > 6 ppm 25 ppm 7.5 ppm 1208 - ECOPOD Tank #2 : 6.66 at 13.1 degrees C > 6 ppm 250 ppm > 25 ppm 1210 - ECOPOD Tank #3 : 7.83 at 13.3 degrees C > 6 ppm 75 ppm 7.5 ppm 1213 - INF Tank : 7.56 at 13.3 degrees C > 6 ppm 50 ppm 7.5 ppm Cf. rrothgeb - Robert Rothgeb - Feb 03, 2023 9:04 AM Arrived rrothgeb - Robert Rothgeb - Feb 03, 2023 9:49 AM WWTP Secure and gates locked on arrival: Yes Unusual odors around plant: No Blowers working if present: Yes, No. Both Micro Drive VFDs shorted out. Replacements have arrived. Any component in Alarm?: Yes - 2. Micro Drive VFDs. Pump Station Locked if present: Not Applicable Test telemetry system raise all floats for notice for office: Telemetry Not working. Need to replace WiFi antennae. Drive through community look for alarms and overflows: No alarms identified Community alarms or overflow detail: NA - 0 Completed Data Sheet: No Peak Flow Last 7 Days: 33719.4 gal. 1/29/23 Low Flow Last 7 Days: 16688.1 gal. 2/2/23 AVG Flow Last 7 Days: 24085.3 gal. From 1/27/23 To 2/2/23 Print workorder and place in binder: Yes Last Week of the month copy or scan data sheet to: No, not the last week of the month Makenzie Lynn - FRANK 2/2/2023 2:02:01 PM - Finstall VFDs Installed vfds for blowers 4and 5. Will have to come back to program. Belts need to be put on blowers 1 and 4. mrlynn - rrothgeb - Robert Rothgeb - Jan 06, 2023 9:34 AM Arrived rrothgeb - Robert Rothgeb - Jan 06, 2023 11:14 AM WWTP Secure and gates locked on arrival: Yes Unusual odors around plant: No Blowers working if present: Yes, No. Both Micro VFDs shorted out. AQUA VFD #3 screen blank. AQUA VFDs #1 and#2 good. Any component in Alarm?: Yes - 3 Pump Station Locked if present: Not Applicable Test telemetry system raise all floats for notice for office: Telemtry working Drive through communi | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/15/2023 | 07:20 PM
10/17/2023 | Alternative | Follow-Up Component Maintenance | 177-14-0027-SWP | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity |  | UV |  |  |  | NA | [9 empty] | 5.000000 |  | 58.100000 | 734.000000 |  |  | Will be sent separately | Inspected | Dissolved Oxygen 8.47 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/01/2023 | 07:38 AM
06/14/2023 | Alternative | RoutineScheduled Component Maintenance | SP-04-274 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
04/13/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 12:00 AM
07/25/2023 | Alternative | RoutineScheduled Component Maintenance | VAG408495 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Pad | Chlorination |  | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Please keep weeds out of ET BEd | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
01/24/2023 |  | Routine/Scheduled | 550-STS-6590 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 01/24/2023 |  | 81.000000 |  | 26.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 8:55AM
12/20/2023 | Alternative | RoutineScheduled | 182-13-0102 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/04/2024 | 12:00 AM
03/31/2023 |  | RoutineScheduled | 154-06-0686 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity |  | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | 12:00 AM
12/14/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | Dec 30 1899 11:05AM
04/10/2023 |  | RoutineScheduled | 175-04-0441 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | 12:00 AM
06/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Removed root in sample port and repaired pipe | This AOSS should now return to normal function after having provided the above state routine maintenance | 08/23/2023 | 06:57 AM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Only one spray head on the EZ treat was functioning. Flushed lines and replaced spray heads. EZ treat should return to proper function. There are roots growing in around the inlet pipe of the clarifying/EZ treat/DF pump tank. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
01/26/2023 |  | Routine/Scheduled | S 800-18-0112 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | Jan 1 1900 2:42PM
05/16/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 1.000000 |  | FAST 0.5 |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation"] | NA | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/24/2023 | 09:20 AM
01/31/2023 |  | RoutineScheduled | 175-07-0191 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Control Panels inside Residence. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 11:08 AM
07/07/2023 | Alternative | RoutineScheduled Component Maintenance | 099-STS-87323 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Sulphitic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
11/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Recirc breaker only receiving 37V from house, jumpered power from control breaker to function properly and notified homeowner of issue | This AOSS should now return to normal function after having provided the above state routine maintenance | 12/06/2023 | 03:05 PM
10/17/2023 | Alternative |  | 003-STS-32635 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Jason | Golomb | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/22/2023 | Alternative | Reportable Incident | 073-STS-105164 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | 03/16/2023 - pumpout of septic tank and pump tank - discharge pump failure - no access riser present on pump tank. 03/17/2023 - installed access riser on pump tank, installed new Liberty pump, float sensors, and 2 breaker control panel. 03/22/2023 - replaced DBox with new 8 port concrete DBox - spliced to existing conveyance line and header lines. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/23/2023 | 06:30 AM
05/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/13/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-03-172 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | Worm casings are building up on the Advantex textile media sheets. We recommend scraping the sheets & pumping the Advantex tank afterwards at next year's inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
04/03/2023 |  | Routine/Scheduled |  | James City | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Mound | UV | 450.000000 | ["Control Operation","Disinfection","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level - requires pumpout. Aeration Tank - normal level - recommend pumpout - mixing present - compressor serviced. U.V. - bulb blown, Cords melted - requires replacing. Pump Tank - recommend pumpout - float sensors, pump (reported to be tripping breaker - unable to duplicate while on property) controls operating. LPP Mound - distal end has surfacing present. - Cypress Point - EVERY onsite system in subdivision is failing in some manner! | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/04/2023 | Jan 1 1900 7:00AM
10/16/2023 | Alternative | Routine/Scheduled | 166-07-128 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level Has no solids with 4" of sludge Pulled and cleaned filter Filter is aged and no longer manufactured -Discharge/Pump Tank: At normal level Pump and floats were replaced last year and are working properly -Peat Moss: Tipping bucket working properly Raked out peat, still in good shape -Control Panel Alarm box: Box is located in the crawl space Box is working properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 09:00 AM
09/21/2023 | Alternative | RoutineScheduled Component Maintenance | 107-19-0061 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 09/21/2023 |  | 3.000000 | [5 empty] | Will be sent separately | Inspected | Lab Sample Normal Replaced vent cap | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
02/17/2023 |  | RoutineScheduled | {FIPSCode}-STS-67316 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["SludgeScum Accumulation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA |  | Discolored | [13 empty] | Will be sent separately | Inspected | There is evidence that paint has been washed into the system. We recommend pumping all tanks to prevent paint from accumulating in the drip dispersal system. We have attempted several repairs on the zoner valve. We now recommend installing a new valve as the current one is not working properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
03/02/2023 | Alternative | Routine/Scheduled | 157-97-103 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. There is visible wetness on the drainfield - most likely from rain - once it dries need to keep an eye on it. The timer is set to 6 minutes every 1 hour. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/02/2023 | 01:30 PM
04/25/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Delta Environmental Products, DF Series | Delta Environmental Products, DF Series | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
05/04/2023 | Alternative | Routine/Scheduled | 136-18-0196 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service - Real Estate Inspection. Trash Tank - normal level Aeration Tank - normal level - mixing present - aspirator serviced. Clarifier - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | 07:15 AM
04/07/2023 | Alternative | Routine/Scheduled | 06-131-4118 | Floyd | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series | Delta Environmental Products, DF Series | Pump | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/07/2023 | 08:15 AM
03/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping Pump chamber. There is a fair amount of scum visible. Small roots were seen around the riser but does not appear to be an issue. Recommend monitoring and resealing if necessary. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/22/2023 |  | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed N98 effluent pump & 2" Brass check valve. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/31/2023 | Jan 1 1900 12:26PM
06/29/2023 | Alternative | RoutineScheduled | 2015-143-0119 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/16/2023 | Alternative | Reportable Incident | 2005-143-0048 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Customer stated alarm was going off this morning Arrived and found panel in alarm state Opened system and found pump tank in above normal level Found the filter in the Septic was covered in debris and feminine products. Pulled and cleaned filter Tested pump and floats and found floats to be functioning properly But the pump was pulling high amperage and not moving any water. Removed bad pump and installed new pump under warranty. Tested and confirmed all components are functioning properly upon departure. System was no longer in alarm but was stilling high level. Need to be conservative with water usage for 24hrs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/17/2023 | 02:40 PM
07/13/2023 | Alternative | RoutineScheduled Component Maintenance | 179-12-0267-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Clearstream | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Effluent Screens" ,"Auxiliary Filter" ,"Distribution Pump Operation" ,"Dispersal System Operation" ,"BlowerCompressorAerator Operation"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | Owner had reported an alarm the day before. Upon arrival, water level was normal. All floats, pumps & controls were working properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
06/24/2023 | Alternative | RoutineScheduled | 2110-06-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 6.900000 |  |  | 2.100000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/03/2023 | 12:00 AM
11/16/2023 | Alternative | Routine/Scheduled | 15-142-0059 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | UV | 250.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | ["Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | [17 empty] | The seals in the Polylok distribution box need to be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | Dec 30 1899 2:57PM
09/25/2023 | Alternative | RoutineScheduled | SD-14-60 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Routine Annual | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | 12:00 AM
09/26/2023 | Alternative | RoutineScheduled | 109-18-0101 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith |  | 1500 | Orenco Advantex AX20RT |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 14" of accumulated solids in septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. 2" of solids in recirculation portion of treatment unit. 6" of solids in discharge portion of treatment unit. Removed roots from the treatment unit that had gotten under the lid. Tested floats, pumps and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 07:03 PM
09/01/2023 | Alternative | Reportable Incident Component Maintenance | 175-14-0065 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced ATU compressor. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
03/07/2023 | Alternative | Reportable Incident | 159-02-314 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | COSS - Maintenance - GMP2018-02 Replaced distribution box with new. Spliced to existing conveyance line. Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/08/2023 | 10:00 AM
06/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Lines were not receiving equal dose. Distribution box was uncovered and dial flows adjusted | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/05/2023 | Alternative | RoutineScheduled | 07-184-5011 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","SludgeScum Accumulation","Septic Tank Baffles"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/05/2023 | 12:00 AM
08/21/2023 | Alternative | Routine/Scheduled | 17-142-0227 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1500 | EZ Treat Sandfilter |  | Pump | Pressure | Drip | Not Applicable | 150.000000 | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | NO | [17 empty] | Dripfield pressure was found at 20 psi. Dripfield was flushed and pressure was reset to 20 psi. The effluent filters were checked and did not need cleaning. Discharge pump counters: PC = 162, PRT = 17h 1m, HL = 0, LL = 0, Power Fault = 1, TFE = 21, Time Since Reset = 4531h 53m. Counters were reset | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | Dec 30 1899 10:35AM
02/23/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
01/23/2023 |  | Initial Visit | 177-STS-92157 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Bottom float (redundant off) in drip tank was stuck on, replaced it. Recirc tank: high level = 1, low level = 14. Discharge tank: high level = 14 (does not alarm for low level). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
06/15/2023 | Alternative | Routine/Scheduled | 085-STS-33887 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/15/2023 | Dec 30 1899 2:18PM
09/12/2023 | Alternative | RoutineScheduled Component Maintenance | 175-02-0079 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
11/15/2023 | Alternative | Routine/Scheduled | 09-160-0221 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 161.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/15/2023 | 12:45 AM
11/08/2023 | Alternative | RoutineScheduled Component Maintenance | 033-15-0073-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
03/23/2023 |  | Reportable Incident | 228-06-0898 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  |  |  | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [17 empty] | Replace pump, UV controls panels, 4 signal floats | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/23/2023 | Jan 1 1900 1:00PM
01/26/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-67358 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - filter broken - requires replacement. PUmp Tank - float sensors, pump and controls operating. BioFilter - 4 modules - peatmoss spent -requires replacement. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | 08:30 AM
06/14/2023 | Alternative |  | 132-10-0055 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Kaitlyn | Harlow-Burner | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/01/2023 |  |  | 08-142-0113 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex | [6 empty] | ["Attached Growth Medium","Distribution Pump Operation","Control Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Recirculation Pump","Distribution Pump Operation"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 12:00 AM
02/01/2023 |  | RoutineScheduled | 153-STS-20267 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | Septic-8"sludge 0"scum/ .75 Microfast ATU-3"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working properly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-2040 ETM-543h 20m/ High level-10/ Watermeter-0,288,417.1 On-10m Off-4h 34m/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/03/2023 |  | RoutineScheduled | 191-STS-36019 | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 Chlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/03/2023 | 12:00 AM
03/02/2023 |  | RoutineScheduled | 175-04-0724 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Drainfield - Two areas where sewage coming to surface | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/31/2023 | 12:26 PM
09/26/2023 | Alternative | Initial Visit | 147-16-0125 | James City | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Peninsula | Hutchens Septic Services LLC | 1942001509 | Robert | Hutchens, Jr. | 2.000000 | 1450 | Clearstream |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear | [14 empty] | Pumped Out | Effluent surfacing at drain field site. System was pumped out and placed on pump and haul until repairs are made. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/26/2023 | 12:00 AM
06/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Zone return valve opens intermittently while dosing, but does not appear to be an issue. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/31/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Fairfax | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | ATU | Polishing Sand Filter | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.200000 |  |  | 1.900000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/02/2023 | 12:00 AM
09/05/2023 | Alternative | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 2.000000 | [8 empty] | ["Other"] | [] | NA | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | 12:00 AM
03/24/2023 |  | RoutineScheduled |  | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Blue Ridge | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
03/30/2023 |  | Initial Visit | 165-STS-338582 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20RT | [6 empty] | [] | [] | [18 empty] | Start Up. Corrected float wiring. Elbow on discharge is cracked and leaking and needing to be replaced. Screws in lid needed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 12:00 AM
06/14/2023 | Alternative | Initial Visit | 199-STS-5009 | York | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the pressure switch assembly (left un-plugged due to the pumping of tanks - need to go back and hook up once there is enough water in tanks) and replaced the alarm light bulb. Repaired the airline and repaired the forcemain. Meet with the pumping company and pumped out the Clearstream tank and pumped out the septic tank. The timer is set to 4 minutes every 1 hour. Did not take sample due to the airline being broken on arrival. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/14/2023 | Dec 30 1899 11:00AM
05/11/2023 | Alternative | Initial Visit | 113-STS-21988 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Best 1 |  |  |  | Trenches |  |  | ["Septic Tank Baffles","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/11/2023 | 12:00 AM
01/09/2023 |  | Routine/Scheduled | 193-STS-101996 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Puraflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES |  |  |  |  | 0.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 06:29 PM
04/19/2023 | Alternative | Reportable Incident | 193-STS-102259 | Westmoreland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 300.000000 | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | AOSS - Repair - VDH Permit 196-23-0049 04/17/2023 - tanks pumped for storage and repair. 04/19/2023 - Installed new 1000g concrete top seam tank as pump tank - installed new timer enabled control panel, float sensors. Refilled tanks for re-start. Flushed drip field with fresh water - reset pressure - reset timers. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/20/2023 | 06:30 AM
07/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Blower panel bypassed need to install a new one outside on post once homeowner has post installed and electric | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 08/23/2023 | 06:57 AM
12/04/2023 | Alternative | RoutineScheduled | 065-STS-32355 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Carrington Pump & Irrigation | 1942001121 | John | Carrington |  |  | Norweco |  | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens"] | ["Level Sensor Operation","Distribution Pump Operation","Control Operation","Dispersal System Operation","BlowerCompressorAerator Operation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
04/28/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/17/2023 |  | RoutineScheduled | 179-06-0126-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Media showing its age but treatment looks clear. Recommend evaluating peat moss next year. Boxwood bushes to close to puraflow pods and makes it very hard to open lids. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
07/05/2023 | Alternative | RoutineScheduled Component Maintenance | 113-STS-25897 | Madison | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Recirculation Pump"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/17/2023 | 12:46 PM
07/10/2023 | Alternative | Follow-Up | 193-STS-102238 | Westmoreland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | adjusted recirc timer | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/17/2023 | Alternative | RoutineScheduled | 109-10-0176 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 16" of accumulated solids in septic tank. Flushed treatment unit spray manifold. Cleaned recirculation pump solids basket filter. Tested floats, pump and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | 07:03 PM
10/06/2023 | Alternative | Reportable Incident | 136-03-654 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm Call: -Clearstream system. Alarm was going off on the air pump house. The air pumps diaphragms were broken and no longer working. Reid approved to replace the air pump and defuser. I also checked and cleaned his septic tank filter. Replaced air pump and defuser. Everything now working properly | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/20/2023 | 09:49 AM
03/14/2023 |  | Routine/Scheduled | 085-STS-31496 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Treatment Module - recirc - recirc pump, media drapes & spray grid serviced. Treatment Module - discharge - float sensors, pump and controls operating. Pumps to community absorption field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | Jan 1 1900 9:30AM
04/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/15/2023 | Alternative | RoutineScheduled | 159-11-155 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
05/24/2023 | Alternative | Routine/Scheduled | 136-08-0303 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Pad | Not Applicable | 300.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank = normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Biofilter - 3 Modules - peatmoss in excellent condition - raked / turned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 11:15 AM
05/22/2023 |  | RoutineScheduled | 175-05-0776 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | NA | [17 empty] | Septic Tank-4"sludge 2"scum/ Microfast-8"sludge/ Pump Tank-2"sludge/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ Redundant off float is faulty and requires replacement, replaced during inspection/ Controls, pump, floats and alarms now functioning properly/ Counts: Pump-36369 ETM-28206/ Watermeter-178,672.8/ No breakout or spongy areas on the drip field and dosing correctly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Lower line appears to show signs of nitrification outside of the trench area. There are no signs of wet or soggy areas though. Recommend rebalancing D-Box and checking header connection to ensure that effluent isn't bleeding down to lower line. Camera headers if necessary. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
02/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
10/26/2023 | Alternative | RoutineScheduled Component Maintenance | SWT-99-64 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Dispersal System Operation" ,"Auxiliary Filter"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
09/25/2023 | Alternative | RoutineScheduled Component Maintenance | 179-13-0077-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
10/04/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 10/04/2023 | Sample Chamber | 7.000000 | [5 empty] | Attached to this report |  | Septic Tank-4"sludge 0"scum/ Microfast-0"sludge 0"scum/ Pump Tank-0"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-160 ETM-6h 10m/ Pump2-165 ETM-6h 5m On-2m 15s Off-6h/ Peak-7/ High-5/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
06/13/2023 |  | Pump-Out Only | 2018-143-0111 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001750 | Matt | Keeley | 1.000000 | 1060 | Orenco Advantex |  | Pump | Gravity | Pad | UV |  | SludgeScum Accumulation | SludgeScum Accumulation | YES | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/16/2023 | 01:43 PM
09/01/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
02/28/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
07/25/2023 | Alternative |  | 03-183-001 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/25/2023 |  | 3.970000 |  |  | 2.900000 |  |  | Will be sent separately |  | BOD: 3.97 TSS: 2.90 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/25/2023 | 12:00 AM
09/27/2023 | Alternative | Routine/Scheduled | 151-06-0122 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank 1: Normal level 5 in of sludge 1 in of solids No signs of infiltration -Septic Tank 2: Normal level 3 in of sludge less than 1 in of solids Pulled and cleaned filter Roots running through riser -Discharge/Pump Tank: Normal level 12 in of suspended solids Pulled and cleaned pump Pulled and tested floats all functioning properly Plumbing intact Junction box intact Pump properly moving water and working as should No signs of infiltration -Aeration: Normal level Less than 1 in for suspended solids Floats functioning properly Pulled and cleaned diffuser Pulled and cleaned weir Air line intact functioning properly Tank is set backwards No signs of infiltration -Air Pump/Blower: 120 volts coming in Pulled and cleaned filter Air pressure sensor intact and working properly -Control Panel: 120 volts coming in All visual and audible alarms functioning properly Air pump pulled 1.7 amps Discharge pump pulled 8.8 amps -Distribution Box: Used camera and located to find d box Dbox is 3"7in deep in ground Customer didn't want to dig up at this time -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | 03:55 PM
06/21/2023 | Alternative | RoutineScheduled | 175-03-1025 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank | Delta DF-60 to Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-8"sludge 0"scum/ DF ATU-4"sludge 4"scum ( Recommend Pump Out) Pump Tank-3"sludge 0"scum/ Blower air filter cleaned and working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-2479 ETM-2756/ High-12 / Watermeter-0,883,360/ No breakout or spongy areas on the drip field and dosing correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/27/2023 |  | RoutineScheduled | 099-11-0040-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
12/21/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | Dec 30 1899 1:25PM
11/20/2023 | Alternative | Routine/Scheduled | 151-04-048 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1000 | Ecoflo |  | Gravity | Gravity | Pad |  |  | ["Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 20.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | 06:47 PM
12/08/2023 | Alternative | Follow-Up | 98-197-A2 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | [29 empty] | Tablets stuck | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
07/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 3.000000 |  | Biomicrobics MicroFAST | Whitewater ATU | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
11/02/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [14 empty] | Replaced aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | Dec 30 1899 3:30PM
03/15/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic/atu and pump tank need pumped out. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
07/21/2023 | Alternative | Routine/Scheduled | 147-04-0154 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Pump | Pressure | Trenches | Not Applicable | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine service - STE LPP absorption field. Primary septic tank - normal level Pump Tank - float sensors, pump and controls operating. LPP Field - exercised valving - no indications of surfacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | Dec 30 1899 9:30AM
12/13/2023 | Alternative | RoutineScheduled Component Maintenance | 154-04-0267 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Recirculation Pump"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | As noted previously, there are small trees growing in the dispersal area. We recommend that this area be mowed and maintained in a mowed condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
09/13/2023 | Alternative |  | 07-197-A11 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 15 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/13/2023 | 12:00 AM
10/06/2023 | Alternative | Routine/Scheduled | 06-120-0652A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Bionest |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/06/2023 | Dec 30 1899 3:21PM
05/01/2023 | Alternative | RoutineScheduled | 136-08-0251 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1200 | Ecoflo |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | 12:00 AM
08/08/2023 | Alternative | RoutineScheduled | 18-100-0170 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 500 | AQUASAFE |  | Pump |  |  |  | 300.000000 | [] | [] | YES | [16 empty] | Pumped Out | PUMPED SEPTIC EVERYTHING WORKING AS IT SHOULD BLOWER REBUILD KIT RECENTLY INSTALLED | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/11/2023 | 11:40 AM
05/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
05/20/2023 | Alternative | Routine/Scheduled | 095-STS-6887 | Williamsburg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/20/2023 | Dec 30 1899 12:30PM
02/25/2023 |  | Reportable Incident | 234-16-307 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/25/2023 | Jan 1 1900 4:00PM
07/10/2023 | Alternative | Routine/Scheduled | 234-08 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | Dec 30 1899 10:20AM
09/26/2023 | Alternative | Pump-Out Only | 18-160-0105 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Brittany | Conner | 2.000000 |  | Aquasafe | [6 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/02/2023 | 12:00 AM
11/30/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-18002 | Bland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Septic Tank Baffles"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/30/2023 | 12:00 AM
06/29/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [8 empty] | 06/08/2023 | Sample Tap | 3.000000 |  |  | 7.790000 | 83.100000 |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | Dec 30 1899 8:55AM
03/28/2023 |  | RoutineScheduled | 154-06-0444 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norwco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 12:00 AM
11/17/2023 | Alternative | RoutineScheduled | 195-STS-27191 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 2 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/17/2023 | 12:00 AM
07/07/2023 | Alternative | RoutineScheduled Component Maintenance | 179-11-0025-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Level Sensor Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for presale inspection. Distribution box has root infiltration not allowing equal flow to all drainfiled trenches. Proposal to be sent to correct this. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
10/17/2023 | Alternative |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:00 AM
01/11/2023 |  | Follow-Up | 177-12-0170-SR | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to disassemble components in recirc tank and assist pumper with proper pump out. Reassembled components and refilled recirc tank with water truck. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
05/08/2023 |  | RoutineScheduled | 179-12-0075-SWP | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We continue to observe wet areas along the bottom of the drip dispersal field. We recommend replacing the check valves and the psi gauge. We also continue to recommend extending the downspouts on the tank side of the house beyond the dispersal area. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/01/2023 | 06:29 AM
08/18/2023 | Alternative | RoutineScheduled Component Maintenance | SP-04-270 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Control Operation" ,"Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Removed some roots from all 5 pods, next year we will need to add root destroyer to all 5 pods and sample box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
01/04/2023 | Alternative | Reportable Incident | 103-STS-103395 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | COSS - Repair - VDH Permit 151-22-0155 Pumped empty, and removed existing septic tank. Installed new 1000 gallon septic tank with effluent screen and riser. Replaced existing distribution box with new. Spliced to existing conveyance line and header lines. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/05/2023 | 06:45 AM
04/04/2023 |  | RoutineScheduled | 177-STS-89610 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Repaired broken pipe in manifold. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
03/29/2023 |  | RoutineScheduled | 10-192-121 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Discharge | UV | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Level Sensor Operation","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation","Disinfection"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/29/2023 | 12:00 AM
01/16/2023 |  | RoutineScheduled | 179-12-0099-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | There are roots growing into the Puraflo modules. At some point in the future, it may become difficult to stir the peat. Additionally, some settling of the peat is occurring. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
10/16/2023 | Alternative |  | 107-15-0015 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | reset air relief valve box | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
02/07/2023 |  | Pump-Out Only | 147-19-0041 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | System pumped out as recommended during previous service event. All compartments pumped empty and serviced. Tank refilled with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/09/2023 | Jan 1 1900 7:30AM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Ecoflo | none | Gravity | Gravity |  | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
05/05/2023 | Alternative | Routine/Scheduled | 157-02-016 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | Effluent Screens | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service - Primary septic tank - nor riser access present - effluent screen serviced! Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | 08:30 AM
03/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | When we arrived the alarm was going off. The pump tank was in high water. The mechanical float was not engaging the timer. The float had to be shaken several times to get the ball inside it to move. When we tested the alarm float it would turn alarm on but would not shut it off. We replaced both floats and tested to insure they were working as they should. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/09/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Aqua Klear |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | NA | Musty | [15 empty] | Inspected | Sludge level- Septic tank 1" scum and 8" slduge- 20-30" slduge amount of sludge in treatment, Good aeration, Discharge tank 4" sludge- cleaned airfilter. Good aeration. Cleaned Effluent filter. System is operational pump run time 75hr 56 min and 921 cycles, water meter reading 216,910, Flushed filter and drip while running pump in test. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
08/08/2023 | Alternative | Routine/Scheduled |  | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Crater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Supervised pumpout of trash tank Aeration tank - mixing present - aspirator serviced. Clarifier - normal level Pump Tank - float sensors, pump and controls operating. Drip Field - headworks serviced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | Dec 30 1899 9:00AM
06/27/2023 | Alternative | Initial Visit | 124-STS-2379 | Franklin City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 9.000000 |  | 4.000000 | [5 empty] | Owner had called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The timer was set at 5 minutes every 2 hours changed it to 8 minutes every 2 hours. Took initial BOD and Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/27/2023 | 02:00 PM
08/17/2023 | Alternative | RoutineScheduled | 11-125-041 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 9 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/17/2023 | 12:00 AM
07/18/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20464 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
05/05/2023 | Alternative | RoutineScheduled | SD-06-336 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | 2 |  | Pump | Gravity | Trenches | Not Applicable | 65.630000 | ["SludgeScum Accumulation","Dispersal System Operation","Effluent Screens"] | ["Effluent Screens","Dispersal System Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/09/2023 | 09:50 AM
04/29/2023 |  | RoutineScheduled | 133 07 0459 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 10" of accumulated solids in septic tank. 12" of solids in discharge pump tank. Flushed treatment unit spray manifold. Cleaned recirculation pump basket filter. Sprayed solids off of treatment sheets. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 07:03 PM
09/25/2023 | Alternative | Follow-Up Component Maintenance | SP-04-552 | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced old AX-20 sheets with new upgrade sheet kit. Installed lid struts. Assisted pumper with pump out of both tanks. Refilled with clean water to operating level. Checked discharge pump rate and set controls to proper dose. Dug up distribution box and inspected box, headers and drainlines. Installed temporary wire for discharge and replaced timer float in discharge. Proposal to be sent to reseal inlet & outlet risers. Reseal pump tank outlet riser. Re-plumb discharge piping for easy access and install blocks under pump. Install new wire and conduit for recirc and discharge. Reset pod with proper fall. Correct badly sagging sewer line. Install proper float tree in discharge. Repair crushes in headers. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/02/2023 | 05:18 AM
02/25/2023 |  | RoutineScheduled | {FIPSCode}-STS-4720 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 3 Chlorine 5 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/25/2023 | 12:00 AM
11/13/2023 | Alternative | Routine/Scheduled | 175-04-0278 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | Dec 30 1899 2:23PM
10/10/2023 | Alternative | Reportable Incident | 157-04-308 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [16 empty] | Pumped Out | Pump out 10/10: -Pumped 1200 gallons from septic tank. 2.5 hoses from truck. System at normal level. Pump out for service experts to perform peat change Repair 10/10: -Installation of 2 floats -Install new Filter Peat Change 10/13: * Arrived for Peat change * Removed peat moss and roots * Replaced new bio filter Everything working as it should | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/20/2023 | 01:43 PM
01/05/2023 |  | Routine/Scheduled | 228-13-0051 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/05/2023 | Jan 1 1900 9:20AM
11/07/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.300000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | 02:30 PM
12/12/2023 | Alternative | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Level Sensor Operation","Distribution Pump Operation"] | ["Distribution Pump Operation","Level Sensor Operation"] | NO | [17 empty] | Service call only: Replaced 2 Zoeller E-140 pumps (230 volts) , 2" check valves and replaced the alarm float. No other services provided. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
09/01/2023 | Alternative | Routine/Scheduled | 228-11-0244 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | EZ Treat Sandfilter |  | Pump |  | Drip | UV |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | Replaced discharge pump and pump in dose tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/01/2023 | Dec 30 1899 10:30AM
11/28/2023 | Alternative | Routine/Scheduled | 196-05-576 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Puraflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 06:25 PM
01/21/2023 |  | RoutineScheduled | 133 07 0823 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | BioMicrobics Microfast |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 6" of solids in septic tank. 20" of solids in treatment unit. 6" of solids in discharge pump tank. Cleaned drip field spin filter. Adequate aeration. Tested floats, pump and alarms. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/16/2023 | 07:03 PM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Lower line might be receiving slightly more effluent than the other lines. Recommend uncovering Distribution Box and re-leveling if necessary | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/10/2023 | Alternative | RoutineScheduled | 061-STS-21686 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation" ,"Level Sensor Operation"] | ["Distribution Pump Operation" ,"Control Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection and maintenance completed. Reset all "R" counts in Advantex panel to zero. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 09:31 AM
05/23/2023 |  | RoutineScheduled | 175-06-0281 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
11/09/2023 | Alternative | RoutineScheduled | 166-15-094 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters, system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/14/2023 | Alternative | Reportable Incident | S-175-13-0090 | Southampton | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Dispersal System Operation","Distribution Pump Operation"] | ["Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Cleaned Weir filter | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/14/2023 | Dec 30 1899 10:00AM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/22/2023 | Alternative | Follow-Up | 085-STS-33529 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 650 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/22/2023 | Dec 30 1899 11:00AM
02/24/2023 |  | RoutineScheduled | 153-STS-20145 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | YES | [17 empty] | Septic Tank-4"sludge 2"scum/ EZ-Treat Recirc. Tank-4"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Recirc pump intake cleaned/ Counts-0381997 ETM-0090283 On-2.5m Off-12.5m/ Discharge Zoeller N-98 pump counts-212 ETM-30h 48m/ High-8 On-6m 24s Off-12h Controls, pumps, floats and alarms functioning properly/ Recommend EZ-Treat 750 Lid be replaced/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/25/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Customer stated alarm has been going off since Monday. Arrived on site and found panel in alarm condition Opened system and found processing tank above normal level Checked voltages and amperage and found no amps or volts on neither pump Called homeowner and gained access to breaker through garage door opener Found septic pump breaker was tripped, reset breaker Tested both pumps and recirc pump pulled 10.82amps and discharge pulled 10.15amps. Combined with both pump running they pulled 37.47amps and tripped breaker after 1 to 2 minutes Both pumps are controlled by one main power feed. Determined that the breaker tripping to be the cause of processing tank being in high level. Pulled and cleaned all components Got system out of alarm Tested and confirmed system is functioning properly at time of departure Spoke with homeowner and let her know that I recommend an electrician to get another feed So that each pump has its own feed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | Dec 30 1899 4:24PM
10/11/2023 | Alternative | RoutineScheduled | 182-04-0070 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | 12:00 AM
11/03/2023 | Alternative | RoutineScheduled Component Maintenance | 177-10-0230-ST | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
04/24/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | Dec 30 1899 12:48PM
05/08/2023 |  | RoutineScheduled | 175-04-0413 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
07/28/2023 | Alternative | Routine/Scheduled | 151-12-0159 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1500 | Clearstream ATU |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 75.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/28/2023 | 05:32 PM
10/12/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | Dec 30 1899 12:20PM
01/09/2023 | Alternative | Routine/Scheduled | NYII-BD5K76 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | Dec 30 1899 3:10PM
08/29/2023 | Alternative | RoutineScheduled Component Maintenance | 061-STS-24805 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
03/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20447 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | 11:24 AM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/15/2023 | Alternative | Routine/Scheduled | 05-160-0373 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable | 62.000000 | None | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/15/2023 | 01:30 PM
10/24/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","Distribution Pump Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","Distribution Pump Operation","SludgeScum Accumulation"] | NA | [17 empty] | New homeowner called with alarm condition. 10-21-2023 onsite to diagnose alarm condition. The PVC union for the discharge pump was broken. Back onsite 10-24-2023 to repair broken union and perform annual inspection. 14" of accumulated solids in septic tank with a 3" solids crust. 22" of solids in treatment unit. 14" of solids in discharge pump tank. Scheduled pump out of septic tank, treatment unit and discharge pump tank next week. Cleaned blower air filter. Cleaned drip manifold cartridge filter. Adequate aeration. Very good treatment quality. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/25/2023 | 07:03 PM
11/16/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"SludgeScum Accumulation"] | ["Auxiliary Filter"] | NA | Septic | Clear | [13 empty] | Will be sent separately | Inspected | Tank needs pumping. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/01/2023 | Dec 30 1899 10:33AM
11/16/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | UV |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 12/06/2023 | Dec 30 1899 9:34AM
04/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/02/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/15/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Water was turned on. Serviced the Singulair Treatment unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/04/2023 |  | Initial Visit |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip |  |  | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | 12:00 AM
10/23/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/23/2023 | Dec 30 1899 1:10PM
12/11/2023 | Alternative | Routine/Scheduled | 2009-143-0012 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Trash Tank Condition of above Component Notes for above Component Water level normal. Outlet baffle appears to be intact. Not due for pump out. Discharge/Pump Tank Condition of above Component Notes for above Component Water level high upon arrival. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Not due for pump out. Aeration Condition of above Component Notes for above Component Water level normal. Flushed and cleaned effluent filter assembly. Not due for pump out. Air Pump/Blower Condition of above Component Notes for above Component Checked and confirmed aerator is functioning properly. Flushed and cleaned aerator. Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly Drip Field Condition of above Component Notes for above Component Flushed and cleaned disk filter. Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 12:48 PM
05/12/2023 |  |  | 2011-143-0078 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Norweco | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out | Replaced bad on/off float switch | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 12:00 AM
02/02/2023 | Alternative | RoutineScheduled | SD-13-125 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Distribution Pump Operation"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | As noted on previous inspections, we recommend pumping the Pump Tank due to sludge accumulation in the tank. It may be advantageous to pump the Advantex Tank at the same time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
03/16/2023 |  | Reportable Incident | SWP-98-140 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | High level alarm caused by the filter flush valves not closing properly, and dirty disc filters slowing down the drip rate. After cleaning those parts, the drip rate went from being too slow to too fast due to both zone check valves being stuck open. Replaced both check valves, then retested rates and cleaned the zone return valve twice. Drip and flush rates are very good considering the system is over 20 years old and does not have pretreatment. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
05/17/2023 |  | RoutineScheduled | 107-10-0114 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 851.000000 | [] | [] |  |  |  | 7.520000 | 6.440000 | 22.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/15/2023 | 05:20 PM
02/27/2023 |  | RoutineScheduled |  | Frederick | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 1.000000 | 749 |  |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/05/2023 | 12:00 PM
01/06/2023 |  | Routine/Scheduled | 234-13-206 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/06/2023 | Jan 1 1900 1:10PM
03/29/2023 |  | RoutineScheduled |  | Page | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 03/29/2023 |  | 16.000000 | [5 empty] | Will be sent separately | Inspected | blower panel visual bad and silence don't work | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/28/2023 | 02:17 PM
06/30/2023 | Alternative | Pump-Out Only | 03-160-0552 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | [9 empty] | [] | [] | [17 empty] | Pumped Out | - tank is cracked in multiple spots, still holding water at this time - outlet line is kicked up, no issues at this time | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/30/2023 | Alternative | Reportable Incident | 124-STS-2379 | Dinwiddie | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the aerator not running. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. Replaced the buzzer. The septic tank needs additional risers on it to be properly inspected in the future. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/30/2023 | Dec 30 1899 2:00PM
07/03/2023 | Alternative | RoutineScheduled Component Maintenance | SD-12-336 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. When the pump was first installed 9 years ago, it was plenty strong and had to be throttled to allow for a slightly longer run time to achieve the designed small dose. Now, the pump is down to barely 18 gpm with the the gate valve wide open. Recommend replace pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
10/17/2023 | Alternative | Routine/Scheduled | 05-120-0142AR | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/17/2023 | Dec 30 1899 5:37PM
09/07/2023 | Alternative | Routine/Scheduled | 550-STS-6634 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | Dec 30 1899 10:45AM
02/02/2023 | Alternative | RoutineScheduled | 151-09-0062 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Pad | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/07/2023 | 12:00 AM
09/11/2023 | Alternative | Routine/Scheduled | 2016-143-0169 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 150.000000 | ["Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | ["Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | [17 empty] | Nitrogen return was adjusted. The Recirculation pump had 12 overrides in the past 30 days. A garbage disposal should not be used with this septic system. The audible alarm needs to be replaced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/11/2023 | 02:58 PM
10/05/2023 | Alternative | Routine/Scheduled | 2019-143-0005 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 400 | Fuji |  | Pump | Pressure | Drip | UV |  | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Fuji maintenance procedure performed. Both zones of Drip field flushed. Filter flushed. 330 overrides. System appears to be operating normally. Due for pumpout in the next few weeks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 10:15 AM
03/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | UV |  | ["Other","Dispersal System Operation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [17 empty] | Told homeowner that all her air release valves are broken and that she has effluent on the ground. Also it looks like its been broken for a while it has eroded the soil where you can see the manifold pipe. Not sure if pipes are broken under the ground. Drain field is across the road | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/15/2023 | Dec 30 1899 4:20PM
01/11/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Cloudy | 7.750000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2023 | 12:15 AM
02/06/2023 |  | RoutineScheduled |  | Warren | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | required pump filter clog cleaned | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/18/2023 | 04:10 AM
07/19/2023 | Alternative | Reportable Incident | 107-05-0376 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Dispersal System Operation","Effluent Screens","Other"] | ["Auxiliary Filter","Dispersal System Operation","Effluent Screens","Other"] | YES | Musty | Clear | [15 empty] | leak repaired in dripfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/19/2023 | 12:00 AM
04/06/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
02/02/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1250 | Septic | pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/17/2023 |  | Reportable Incident | 175-17-0409 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["Distribution Pump Operation","Disinfection","Other"] | ["Other","Distribution Pump Operation"] | NA | [17 empty] | Service call only: High level alarm- Found faulty Orenco turbine pump, ground water infiltrating the inlet riser, sewer cleanout broken and faulty Orenco UV-Light. Replaced the pump, repaired the cleanout and sealed the riser. The UV-Light has been ordered and will be repaired at a later date. Pump cycles-8198/ Pump run time-1215h 20m/ High counts-21 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/19/2023 | Alternative | RoutineScheduled | 08-100-0948 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | BIOCOIR |  | Pump | Gravity | Mound | Not Applicable | 1000.000000 | [] | [] | [17 empty] | Pumped Out | CLEANED SPRAY NOZZLES TO UNCLOG. FIBER IN TANK IS 12". PUMPED. EVERYTHING WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | 10:25 AM
05/02/2023 |  | RoutineScheduled |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 0-0 0-00-0 |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear | [14 empty] | Inspected | new home looks good | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | 12:00 AM
10/21/2023 | Alternative | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Loudoun | Loudoun Environmental Treatment | 1942001460 | Raymond | Kirkpatrick | 1.000000 | 2000 | AX20 | AX20 |  |  | Discharge | Chlorination |  | [] | [] | NA | Musty | Cloudy | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/21/2023 | 09:00 AM
12/21/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | Dec 30 1899 9:10AM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Two lateral ends are broken. Homeowner has scheduled repair | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/15/2023 | 06:51 AM
05/30/2023 | Alternative | RoutineScheduled Component Maintenance | 177-19-0100-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The psi gauge for the drip dispersal system is not working and should be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
05/22/2023 | Alternative | Pump-Out Only | 234-15-010 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [8 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/22/2023 | Dec 30 1899 11:20AM
12/27/2023 | Alternative | RoutineScheduled Component Maintenance | {FIPSCode}-STS-78520 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Effluent Screens" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping all three compartments of the Norweco tank due to scum and sludge accumulation in the tank. Soil has eroded over the drainfield header lines. We recommend adding topsoil and reseeding in the spring. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2024 | 07:56 AM
04/05/2023 |  | Routine/Scheduled |  | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - plastic - at grade - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/06/2023 | 08:15 AM
12/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 12/28/2023 |  | 14.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
11/10/2023 | Alternative | Routine/Scheduled | 166-11-149 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Found at normal level, 3in of sludge and less than 1in of solids. Pulled and cleaned filter -Discharge/Pump Tank: Found at normal level, less than 1in of sludge and solids. Teste floats and pump. All working as they should. -Peat Moss: Raked out peat in all modules. Peat looks good. -Control Panel: 120 volts to panel. 240 volts to pump. Audio and visual alarms working as they should. Wrote down counts on card. Pump pulled 4.9 amps -Drain Field: Inspection port is dry. No signs of surfacing in drainfield area | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 03:04 PM
11/13/2023 | Alternative | RoutineScheduled | 015-STS-335202 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
05/13/2023 | Alternative | Reportable Incident | 157-16-0027 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Control Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Alarm - found power breaker for control panel tripped in residence. All tanks in high level - pumped for storage and relief. Found Aquaworx control panel not functioning - approved for replacement. 05/17/2023 - replaced failed control panel with new Orenco MVP DM Controls | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/30/2023 | 01:45 PM
10/11/2023 | Alternative | Routine/Scheduled | 04-120-0342A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact and. Flushed and cleaned effluent screen. Effluent screen assembly is broken. Not due for pump out. Effluent screen is obsolete and discontinued. Riser is not properly sealed to septic tank and has signs of groundwater infiltration. -Discharge/Pump Tank: Water level normal. Structural integrity of tank appears to be intact. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. -Peat Moss: Raked and tilled peat moss. Peat moss is in good condition. Structural integrity of biofilter tank appears to be intact. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact. -Drain Field: Found no signs of surfacing on dispersal field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | Dec 30 1899 3:59PM
03/22/2023 | Alternative |  | 203-12-0177 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | [34 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/04/2023 | Alternative | Routine/Scheduled | 147-17-0079 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Multiflo FTB |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank normal level - riser damaged from lawn care operations. Aeration Tank - normal level - mixing present - submersible aerator serviced. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | Dec 30 1899 7:09AM
09/28/2023 | Alternative | Pump-Out Only |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 2.000000 | [8 empty] | [] | [] | YES | [17 empty] | Pumped Both Tank Pump and Septic Tanks Pump in Pump Tank Not Working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/29/2023 | 12:00 AM
07/25/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/01/2023 | 12:00 AM
10/03/2023 | Alternative | RoutineScheduled | 182-03-0360 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None |  | 8.210000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | 12:15 PM
11/28/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-15876 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Recirculating Sand Filter |  | Pump | Pressure | Discharge | Chlorination | 500.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | Musty | Clear | 6.900000 |  |  | 1.700000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/01/2023 | 12:00 AM
07/21/2023 | Alternative | Reportable Incident Component Maintenance | 179-18-0386-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | On site to address discharge high level alarm that owner said started 4 days ago. Recirc tank also in high level, but the high level float was not working. Measured 0 amps for recirc pump. Recirc tank would have been overflowing except that effluent was running up and over into the top of the RSV pipe and running into the pump tank. Repaired rotten/broken neutral connection in splice box at tank (no water in box) and restored recirc pump operation. Discharge tank in high level due to low drip rate. Cleaned dirty disc filter, cleaned pump intake, and cleaned small debris from field flush valve to restore the drip rate. Will return next week for annual inspection, maintenance, and fix non functioning high level float in recirc tank. Advantex vent cap is broken and will be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 07:01 AM
10/19/2023 | Alternative | RoutineScheduled | 019-STS-27296 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Effluent filter installed or maintained | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Drip |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | Repaired sprayed head pump line which had broken off at the union. Will attempt a warranty claim on broken fittings. System now functioning normally | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/21/2023 | 09:30 AM
05/25/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 12:00 AM
05/17/2023 |  | Routine/Scheduled | 234-14-308 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | Jan 1 1900 11:25AM
02/09/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
03/15/2023 | Alternative | RoutineScheduled | 159-02-406 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | [] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance | 113-STS-25897 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
05/25/2023 | Alternative | Initial Visit | 095-STS-5670 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Visit Primary septic tank - normal level Aeration tank - normal level - mixing present - compressor serviced Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | Dec 30 1899 1:45PM
06/05/2023 | Alternative | RoutineScheduled | 133 08 0035 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Western Virginia Water Authority | 1942001145 | Michael | Doss | [9 empty] | ["None"] | ["None"] | YES | None | Clear | [5 empty] | 06/05/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | 01:55 PM
12/01/2023 | Alternative | RoutineScheduled | DISCHARGE | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 4 Dechlorine | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/01/2023 | 12:00 AM
07/24/2023 | Alternative | RoutineScheduled |  | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/18/2023 | 12:00 AM
08/15/2023 | Alternative | Reportable Incident | 05-190-123 | Surry | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Control Operation","Level Sensor Operation"] | ["Control Operation","Level Sensor Operation"] | N/A | [17 empty] | Replaced float | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/15/2023 | Dec 30 1899 3:00PM
07/03/2023 | Alternative | Routine/Scheduled | 151-03-430 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 2500 | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level Flow Equalization Tank - float sensors pump and controls operating. Processing Tank - rSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. Drip Field - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | 12:30 PM
08/09/2023 | Alternative | RoutineScheduled | 015-STS-334203 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Auxiliary Filter"] | ["Effluent Screens","Auxiliary Filter"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
07/10/2023 | Alternative | RoutineScheduled Component Maintenance | 179-18-0284-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Effluent Screens"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
11/06/2023 | Alternative | RoutineScheduled |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 1750 | 750 | 250 | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Pungent | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | Dec 30 1899 5:00PM
06/15/2023 | Alternative | RoutineScheduled | 001-STS-92400 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn |  |  | FUJI CLEAN |  | Pump | Pressure | Mound | UV | 300.000000 | [] | [] | [18 empty] | EVERYTHING WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/16/2023 | 09:25 AM
09/18/2023 | Alternative | RoutineScheduled Component Maintenance | SD-08-147 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Control Operation" ,"Auxiliary Filter"] | ["Recirculation Pump" ,"Control Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Completed annual inspection and maintenance for new owner. She stated that the septic/ recirc tank was pumped out last August at time of home sale. Advantex vent was almost closed off with moss. Removed vent cap and cleaned out the moss. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
08/29/2023 | Alternative | Reportable Incident |  | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Purasys |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | N/A | [17 empty] | Replaced failed aerator - assisted by Anua Technician | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/06/2023 | 07:30 AM
05/02/2023 |  | RoutineScheduled | 175-11-0323 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 05/17/2023 | Sample Chamber | 22.000000 | [5 empty] | Attached to this report |  | Septic Tank-4"sludge 0"scum/ Microfast-0"sludge/ Pump Tank-0"sludge/ No pump out needed at this time/ Blower air line broken and repaired during inspection/ Blower air filter cleaned and now working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-238 ETM-17h 43m/ High-4/ No breakout or spongy areas on the drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/09/2023 |  | Routine/Scheduled | 550-STS-6399 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | Jan 1 1900 10:00AM
09/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
07/17/2023 | Alternative | RoutineScheduled | 17-152-009 | Lee | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | CLEARSTREAM |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 12:00 AM
12/14/2023 | Alternative | Reportable Incident | 166-05-789 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Clearstream. System was flooded because someone turned the power off. Turned it back on and everything seems to be working. Customer approved to pump the system down and a SA to re evaluate everything. Used 1st alarm call for today SA 12/15: Septic Tank Condition of above Component Notes for above Component Pumped tank while onsite Discharge/Pump Tank Condition of above Component Notes for above Component Pumped tank while onsite Tested pump and floats Floats are not functioning properly Air Pump/Blower Condition of above Component Notes for above Component Tested and confirmed everything is functioning properly Control Panel Condition of above Component Notes for above Component Control panel has failed Drain Field Condition of above Component Notes for above Component No signs of surfacing and or blow outs PO 12/15: -Pumping of system -Quoted for 2000 gallons -Meeting SE on site | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 10:02 AM
01/30/2023 |  | Routine/Scheduled | 04-118-0084 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | Jan 1 1900 8:00AM
05/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
11/07/2023 | Alternative | Reportable Incident Component Maintenance | 177-11-0039-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["SludgeScum Accumulation" ,"Control Operation" ,"Distribution Pump Operation"] | ["Control Operation" ,"Distribution Pump Operation"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Owner called about both control panels alarming. It appears that a running toilet caused both alarms. Cleaned RSV in recirc tank and ensured that effluent was being transferred over to the discharge tank. Suctioned out a couple of inches of water from the recirc tank splice box. Ran a complete cycle for each drip zone, headworks and pump working normally. Discharge tank needs pumped out due to excessive sludge accumulation, owner to make arrangements with local pumper. Effluent is a bit on the cloudy side, probably due to residual chemo drugs entering the septic. Recirc tank may need to be pumped next spring. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
07/24/2023 | Alternative | RoutineScheduled | 033-17-0026-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Elite Onsite | 1942001726 | Drew | Saunders | 3.000000 | 2000 | 1000 | 1000 | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | 05:50 PM
10/25/2023 | Alternative | RoutineScheduled Component Maintenance | 061-19-084 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Audible portion at atu panel alarm no longer works. Will probably need to replace entire panel as manufacturer does not make those parts available. If so, recommend adding more boards to the 6x6 post and then re-mounting the new panel so that it faces the church. As it is now, the red alarm light faces the field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
10/31/2023 | Alternative | RoutineScheduled | 175-15-0419 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic/ Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [8 empty] | 10/31/2023 | Sample Chamber | 45.000000 | [5 empty] | Attached to this report |  | Septic Tank-2"sludge 0"scum/ Microfast ATU Tank-0"sludge but the Media is clogged and requires chemical cleaning and pump out. Took samples for BOD out of the inlet of the Septic Tank (Result-55 mg/L) and out of the outlet sample box (Results-45mg/L) Hexane Extractable Material results less than 5.00 mg/L Blower air filter cleaned and blower working correctly/ No breakout or spongy areas on the drainfield and dosing correctly/ Alarm on the Microfast control unit working properly. Returned on 11/01/2023 and did a chemical cleaning and pump out of the Media. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/26/2023 | Alternative | RoutineScheduled | 159-07-0088 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 12:00 AM
01/06/2023 |  | Routine/Scheduled | 093-06-0294 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/06/2023 | Jan 1 1900 10:31AM
01/12/2023 |  | Routine/Scheduled | 128-03-129 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the filter in the septic tank. Changed the diffuser in the Clearstream and changed the filter in the aerator. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/12/2023 | 08:30 AM
05/15/2023 | Alternative | Routine/Scheduled | 166-11-005 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Advanced Septic |  | Pump | Pressure | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 0.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | 05:56 PM
08/25/2023 | Alternative | RoutineScheduled | 150-03-130 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/23/2023 | Alternative |  | ST-03-177 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
05/16/2023 | Alternative | Pump-Out Only | 18-160-0110 | Montgomery | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [18 empty] | - Rodney Rice is maintenance provider, Rodney Requested pretreatment be serviced as he is completing maintenance on system. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/18/2023 | 12:00 AM
08/25/2023 | Alternative | RoutineScheduled Component Maintenance | 179-12-0210-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
11/22/2023 | Alternative | Follow-Up Component Maintenance | SP-01-593 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Chemically cleaned FAST unit, both tanks pumped out by others. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
05/02/2023 |  | RoutineScheduled | 107-06-0478 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to pumped. The blower filter was cleaned. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/06/2023 | 10:15 PM
09/12/2023 | Alternative | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | [18 empty] | Alarm on 8/22/2023 found pump #1 (Zoeller 191) was not working and requires replacement/ Water meter reading 1913243. System will function with 1 pump temporally but recommend replacement of both pumps with turbine pumps. Replaced both pumps on 9/12/2023 with turbine 230 volt pumps with cool guides. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
12/07/2023 | Alternative | Routine/Scheduled | 228-04-1027 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/07/2023 | Dec 30 1899 1:10PM
01/03/2023 |  | Routine/Scheduled | 550-STS-5885 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2023 | Jan 1 1900 10:05AM
11/13/2023 | Alternative | Routine/Scheduled |  | Surry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal level 6 in of sludge less than 1 in of solids Pulled and cleaned filter No signs of infiltration -Discharge/Pump Tank: Normal level Less than 1 in of suspended solids Tested floats and pump all working as should All plumbing intact and pump moving water properly No signs of infiltration -Aeration: Normal level 13 in of suspended solids Air line intact and properly dispersing air No signs of infiltration re-evaluate sludge levels next yea -Air Pump/Blower: 120 volts coming in Air pump pulled 1.53 amps Air pressure sensor working as should -Control Panel: 120 volts coming in All visual and audible alarms functioning properly -Distribution Box Surge box to distribution: Normal level 7 lines in Dbox all intact and taking water properly Speed balancers intact and functional Surge box is normal level Removed some small grass roots on site however intact and working as should -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | Dec 30 1899 10:22AM
10/20/2023 | Alternative | RoutineScheduled | 107-04-0340 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | ["Auxiliary Filter","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:00 AM
11/01/2023 | Alternative | RoutineScheduled | 136-17-0340 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | checked sludge, replaced uv bulb and alarm components, system check okay | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
07/17/2023 | Alternative | Routine/Scheduled | 234-13-417 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | Dec 30 1899 12:25PM
12/28/2023 | Alternative | Routine/Scheduled | 2013-143-0116 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Septic Tank Condition of above Component Notes for above Component Water level normal. Inlet tee appears to be intact. Flushed and cleaned effluent screen. Not due for pump out Recirculation Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Checked and confirmed UV system is functioning properly. Flushed and cleaned UV system Discharge/Pump Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Flushed and cleaned vortex filter. Media Sheets Condition of above Component Notes for above Component Cleaned media sheets. Checked and confirmed spray pattern is good Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Drip Field Condition of above Component Notes for above Component Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2024 | 09:26 AM
12/14/2023 | Alternative | Reportable Incident Component Maintenance | 175-01-0073 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation"] | ["Control Operation" ,"Distribution Pump Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | High level alarm. Inside pump breaker was tripping although pump was actually pulling low amps. Verified power supply and connections, then discussed with Zoeller tech rep. Replaced E191 pump per his recommendation, problem solved. New pump running at 11.3 amps (247V supply). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
08/07/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesapeake | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.000000 | 5.600000 | [13 empty] | Routine Service Processing Tank - normal level - RSV, recirc pump, Effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | Dec 30 1899 7:00AM
02/15/2023 | Alternative | Reportable Incident | 073-STS-103640 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | COSS - Maintenance - GMP2018-02 Primary septic tank pumped empty and serviced. Installed access risers to grade. Installed new 4" PVC conveyance line. Replaced DBox with new 8 port concrete DBox - Installed new PVC header lines. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/16/2023 | 06:45 AM
10/09/2023 | Alternative | Routine/Scheduled | 175-STS-14483 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | Dec 30 1899 2:56PM
06/20/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was replaced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/18/2023 | Alternative | RoutineScheduled | 133-STS-101233 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance | 047-16-158 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity |  | UV |  | ["Disinfection" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["Disinfection" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy |  | 9.410000 |  |  |  | 06/08/2023 | Sample Chamber | 2.000000 |  | 1.000000 | 5.500000 |  |  | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
07/15/2023 | Alternative | RoutineScheduled | 109-16-0007 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 4.000000 | 8500 | EZ Treat |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Septic tank #1 - 6" of accumulated solids. Septic tank #2 - 10" of accumulated solids. Recirculation Tank - 10" of accumulated solids. Discharge Pump Tank - 0"of accumulated solids. Cleaned septic tank filter. Cleaned EZ Treat spray nozzles | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | 07:03 PM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Rejected | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity |  | Chlorination |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | There was not discharge to collect samples. Discharge point does not have discharge sign. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 06/20/2023 | Dec 30 1899 12:57PM
04/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. AR valve has been damaged by lawn equipment. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 12:48 PM
10/23/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Routine Annual, nothing to report | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/23/2023 | 12:00 AM
09/21/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Puraflo |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","Control Operation","Dispersal System Operation"] | ["Auxiliary Filter","Control Operation","Dispersal System Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/05/2023 | 01:35 PM
11/25/2023 | Alternative | Routine/Scheduled | 08-160-0052 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable | 255.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/25/2023 | 11:15 AM
10/23/2023 | Alternative | Routine/Scheduled | 151-11-0125 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Found at normal level, 3in of sludge and less than 1in of solids. Pulled and cleaned filter. Current filter style has been discontinued. -Discharge/Pump Tank: Found at normal level. Tested floats and pump. All working as they should. -Peat Moss: Tipping bucket and trays are in working order. Raked out peat on both sides. Some compacting but peat still good. -Control Panel: 120 volts, audio and visual alarms working as they should. Pump pulled 5.9 amps -Distribution Box: Found at normal level, no roots or cracks. All lines taking water -Drain Field: No signs of surfacing in drainfield area | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 02:31 PM
01/03/2023 | Alternative | Routine/Scheduled | 151-08-0318 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1250 | Ecoflo |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 0.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2023 | 07:05 PM
03/15/2023 |  | Routine/Scheduled | 087-STS-6220 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1060 | Purasys |  | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation"] | N/A | [17 empty] | System checked. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | 01:48 PM
05/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend bringing risers slightly above grade | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/16/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-91873 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [5 empty] | 08/16/2023 |  | 6.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Hard grease starting to build up in septic tank, left copy of do's and don'ts. RECIRC: HL-3, LL-26, OVERRIDE-144. DISCHARGE: HL-1,0VERRIDE-0. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
12/07/2023 | Alternative | Routine/Scheduled | R16-180-0037 | Roanoke City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | EZ Treat Sandfilter |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | Musty | Clear | 6.700000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/07/2023 | Dec 30 1899 10:15AM
03/29/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Needs new airblower | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
08/02/2023 | Alternative |  | 195-STS-27344 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 08/02/2023 |  | 7.630000 |  |  | 11.400000 |  |  | Will be sent separately |  | BOD: 7.63 TSS: 11.4 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | 12:00 AM
08/07/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-531 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
05/02/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/26/2023 | Alternative | Reportable Incident Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced N140 effluent pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
06/05/2023 | Alternative | RoutineScheduled | C-11-111-0103 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | [18 empty] | The system did not need to be pumped. The blower and spin filters were both cleaned. The controls were operating as designed. There were no visible leaks in the drip field. There was return effluent returning to the pump tank so the drip field was operating as designed. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/06/2023 | Jan 1 1900 11:40PM
10/06/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1200 |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [16 empty] | Pumped Out | Replaced 2 Relay valves | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/11/2023 | Dec 30 1899 3:50PM
11/10/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Septic Pumping Riser Installation Sealed 6" pipes and tar Seals parged Sealed 2" pipe and tar Sealed entire top of microfast unit | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | 12:00 AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Strongly recommend moving the new tree that is in between the lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/07/2023 |  | RoutineScheduled | 087-STS-6127 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Norweco Singulair |  | Pump | Pressure | Drip |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Cloudy | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/07/2023 | 12:00 AM
03/23/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Advantex | Pump | Pressure | Drip | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [17 empty] | 2" Scum, 12" sludge , some sludge in recirc tank, little in pump tank recommend pumping and cleaning all tanks with in the year filters cleaned . pumps alarms working. field looks good | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/24/2023 | 03:00 PM
09/21/2023 | Alternative | RoutineScheduled Component Maintenance | 182-02-0344 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Recommend adding riser on inlet | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
04/25/2023 |  | RoutineScheduled |  | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 1.000000 | 1500 | MircoFast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | 01:45 PM
12/28/2023 | Alternative |  | VAG400175 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/28/2023 |  | 6.540000 | [5 empty] | Will be sent separately |  | BOD: 6.54 TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 12:00 AM
11/08/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty |  | 7.010000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | 02:30 PM
12/07/2023 | Alternative | RoutineScheduled Component Maintenance | 175-16-0341 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/18/2023 | 08:36 AM
08/18/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-02-746 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
08/08/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | Dec 30 1899 3:58AM
01/23/2023 |  | Follow-Up | 179-09-0062-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [7 empty] | 01/23/2032 |  | 73.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
09/05/2023 | Alternative | Routine/Scheduled | 234-13-297 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | Dec 30 1899 10:30AM
04/12/2023 |  | RoutineScheduled | 12-142-0026 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 2.000000 | 2500 | EZ Treat |  | Pump | Pressure | Drip |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 12:00 AM
01/30/2023 |  | Routine/Scheduled | 550-STS-6523 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | Jan 1 1900 1:35PM
07/06/2023 | Alternative | RoutineScheduled | 19-142-0015 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
03/23/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | damp spot on drainfield rec camera and pOSSIBLE repair | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | House is not occupied at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance | 137-STS-25061 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | 90-Day Inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
05/19/2023 |  | Reportable Incident | 175-16-0436 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | High level alarm for both tanks. Discharge tank got into high level first, which then locked out the recirc pump and eventually caused a high level alarm in the recirc tank. Control panel would call for a drip cycle, but no power was making it to the bottom terminal strip (last place before leaving the panel). Cycled control panel off for a minute and then back on. Power was restored to the solenoids. Suspect problem was from a stuck relay in one of the circuit boards. Tech Support for the control panel (Orenco in Washington state) was not available yet. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
02/07/2023 |  | Routine/Scheduled | 15-174-0221 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Aqua Klear | None | Pump | Gravity | Trenches | Not Applicable | 600.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Trash Tank & Aeration tank pumped empty and serviced as recommended during last service event. Aeration tank refilled with fresh water for restart. 5 year lab sampling obtained for BOD5 & TSS and transported to Envirocompliance laboratories. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/09/2023 | Jan 1 1900 7:00AM
04/05/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 04/05/2023 |  | 83.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
06/16/2023 | Alternative | Reportable Incident | 234-03-10843 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/16/2023 | Dec 30 1899 11:30AM
11/09/2023 | Alternative | RoutineScheduled | 182-03-0209 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/09/2023 | 12:00 AM
03/03/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower connection was repaired. System appears to be functioning as designed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
08/23/2023 | Alternative | RoutineScheduled | 179-06-0175-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 3.000000 | 1500 | 0-4 0-3 | 0-0 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | None | Clear |  |  | 6.000000 | [11 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/23/2023 | 03:00 PM
04/06/2023 | Alternative | RoutineScheduled | 109-STS-31127 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
08/31/2023 | Alternative | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["BlowerCompressorAerator Operation","Other"] | ["BlowerCompressorAerator Operation","Other"] | [18 empty] | System in alarm, Repairs needed: Filter and AX-100 nozzles need to be cleaned. Replace one nozzle/ Replace the blower. Returned on 9/21/2023and all above stated repairs were done. Blower was a AXVFA-Fan for the AX-100 Advantex unit. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
01/06/2023 |  | RoutineScheduled | 09-100-0597 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 |  | CLEARSTREAM |  | Pump | Pressure | Mound | Not Applicable |  | [] | [] | [17 empty] | Pumped Out | INSTALLED A NEW DRIP DISPOSAL PUMP-PUMPED 200 GALLONS OF SEWAGE-RECONNECTED ALARM. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/21/2023 | 10:00 AM
02/20/2023 |  | RoutineScheduled | 132-03-0191 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Drip | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/25/2023 | 12:00 AM
08/14/2023 | Alternative | RoutineScheduled | 07-113-079 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 4 - Blue Crystal tablets installed 14 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/14/2023 | 12:00 AM
02/22/2023 | Alternative | RoutineScheduled | 009-STS-24097 | Amherst | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 600 | Advantex AX20RT |  | Pump | Pressure | Drip | UV |  | ["Effluent Screens"] | [] | NA | [16 empty] | Inspected | Replaced Bulb- new Orenco UV light and serviced system - Found 2 leaks in drip drainfield piping which owner repaired. Effleunt filter is stuck and appears jammed in its location to bottom of tank.. It may need replacement or some modifictation work out the jammed filter. Currently the filter flows freely, tank has little sludge and has no sign of clog or back up. The filter should be addressed. Sign of mud in septic tank from installation. Septic tank has 1 inch scum layer on top and 12-16" newish sludge/soil on bottom, Recirc zone has 6-8 inches and discharge has 4 to 5 inches. Recirc time 494 Recirc cycles 36,246, Discharge time 75 min and 18300 cycles. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/24/2023 | 09:30 AM
08/24/2023 | Alternative | Routine/Scheduled | 10-163-0025 | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Aquaworx Remediator |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/24/2023 | Dec 30 1899 8:43AM
10/19/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 12:00 AM
08/17/2023 | Alternative |  | 2001-143-0376 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1750 | 1000 | 750 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","SludgeScum Accumulation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Pungent | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/17/2023 | 12:00 AM
05/04/2023 | Alternative | Initial Visit | -STS-43590 | Roanoke | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Pura-Flo Peat |  | Gravity | Gravity | Trenches |  |  | ["Control Operation"] | ["Control Operation"] | NA | [17 empty] | Annual inspection. First inspection by this operator. Control panel is not functional. Pump will not run in "hand" or automatic. Control panel repaired on 1-11-2024. Raked peat in the three pods. Peat is about 40% spent. 10" of accumulated solids in septic tank. 6" of solids in discharge pump tank. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/18/2024 | 12:00 AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Inspection was performed. System components need to be updated. Will re-file once components are updated. System appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
04/24/2023 |  | RoutineScheduled | 02-113-116 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Septic Tank Baffles","Disinfection","BlowerCompressorAerator Operation","SludgeScum Accumulation","Dispersal System Operation","Control Operation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/24/2023 | 12:00 AM
03/23/2023 | Alternative | Pump-Out Only | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | McKim Septic & Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | [] | NA | [16 empty] | Pumped Out | septic and atu tank pumped out microfast | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/28/2023 | Dec 30 1899 3:30PM
12/11/2023 | Alternative | Routine/Scheduled | 119-STS-106482 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [16 empty] | NEEDS NEW TRI CHECK PUMP | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/11/2023 | 09:30 AM
07/26/2023 | Alternative |  | 04-197-A15 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/26/2023 |  | 2.320000 |  |  | 1.600000 |  |  | Will be sent separately |  | BOD: 2.32 TSS: 1.60 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
10/13/2023 | Alternative | Initial Visit Component Maintenance | 177-STS-92704 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
10/16/2023 | Alternative | RoutineScheduled | 128-08-0041 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 0 | Anthony | Santucci-Curci | 1.000000 | 1250 |  |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/09/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1875 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/12/2023 | Alternative | RoutineScheduled | C-12-111-0031 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Delta whitewater |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Routine yearly inspection visit. Blower motor runnning and in good aerastion in treatment tank, Adjusted air line to stop a leak. Dog house cover good. Septic tank trace scum and 14" sludge. Treatment tank no scum and light trace sludge, pump tank has trace sludge. 23,559 cycles and 455hrs 44min, HLA 0 , Low level 18, overide 8 , timer events 30040, power fail 363, time in service 90262 hours 32 min. Audible light working but buzzer doesnt sound, maybe bad and replacingment needed, 3 psi on drainfield when pump runs and no leaks opbserved. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | Jan 1 1900 9:30AM
04/03/2023 |  | Routine/Scheduled |  | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Trenches | UV | 600.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash Tank - normal level Aeration tank - mixing present - compressor serviced. U.V. disinfection - bulb and housing serviced. Pump Tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | 09:45 AM
09/01/2023 | Alternative | Routine/Scheduled | 228-14-0447 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/01/2023 | Dec 30 1899 8:45AM
06/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Effluent Screens" ,"Auxiliary Filter" ,"Disinfection"] | ["Effluent Screens" ,"Auxiliary Filter" ,"Disinfection"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
03/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank and pump tank full. Pump appears to be functioning on hand but not under control of the panel. Homeowner is scheduled for pumping and repair | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
03/24/2023 |  | RoutineScheduled | 179-07-0291-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
05/02/2023 |  |  | 02-197-091 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 05/02/2023 |  | 2.260000 |  |  | 1.900000 |  |  | Will be sent separately |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | 12:00 AM
11/14/2023 | Alternative | RoutineScheduled | 06-160-0034 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2500 | MICROFAST |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | Septic | Cloudy | [15 empty] | - EVERYTHING IS FUNCTIONAL, BUT WIRE CONNECTIONS ARE INSIDE TANK - RECOMMEND INSTALLING JUNCTION BOX AND POST OUTSIDE OF TANK AND REWIRING - RECOMMEND INSTALLING NEW PUMP AND ALARM FLOAT - RECOMMEND BLOWER FILTER BE REPLACED | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/17/2023 | 12:00 AM
02/16/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1875 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/05/2023 | Alternative |  | ST-04-507 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
12/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 12/12/2023 |  | 79.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
05/02/2023 |  | Reportable Incident | 193-STS-94787 | Westmoreland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | High water alarm due to clogged filter. Cleaned filter. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
07/14/2023 | Alternative |  | 033-17-0215-VU | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
05/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | UV |  | ["Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | UV assembly was not in holster corrected do not drive around rear of house | This AOSS should now return to normal function after having provided the above state routine maintenance | 07/06/2023 | 08:40 AM
01/19/2023 | Alternative | RoutineScheduled | 154-15-0090 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity |  | UV |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Disinfection" ,"Distribution Pump Operation"] | ["Attached Growth Medium" ,"Disinfection" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy |  | 10.790000 |  |  |  | 01/19/2023 | Sample Chamber | 2.000000 |  | 1.000000 | 5.400000 |  |  | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
07/19/2023 | Alternative | RoutineScheduled | 151-07-0017 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/30/2023 |  | RoutineScheduled | 175-99-0361 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/24/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Dabney & Crooks, Inc. | 1941001489 | Robert | Fessler |  |  | Puraflo |  | Pump | Gravity | Pad | Not Applicable | 500.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [5 empty] | 11/13/2023 | [10 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/02/2023 | 12:00 AM
10/07/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20 |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 6" of accumulated solids in septic tank. Flushed treatment unit spray manifold. Cleaned recirculation pump solids basket filter. 0" of solids in discharge pump tank. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 07:03 PM
03/13/2023 |  | RoutineScheduled |  | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Rappahannock-Rapidan | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
06/02/2023 |  | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/13/2023 | 12:57 PM
07/05/2023 | Alternative | RoutineScheduled | 2009-143-0057 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Hoot |  | Pump | Pressure | Drip |  |  | [] | ["Effluent Screens","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/05/2023 | 12:00 AM
02/16/2023 |  | RoutineScheduled | 179-14-0001-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We would recommend scraping the Advantex sheets to remove solids build up and pumping the Advantex tank after scraping. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
06/23/2023 | Alternative | Reportable Incident | 19-172-0128A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Alarm Event - found multiple high level alarms following rain events. Septic tank riser leaking badly and needs to be resealed. Effluent screen serviced. Recirc pump, discharge pump, media drapes serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/26/2023 | Dec 30 1899 12:45PM
07/04/2023 | Alternative | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 | 1000 |  |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | 12:00 AM
05/18/2023 |  | Routine/Scheduled | 550-STS-6727 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/18/2023 | Jan 1 1900 3:15PM
08/23/2023 | Alternative | Routine/Scheduled | 085-STS-33652 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | UV | 450.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Processing Tank - recirc - pump, spray grid, media drapes serviced. U.V. disinfection - bulb and housing serviced. Processing Tank - discharge - pump, float sensors, controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | Dec 30 1899 9:30AM
04/20/2023 |  | RoutineScheduled | 107-14-0182 | Augusta | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter"] | NA | [7 empty] | 04/20/2023 |  | 64.000000 | [5 empty] | Will be sent separately | Inspected | bad blower panel needs replaced and primary tank requires pumping for passing inspection owes | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/21/2023 | 03:35 PM
05/16/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection"] | ["Disinfection" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
12/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/30/2024 | 01:28 PM
03/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
07/19/2023 | Alternative | Routine/Scheduled | 151-15-0088 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. BioFilter - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | 07:00 AM
08/14/2023 | Alternative | RoutineScheduled | 075-STS-33156 | Goochland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2500 | Microfast |  | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["Effluent Screens","Dispersal System Operation"] | YES | Musty | Clear | [14 empty] | Inspected | Effluent seepage in drip field - not consistent or even Drip system flushed - large amount of mud/dirt flushed from lines - system hasn't been flushed since installed (2 plus years). Advised follow up if field doesn't change after flushing | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/14/2023 | Dec 30 1899 2:00PM
06/24/2023 | Alternative | RoutineScheduled | 2070-01-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination | 500.000000 | ["Disinfection","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | ["Disinfection","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | Musty | Clear | 6.500000 |  |  | 2.200000 |  | 07/03/2023 | Sample Chamber | 3.000000 |  |  | 13.400000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/12/2023 | 12:00 AM
06/01/2023 | Alternative | RoutineScheduled | 06-142-0569 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/21/2023 |  | Routine/Scheduled | 2017-143-0122 | Henrico | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Henrico | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Meet with the pumping company and pumped out and cleaned the Clearstream tank and pump tank and pumped out the septic tank. Disconnected the pressure switch due to the pumping. The motor on the pump runs - no H20 - could not tell if it is pumping. The UV is not working. Replaced the alarm light bulb and installed 11 silicone wire nuts. Need to go back to perform a draw down test, hook up pressure switch, and flag off the drainfield. The timer is set to 5 minutes every 1 hour. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 02/21/2023 | 10:30 AM
09/26/2023 | Alternative | RoutineScheduled |  | Page | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","SludgeScum Accumulation","Control Operation"] | ["Auxiliary Filter","SludgeScum Accumulation","Control Operation"] | [17 empty] | Pumped Out | Pumped out all tanks. Spin filter replaced and alarm repaired | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/21/2023 | 12:00 AM
06/30/2023 | Alternative | Initial Visit | C102-08-0057 | Alleghany | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | Septic Tank Only | AdvantexAX20 | Pump | Pressure | Drip |  |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The effluent filter was pulled and cleaned. The RSV valve was pulled and cleaned. The recirculating and discharge pumps were both pulled and cleaned. The textile sheets were sprayed off. The controls were operating as designed. There were no visible leaks in the drip field. There was return effluent returning to the pump tank so the drip field was operating as designed. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | Jan 1 1900 9:05PM
08/31/2023 | Alternative | Routine/Scheduled | 15-137-0035 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1250 | None |  | Pump | Pressure | Trenches | Not Applicable |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | Flushed LPD, CLeaned Effluent Filter. System Appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/11/2023 | Dec 30 1899 9:27AM
08/08/2023 | Alternative | RoutineScheduled | 02-197-091 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/08/2023 | 12:00 AM
10/20/2023 | Alternative | Routine/Scheduled | 800-02-0569 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | Dec 30 1899 9:35AM
02/08/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/17/2023 | Jan 1 1900 10:44AM
11/29/2023 | Alternative | Initial Visit | 061-STS-26875 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 1.000000 | 1500 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["Dispersal System Operation","Control Operation","Distribution Pump Operation","SludgeScum Accumulation"] | ["Control Operation","Distribution Pump Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Septic | Clear | [5 empty] | 11/29/2023 | Pump Chamber | 11.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2024 | 12:00 PM
08/14/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | 11:15 AM
03/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Clearstream | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
01/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
09/13/2023 | Alternative | RoutineScheduled Component Maintenance | 175-12-0276 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
12/07/2023 | Alternative | RoutineScheduled Component Maintenance | 179-16-0186-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith |  |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/17/2023 | 09:07 AM
05/02/2023 |  | Routine/Scheduled | {FIPSCode}-STS-3480 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | Jan 1 1900 7:45AM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance | 2133-10-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Whitewater ATU | none | Pump | Gravity |  | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection"] | ["BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 09/15/2023 | 02:41 PM
01/17/2023 |  | Initial Visit | 09-160-0158 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 | 1000 | Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | Septic | Cloudy | [14 empty] | Inspected | - blower needs to be replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12:00 AM
01/26/2023 |  | RoutineScheduled |  | Page | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | alarm unplugged filter clogged | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
11/15/2023 | Alternative | RoutineScheduled | 165-STS-333569 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | E-Z Treat |  |  | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","Septic Tank Baffles","SludgeScum Accumulation","Recirculation Pump"] | ["Attached Growth Medium","Auxiliary Filter","Septic Tank Baffles","SludgeScum Accumulation","Recirculation Pump"] | [17 empty] | Pumped Out | Pumped out and pump replaced | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/30/2023 | 12:00 AM
10/02/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:00 AM
06/15/2023 | Alternative | RoutineScheduled Component Maintenance | 175-18-0488 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity |  | UV |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/07/2023 | 06:25 AM
11/22/2023 | Alternative | Reportable Incident Component Maintenance | 179-09-0104-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Complaint inspection. System was on high level due to a running toilet and clogged spin filter. customer fixed toilet and system was still not catching up due to clogged spin filter, replaced filter with a clean used filter. Override float for recirc tank was not working due to bad connection, fixed connection and float started to work. Customer said he will have pump tank pumped to get rid of stuff that keeps clogging spin filter and to make room in tank for usage during thanksgiving weekend. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/14/2023 | Alternative | RoutineScheduled | 109-08-0297 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Quanics |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | [] | NA | [16 empty] | Inspected | Cleaned the effluent filter- Water level was correct. Media looks good, good spray pattern and the float switches all tested ok, found roots in pump tank and a leak in the sprayer box. appeared due to settling, scheduled to return and repaiur - Pump counter 20507cycles vs 18348 Cycles last year ; Run time - meter 1059:09 hrs vs 956:10hrs last year. System appears operational- leak in tank is not external and has been fixed- | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/28/2023 | 09:30 AM
04/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance | SP-05-57 | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump" ,"Auxiliary Filter"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Auxiliary Filter" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | As noted previously, there is exposed drip tubing on the lower part of the dispersal area. We recommend contacting a landscaper to add topsoil and reseed this area. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/03/2023 | 05:43 AM
05/02/2023 |  | Routine/Scheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/18/2023 | 01:31 PM
10/05/2023 | Alternative | RoutineScheduled Component Maintenance | 033-06-0479-ST | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
11/28/2023 | Alternative | RoutineScheduled | 182-00-0459 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 12:00 AM
01/16/2023 | Alternative | Initial Visit | 103-STS-96797 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | AOSS - Install - VDH Permit 151-22-0046 Initiated installation of PE Permit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/17/2023 | 07:15 AM
03/07/2023 |  | RoutineScheduled |  | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Fixed air vac and valve box | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
08/18/2023 | Alternative | RoutineScheduled Component Maintenance | 175-14-0076 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
11/06/2023 | Alternative | RoutineScheduled Component Maintenance | 179-14-0291-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend removing the trees growing in the drainfield area to prevent root intrusions in the drainfield lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
11/03/2023 | Alternative | Routine/Scheduled | 145-STS-258782 | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 600 |  |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [16 empty] | Recommend pumpout | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/03/2023 | Dec 30 1899 9:30AM
10/20/2023 | Alternative | RoutineScheduled Component Maintenance | 179-17-0366-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Upon arrival system was in high level due to a filter clog. System went from 2.9 gpm to 5.2 gpm after servicing. We recommend pumping and cleaning the pump tank during next year?s inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
05/18/2023 | Alternative | Follow-Up Component Maintenance | 175-04-0706 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | Installed new recirculation pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 09:34 AM
01/24/2023 |  | Routine/Scheduled | 550-STS-6670 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 01/24/2023 |  | 17.000000 |  | 151.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 8:51AM
03/04/2023 |  | RoutineScheduled |  | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter","Control Operation"] | ["Auxiliary Filter","Control Operation"] | NA | [17 empty] | Annual inspection. Control panel circuit board has a bad recirculation pump control relay. Replaced circuit board on 3-11-2023. Set up timers and settings on new circuit board. 14" of accumulated solids in septic tank. Cleaned septic tank solids filter. 12" of solids in recirculation portion of treatment unit. 12" of solids in discharge portion of treatment unit. Flushed treatment unit spray manifold. Tested floats, pump and alarm. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/11/2023 | 07:03 PM
06/26/2023 | Alternative | Pump-Out Only | 04-160-0024 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [18 empty] | - pumped/cleaned septic tank and pump chamber - blower is not functional, customer has not given approval to proceed with replacement | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/27/2023 | 12:00 AM
10/07/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 4150 | BioMIcrobics MicroFast |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | 3rd Qtr. 2023 inspection. Grease trap accumulation - Chamber #1 - 2" crust, 6" bottom. Chamber #2 - 4" crust, 12" bottom. Chamber #3 - 1" crust, 24" bottom. Chamber #4 - 8" crust, 12" bottom. Solids in septic tank - First chamber - 8" crust, 12" bottom, Second chamber - 0" crust, 34" bottom. MicroFast clarifier- 0" crust, 42" solids. Needs to be pumped out. Cleaned blower filter. 15" solids in discharge pump tank. Needs to be pumped out. When the grease traps are pumped out, they need to be mixed. Currently the septic hauler is just sticking hose into tank and emptying. The accumulated grease on the sides are not being pumped out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | 07:03 PM
05/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Some of the lines are slightly wet in the gravel. No surfacing effluent. Recommend checking back in a few months. Advised homeowner to monitor water usage and notify us if there is any change in the field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/09/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 270505173 | Joshua | Hott | 1.000000 | 1500 |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/24/2023 |  | RoutineScheduled | 133 09 0379 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20-RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | Sludge level-minimal scum layer on top-8" sludge on bottom in Septic tank zone - Recir zone 10" sludge - Pump tank - light Trace sludge, Discharge zone 6" sludge, Pulled out and Cleaned Effluent filter, media looks clean, good spray on media. Float switches tested good, alarm test good. Recirc pump run time 870.1 hours and 64291 cycles and discharge pump has 65.8 hours run time and 144 cycles. Computer was in extreme high overcycling on arrival, Zero days trended in memory, system in start up mode, changes trend to 3 days. Alarms in history on April/8-9th/23, A lot of alerts in history.Soil is to close to the lid and may cause hinge damage We reccomend keeping lid 2 inches above grade to prevent infiltration, soil and roots in the treatment tank.Date set at 10-13-2000 reset date time but data maybe corrupt/ | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
10/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
08/23/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-89371 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Biotube filter was clogged up, cleaned. Replaced off float for discharge due to blue float being stock close. RECIRC: HL-2, LL-16, OVERRIDE-414. DISCHARGE: HL-3, LL-18, OVERRIDE-11. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
11/20/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Replaced the UV light bulb. The timer is set to 5 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/20/2023 | Dec 30 1899 1:15PM
09/12/2023 | Alternative | Follow-Up Component Maintenance | SWP-05-188 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Follow up. Replaced broken tipping trade and added Root destroyer in eco-flow pod. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
02/28/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
07/13/2023 | Alternative | Reportable Incident | 13-142-0104 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | Orenco Advantex |  | Pump | Pressure | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [17 empty] | Received a vericomm alert of discharge bottom float stuck down. Found relay bad replaced it. Cleaned effluent filter, flushed manifold. Changed recirc off time to 36min from 15 min. System should return to normal operation. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/13/2023 | Dec 30 1899 10:14AM
05/26/2023 |  |  | 033-18-0060-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
08/16/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
04/06/2023 | Alternative | RoutineScheduled | 159-02-315 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1500 | Advantex |  | Pump | Gravity | Pad | Not Applicable |  | ["SludgeScum Accumulation"] | [] | YES | [17 empty] | Tank should be pumped in near future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 12:00 AM
10/06/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1200 |  |  | Pump | Gravity | Drip | Not Applicable |  | ["None"] | ["None"] | NA | None | Clear | 7.040000 | 5.600000 | [13 empty] | Micro-fast system | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/26/2023 | Dec 30 1899 10:00AM
06/19/2023 | Alternative | Initial Visit | 085-STS-34892 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - System Commissioning - Initial Visit. Primary septic tank - normal level - effluent screen serviced. Processing Tank - recirc - recirc pump, media drapes, spray grid serviced - adjusted recirc return. U.V. - single bulb - operating - adjusted amperage settings. Processing Tank - discharge - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | Dec 30 1899 11:30AM
04/11/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 12:00 AM
03/28/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | pumped all | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
04/19/2023 | Alternative | Routine/Scheduled | 09-160-0146 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/19/2023 | 03:45 PM
01/31/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/03/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | 12:00 AM
02/10/2023 |  | RoutineScheduled | {FIPSCode}-STS-24251 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/10/2023 | 12:00 AM
10/02/2023 | Alternative | RoutineScheduled Component Maintenance | SD-05-414 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Turned on pump until 25 psi back-pressure was achieved, then opened flush valve fully. System flushed at 22 gpm for 4 minutes, then throttled back the return line valve to 25 psi. Roughly 31 psi showing on supply line gauge. Leaving the return line valve open a bit more (compared to last year) allowed for about a 2 gpm increase in flushing flow rate. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
01/26/2023 |  | Routine/Scheduled | 800-STS-14194 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | Jan 1 1900 1:50PM
07/20/2023 | Alternative | Routine/Scheduled | 151-12-0012 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Primary septic tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - concrete - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | 07:00 AM
09/14/2023 | Alternative | RoutineScheduled Component Maintenance | 175-04-0593 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
04/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend servicing advantex in the near future | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/29/2023 | Alternative |  |  | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
04/03/2023 |  | RoutineScheduled | 101-08-0267 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Biomicrobics |  | Pump | Pressure | Drip | Not Applicable | 150.000000 | ["BlowerCompressorAerator Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Distribution Pump Operation"] | YES |  |  | 0.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/11/2023 | 10:25 AM
05/16/2023 |  | Routine/Scheduled | 124-STS-2379 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 2.000000 | 1250 | None |  | Pump | Gravity | Trenches | Not Applicable |  | SludgeScum Accumulation | SludgeScum Accumulation | YES | [17 empty] | Replaced access risers on both septic tanks and replaced dbox and some of the header and force main. Pumped out first septic tank. System should return to normal operation. Field should be maintained as grass. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/22/2023 | Jan 1 1900 9:22AM
01/20/2023 |  | RoutineScheduled | 177-STS-90035 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
01/19/2023 |  | Pump-Out Only | 175-01-0768 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Clearstream | [8 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | 02:45 PM
10/09/2023 | Alternative | Routine/Scheduled | 04-174-0078 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Ecoflo |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/09/2023 | Dec 30 1899 2:24PM
05/13/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. Cleaned recirculation pump basket filter. Flushed treatment unit spray manifold. Cleaned solids from several spray heads. Sprayed solids off of treatment unit "sheets". 8" of solids in discharge pump tank. Tested floats, pumps and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/29/2023 | 07:03 PM
01/10/2023 |  | RoutineScheduled | 177-STS-88730 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Disinfection" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Disinfection" ,"Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
03/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air line had broken. DSS moved the blower and replaced the air line. System appears to be functioning as designed at this time | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
11/17/2023 | Alternative | RoutineScheduled Component Maintenance | 177-17-0044-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump"] | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump"] | NA | Sulphitic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
06/16/2023 | Alternative | RoutineScheduled Component Maintenance | 099-11-0042-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | It appears that a fence has been installed through the drainfield and the ends of the drainfield lines are overgrown with trees. We have sent the owner a copy of his system design. If there are trees in the drainfield area they should be removed to prevent root instrusions in the drainfield lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/10/2023 | 10:02 AM
08/19/2023 | Alternative | RoutineScheduled | 2008-01-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.900000 |  |  | 1.900000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/17/2023 | Alternative | Routine/Scheduled | 093-03-0092 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | Dec 30 1899 1:15PM
08/30/2023 | Alternative | RoutineScheduled | 06-195-518-DIS | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/30/2023 | 12:00 AM
08/11/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 | 1000 | 1000 | Pump | Pressure | Drip | Not Applicable |  | [] | [] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | 12:00 AM
02/28/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
04/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/20/2023 | Alternative | RoutineScheduled | VAG408440 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None |  | 8.210000 |  |  | 1.330000 |  | 09/20/2023 |  | 3.000000 |  |  | 1.000000 | [5 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/13/2023 | 04:15 PM
06/15/2023 | Alternative | RoutineScheduled | 150-08-0117 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 3.000000 | 2900 gallons | septic tank | Delta Whitewater | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","Control Operation"] | ["SludgeScum Accumulation","Level Sensor Operation","Distribution Pump Operation","BlowerCompressorAerator Operation","Control Operation"] | NA | Musty | Clear |  |  | 70.000000 | [12 empty] | Septic tank 6" fog, 3" sludge. Delta Whitewater 70% SS. Serviced aerator. Pump, alarm, floats, controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/23/2023 | 08:00 PM
01/19/2023 |  | RoutineScheduled | 179-13-0362-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend scraping the Advantex sheets & pumping tanks at your next inspection. We would also re-plumb the discharge pump plumbing that has settled inside the tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
12/29/2023 | Alternative | RoutineScheduled Component Maintenance | -STS-93247 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2024 | 07:56 AM
06/09/2023 | Alternative | RoutineScheduled | 11-142-0002 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/20/2023 |  | RoutineScheduled |  | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | PuraFlo |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 12:00 AM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance | 177-10-0129-ST | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/26/2023 |  | RoutineScheduled |  | Cumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Piedmont | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Drip | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/28/2023 | 12:00 AM
04/25/2023 | Alternative | RoutineScheduled | C102-12-0007 | Alleghany | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | Septic Tank Only | AdvantexAX20 | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter and spin filter was both cleaned. The recirculating and discharge pumps were pulled and sprayed off. The RSV valve was pulled and cleaned. The textile sheets were sprayed off. The pressure was adjusted on the treatment unit and the drip field. The controls were operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/24/2023 | Jan 1 1900 9:05PM
04/01/2023 |  | Reportable Incident | {FIPSCode}-STS-2015 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/01/2023 | Jan 1 1900 10:00AM
11/21/2023 | Alternative |  | 08-183-278 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/21/2023 |  | 8.910000 |  |  | 12.400000 |  |  | Will be sent separately |  | BOD: 8.91 TSS: 12.4 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/21/2023 | 12:00 AM
02/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Water Meter Readings: 01/10/2023 1831100 02/06/2023 1831100 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2023 | 08:47 AM
05/25/2023 |  | RoutineScheduled | 033-STS-89022 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/20/2023 |  | Routine/Scheduled |  | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Multiflo FTB |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - normal level MultiFlo ATU - normal level - mixing present - compressor serviced - socks serviced. Pump Tank - float sensors, pump and controls operating. LPP intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/24/2023 | 07:45 AM
12/05/2023 | Alternative | RoutineScheduled | 115-07-0489 | Campbell | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Acres of Virginia, Inc. |  | Melvin | Collins | 1.000000 | 1500 | Septic Tank | Ecoflo | Pump | Pressure | Drip | Not Applicable | 450.000000 | ["Auxiliary Filter","Other"] | ["Auxiliary Filter","Other"] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/12/2024 | 12:30 PM
04/03/2023 |  | RoutineScheduled | 132-05-0052 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 450.000000 | [] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | 12:00 AM
03/22/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
07/05/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | NA | [17 empty] | Septic Tank-10"sludge 2"scum/ Microfast-10"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time but may need the Septic-Microfast Tank pumped next year/ Blower air filter cleaned and blower working correctly/ Replaced faulty timer enable float during inspection/ Controls, pumps, floats and alarms now functioning properly/ Counts: Pump1-94 ETM-10h 24m/ Pump2- 90 ETM-10h 15m On-7m 2s Off-12h/ Peak off-9h 48m/ Peak-5/ High-6/ Replaced broken 20" tank lid/ No breakout or spongy areas on the LPD Pad Site. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/23/2023 | Alternative | RoutineScheduled Component Maintenance | 175-11-0126 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | 11:24 AM
04/13/2023 |  | RoutineScheduled | 177-18-0373-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | There appears to be a break in the drip line or a defective emitter at the end of the drip dispersal system. We recommend excavating and repairing this as soon as possible. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
09/07/2023 | Alternative | RoutineScheduled | 166-05-742 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters, checked peat, | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/06/2023 | Alternative | RoutineScheduled | 06-197-A10 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.500000 | 7.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/13/2023 | 12:00 AM
03/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank to Puraflo Modules | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium"] | [] | YES | [17 empty] | Septic Tank-8"sludge 0"scum/ Pump Tank-3"sludge 0"scum/ No pump out needed at this time/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-257263 ETM-0017085/ Pump2-076135 ETM-0016476/ Peat is broke down and require replacement in all 4 modules. No breakout or spongy areas at the Pad Site. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12:00 AM
10/17/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Puraflo peat needs replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/15/2023 | Dec 30 1899 2:02PM
05/08/2023 | Alternative |  | 15-177-1108 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | R & R Enterprises, Inc | 1942001111 | William | Robinson | 1.000000 | 1000 | AQUA SAFE ATU |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | 12:00 AM
02/21/2023 | Alternative | RoutineScheduled | 073-STS-96140 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1250 | Aquasafe |  | Pump | Gravity | Pad | Not Applicable |  | [] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/01/2023 | 12:00 AM
01/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
10/11/2023 | Alternative |  | SD-13-313 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Control Operation","SludgeScum Accumulation","Dispersal System Operation","Effluent Screens"] | YES | Sulphitic | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | 12:00 AM
11/20/2023 | Alternative | RoutineScheduled Component Maintenance | 177-07-0221-SP | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Control Operation"] | ["Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | The alarm horn in the control panel is not working and should be replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 01/02/2024 | 11:12 AM
12/12/2023 | Alternative | Routine/Scheduled | 095-STS-6849 | Williamsburg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | Dec 30 1899 10:30AM
08/23/2023 | Alternative | Routine/Scheduled | 007-STS-24858 | Amelia | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Piedmont | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/23/2023 | Dec 30 1899 12:57PM
04/16/2023 | Alternative | Routine/Scheduled | 149-STS-10436 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 2.000000 | 1000 |  |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/16/2023 | Dec 30 1899 11:30AM
02/05/2023 |  | Routine/Scheduled | 041-STS-260223 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/05/2023 | Jan 1 1900 10:00AM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | Delta Environmental Products, DF Series | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | One air release valve is not functioning properly. Corrections in progress. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-49 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
03/07/2023 | Alternative | RoutineScheduled | 061-STS-22203 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-4"sludge 3"scum/ .50 Microfast-3"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-004858 ETM-0022427 On-3m 25s Off-12h/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/03/2023 | Alternative | RoutineScheduled | 136-10-0052 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Virginia Septic Solutions LLC | 1942001500 | Justin | Barker | 1.000000 | 1000 | Ecopod |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/03/2023 | 12:00 AM
03/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Effluent pump had failed. It was replaced and the system appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/19/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 12:00 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | UV light is not functioning | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
08/07/2023 | Alternative | RoutineScheduled | 128-16-0082 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned pump intake, cleaned atu filter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/01/2023 | Alternative | Routine/Scheduled | 16-120-0107A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/01/2023 | Dec 30 1899 11:50AM
11/06/2023 | Alternative | RoutineScheduled | 133-STS-95841 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned atu filter, system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/25/2023 |  | Routine/Scheduled |  | Warren | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","Distribution Pump Operation","Effluent Screens"] | Auxiliary Filter | NO | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/05/2023 | 01:36 PM
01/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Air pre-filter cleaned as a matter of preventative maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
10/20/2023 | Alternative | RoutineScheduled | 04-160-0598 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000 | LPD |  | Pump | Pressure | Trenches | Not Applicable |  | [] | [] | NA | Septic | [15 empty] | Inspected | - recommend new 6in Tufftite lid and ring - recommend installing a 6x6 electrical box - recommend new lid for valve cover be installed | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/31/2023 | 12:00 AM
04/18/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
11/06/2023 | Alternative | RoutineScheduled Component Maintenance | 099-06-0307-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. musty strong smell around tank, maybe using product that causes that. System has a lot of trash as if garbage disposal being used, left note at door. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
03/09/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Fast | Pump | Pressure | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | 0 Scum 2" Of sludge. Filed looks good and dry. Alarms, floats Blower, pump are all operational. 462 Pump Cycles, 49h 54m Run time. Riser lids do not fit tight . recommend you get with the contractor to have this fixed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/27/2023 | 12:00 PM
09/08/2023 | Alternative | Reportable Incident | 234-16-403 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/08/2023 | Dec 30 1899 7:30AM
02/14/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Puraflo |  |  |  | Trenches |  |  | ["Septic Tank Baffles"] | ["Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | 12:00 AM
11/21/2023 | Alternative | RoutineScheduled | 1997-143-0096 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens","Control Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/17/2023 |  | RoutineScheduled | SP-05-357 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Control Operation" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation"] | YES | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Rsv was had alot of grease and seeds inside, cleaned. Spoke to customer about grease and nondegreadable material going down the drain. Recirc tank might need pumpout next year. Vacuumed seeds out of pump housing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
08/25/2023 | Alternative | RoutineScheduled | 05-100-1456 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | ECOFLO |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | [] | [] | YES | [17 empty] | SLUDGE TEST REVEALED 4" FROM BOTTOM-DOES NOT NEED PUMPED AT THIS TIME ALL COMPONENTS WORKING AS THEY SHOULD REPLACED PEAT IN SYSTEM | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/25/2023 | 12:35 PM
01/10/2023 |  |  | 15-118-0024 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | EZ Treat | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/27/2023 | 12:00 AM
03/27/2023 | Alternative | RoutineScheduled | 09-184-5002 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/27/2023 | 12:00 AM
11/06/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | Dec 30 1899 2:02PM
06/14/2023 | Alternative | RoutineScheduled Component Maintenance | 154-08-0055 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend replacing the filter for the air pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
04/12/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Drip system appears to be functioning exactly as designed. Field shows perfect emitter spacing. If viewed from Spinks Ferry, it might appear that there is a nitrified streak coming from the pump chamber riser down, but during inspection, there were no signs of any malfunction, sewage on the ground, or any other explanation for the discoloration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/10/2023 | Alternative | RoutineScheduled | 15-100-0393 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | RECIRCULATIING SAND FILTER |  |  | Pressure | Mound | UV | 450.000000 | [] | [] | [18 empty] | EVERYTHING WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/16/2023 | 10:00 AM
09/05/2023 | Alternative | RoutineScheduled | 16-137-0191 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | All In Septic Services | 1942001442 | Dennis | Mitchell | 1.000000 | 1250 | Norweco |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["Auxiliary Filter"] | NA | Musty | Clear | [14 empty] | Inspected | Sludge/Scum Accumulation - Septic 4" sludge 4" scum, ATU 2" sludge, Filter 12" sludge Aerator Amperage 4.1 Recommend Pumping in 2024 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | Dec 30 1899 9:30AM
08/08/2023 | Alternative | RoutineScheduled Component Maintenance | 177-09-0258 | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Puraflo modules are overgrown. Conditions observed on 2022 inspection. At last years inspection we observed the first two Puraflo modules were holding water. We also observed the pad was holding water and backing up into the sample chamber. 9/19 - MWebb will reach out to provider for any updates, then can send NOAV | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 09/01/2023 | 07:38 AM
10/16/2023 | Alternative | Reportable Incident | 115-18-0131 | Campbell | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1500 | Septic Tank | Ecoflo | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Other"] | ["Other"] | [18 empty] | Bio media was removed and new media installed in Eco flo pod. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/31/2023 | 10:30 AM
12/07/2023 | Alternative | Routine/Scheduled | 147-19-0041 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Trash Tank Condition of above Component Notes for above Component Above normal Level due to breaker inside of home being off System pumped to normal level once breaker was turned back on by customer. 6"of sludge and 5" of solids Discharge/Pump Tank Condition of above Component Notes for above Component Above normal Level due to breaker inside of home being off System pumped to normal level once breaker was turned back on by customer. 6" suspended solids Pulled and cleaned pump and floats. All floats and pump functioning properly Aeration Condition of above Component Notes for above Component Above normal Level due to breaker inside of home being off System pumped to normal level once breaker was turned back on by customer. 18" of suspended solids Pulled and cleaned weir and diffuser Air Pump/Blower Condition of above Component Notes for above Component 120v Pulled air filter Made sure housing was free of debris Control Panel Condition of above Component Notes for above Component 120v All audible and visual alarms are functioning properly Discharge pump pulled 8.0amps Air pump pulled .49amps Drain Field Condition of above Component Notes for above Component No signs of surfacing Customer wanted to skip distribution box inspection this year. And do it next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 11:59AM
11/21/2023 | Alternative | Reportable Incident | 800-11-0074 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/21/2023 | Dec 30 1899 2:00PM
01/12/2023 |  | RoutineScheduled | 033-17-0197-SP | Caroline | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"SludgeScum Accumulation" ,"Dispersal System Operation"] | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the Septic Tank and the Aerobic Treatment Unit due to sludge accumulation in the tanks. As we noted in our inspection report last February, the dispersal area is very spongy near the distribution box. We recommend contacting the Alternative Onsite Soil Evaluator (AOSE) who designe the system for further evaluation and possible recommended repairs. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/02/2023 | 07:17 AM
03/20/2023 |  | RoutineScheduled | 133 11 0106 | Franklin | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Gravity | Gravity | Trenches |  |  | ["None","Auxiliary Filter"] | ["None","Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 14" of accumulated solids in septic tank. Cleaned recirculation pump basket filter. Flushed treatment unit spray manifold. Tested floats, pump and alarm. Replaced recirculation pump magnetic contactor. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/11/2023 | 07:03 PM
08/29/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 08/29/2023 | Sample Chamber | 13.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/20/2023 | Alternative | RoutineScheduled | 107-05-0472 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Septic Tank Baffles"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles"] | [18 empty] | Blower seems to be running hot. Schedule for eval | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2024 | 12:00 AM
05/01/2023 | Alternative | Routine/Scheduled | 800-11-0073 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | Dec 30 1899 10:40AM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance | SD-89-288 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity |  | Chlorination |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | 8.100000 | 18.100000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 11/15/2023 | 02:02 PM
04/17/2023 | Alternative | RoutineScheduled | 061-STS-22612 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance | 177-09-0059-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
08/08/2023 | Alternative | Initial Visit |  | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | Effluent Screens | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit Primary septic tank - effluent screen broken - approved to replace - serviced. Pump Basin - plastic - float sensors, pump and controls operating. BioFilter - fiberglass - appears intact - peatmoss in fair condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | 08:30 AM
10/27/2023 | Alternative | RoutineScheduled Component Maintenance | 175-10-0353 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
06/21/2023 | Alternative | Follow-Up Component Maintenance | 175-13-0028 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed enable float, heater for hydraulic unit & repaired fittings. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
06/20/2023 | Alternative | RoutineScheduled | 153-STS-18990 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | YES | [17 empty] | Septic Tank-8"sludge 0"scum/ EZ-Treat Recirc. Tank-3"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Recirc. Pump intake cleaned and unit dosing correctly/ Controls, pumps, floats and alarms functioning properly/ Pump Tank Counts- 530 ETM-27h 51m/ High-8 On-3m 12s Off-12h/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/12/2023 |  |  | 177-07-0293-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
06/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
05/10/2023 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Puraflo |  | Pump | Gravity | Trenches |  | 450.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | 01:59 PM
09/27/2023 | Alternative | RoutineScheduled | 00-142-0600 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/12/2023 | Alternative | RoutineScheduled | 07-197-A2 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 4 - Blue Crystal tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/12/2023 | 12:00 AM
01/03/2023 |  | Routine/Scheduled | 2007-143-0230 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/03/2023 | 04:46 PM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 |  | none | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NO | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/10/2023 | 11:17 AM
01/04/2023 |  | Routine/Scheduled | 550-STS-6601 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 |  |  |  | 01/24/2023 |  | 5.000000 |  | 61.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 10:50AM
01/23/2023 |  | RoutineScheduled | 179-09-0062-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"Recirculation Pump"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Sample really cloudy. Recirc valve was clogged with sludge. The whole system was very dirty as if something is being used in the house that is messing up treatment. Left copy of Do's and don'ts. Cleaned pump intake, biotube and sheets that should help clean treatment. System has a few had 4 high level alarms in December and 4 in january most likely due to clogged Recirc valve. Water level normal after cleaning. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
03/22/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | septic tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
12/20/2023 | Alternative | Routine/Scheduled | 085-STS-33307 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Septic Tank Condition of above Component Notes for above Component Water level high due to clogged effluent screen. Flushed and cleaned effluent screen and water level returned to normal. Not due for pump out Recirculation Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Discharge/Pump Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats. Media Sheets Condition of above Component Notes for above Component Cleaned media sheets. Checked and confirmed spray pattern is good. Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | Dec 30 1899 8:38AM
03/29/2023 |  | RoutineScheduled | 179-STS-92280 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Black | [13 empty] | Will be sent separately | Inspected | We continue to recommend remounting the control panel & resealing the riser on the pump tank. We also recommend replacing the 4" male plug on the pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
04/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was in the off position and not running. That was resolved at the time of inspection. Lower Distribution box orange blank is broken and had roots coming in. Recommend replacing pump tank lid. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
04/07/2023 | Alternative | Routine/Scheduled | 04-160-0061 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/07/2023 | 02:00 PM
04/12/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Advantex AX25RT |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge levels 7" sludge in septic tank, 5-6" in recirc zone 5" in discharge zone, Alarm and light works. No roots visable, Cleaned biofilter, it was backed up and glogged about 6" over baffle, Recirc pump has 981 hours and 72 419 cycles on it. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance | 179-10-0184-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
10/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation" ,"Dispersal System Operation" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"Control Operation" ,"Dispersal System Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced both pumps and control panel Please keep all areas including drainfield mowed and maintained | This AOSS should now return to normal function after having provided the above state routine maintenance | 11/22/2023 | 09:18 AM
10/30/2023 | Alternative | Routine/Scheduled | 150-06-075 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level Has 1" of solids and 1" of sludge Pulled and cleaned rsv -Recirculation Tank: At normal level Has 4" of sludge Pulled and cleaned pump, floats and filter Pump and floats replaced recently -Media Sheets: Sheets in decent shape, may need wanting soon Brushed and flushed laterals Sprayed of sheets and flushed chamber -Control Panel: Panel functioning properly Visual and audible alarms working Recirc pulling 10.70amps -Distribution Box: Concrete dbox at grade At normal level Minor grass roots coming through lid -Drain Field: Showing no signs of surfacing or blowouts | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | 08:50 AM
02/07/2023 |  | RoutineScheduled | 133 04 1026 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | BioWheel |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | Monthly Report. Total flow for month of January 2023 - 49,407 gallons. Average daily flow - 1,594 gallons | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/08/2023 | 07:03 PM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/01/2023 |  | Routine/Scheduled | 234-15-263 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | Jan 1 1900 2:55PM
05/13/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. Cleaned septic tank solids filter. 10" of solids in recirculation portion of treatment unit. 8" in discharge portion of treatment unit. Flushed treatment unit spray manifold. The treatment unit may need to be pumped out next year due to solids buildup. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/17/2023 | 07:03 PM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance | SD-05-214 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
05/02/2023 | Alternative | RoutineScheduled | 061-17-045 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | EcoVirginia LLC | 1942001235 | William | Poindexter | 2.000000 |  | Advantex ATU |  | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","Effluent Screens"] | ["Attached Growth Medium","Auxiliary Filter","Effluent Screens"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/07/2023 | Alternative | Routine/Scheduled | 093-11-0089 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | Dec 30 1899 1:15PM
11/15/2023 | Alternative | RoutineScheduled | 115-07-0522 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 12000 | Dual Biomicrobics Fast 2.5 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Level Sensor Operation","Control Operation","Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Effluent Screens","Level Sensor Operation","Control Operation","Auxiliary Filter","BlowerCompressorAerator Operation"] | YES | [16 empty] | Inspected | Septic Tank #1 Sludge levels- 2" scum and 14-18" sludge , septic tank #2 minimal scum and 12-18" sludge trace- Fast treatment units have good Aeration- One blower motor has been replaced due to recent failure- Fast #1 12" sludge layer and Fast #2 8" sludge. Cleaned blower airfilters, Good Aeration observed from both Blowers, cleaned all the probes. Took pH and Do Readings. Cleaned both Effluent screens. Treatment unit #1 7.9 DO and 7.3 pH 19.0c. Treatment unit #2 7.8 DO, pH 7.0. pH 19.0c. In pump tank pH was 7.1 @ 19.0c -TSS#1 1000 #2 800 - Effluent meter reading 7036868 previous 6906203 vs 6814689 84 days 130,665 gallons or about 1,555 gallons per day. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | 09:30 AM
08/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Distribution Pump Operation" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Access to control panel, tank manway lid, and filterbed all blocked by tall, thorny weeds. Cut down enough to complete service today, but advised owner that more work is needed. While repairing broken discharge line (near filterbed connection), it was discovered that both vent pipe hubs were broken. Removed broken fittings and removed hard-packed soil from inside pipes as best as possible. Installed new tees and fitting to connect discharge piping, extended vent pipes and added rodent guards. During testing, effluent was observed at manifold inlet but not seen at other side of manifold. Effluent did not back up, but the lack of visible flow to the other side could indicate additional dirt remains. Filterbed is in poor shape overall. Several gopher holes visible, weeds growing instead of grass, bare gravel in some areas, and not a single tree growing. Lack of proper vegetation is partly due to low water use in the house. Weeds need to be removed, dirt added (or moved around) as needed, and drought-resistant grass seed put down. At least one approved tree needs to be planted on the filterbed, more if number of occupants increases. Filterbed will need to be carefully watered to establish the grass. A site visit will be needed within 6 months to check the operation and vegetation growth. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 06:43 AM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance | 179-13-0180-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
02/21/2023 |  | Routine/Scheduled | 228-05-0723 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/21/2023 | Jan 1 1900 11:35AM
08/22/2023 | Alternative | Routine/Scheduled |  | King William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 1000.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - grease trap - normal level Secondary septic tank - normal level - effluent screen serviced. Pump tank - float sensors, pump and controls operating. Biofilter - peatmoss spent - ponding and saturated. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/28/2023 | 06:45 AM
12/14/2023 | Alternative | Reportable Incident | 166-16-064 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Replaced failed UV bulb. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
11/01/2023 | Alternative | Routine/Scheduled | 166-14-193 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Mound |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 75.000000 | [11 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | 05:04 PM
08/09/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-70 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Zone 1 solenoid would only chatter and not allow effluent flow to the lower mound (zone 1). Replaced that solenoid and base. Advised owner to cut down the large, dead tree next to his tanks and panel before it fell down and caused a lot of damage. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
08/16/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | replace pressure gauge in pump tank at next inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/16/2023 | 12:00 AM
03/09/2023 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 02:34 PM
01/03/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | None | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/13/2023 | 07:55 AM
10/24/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/24/2023 | Dec 30 1899 10:45AM
05/18/2023 |  | Routine/Scheduled | 234-17-0299 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/18/2023 | Jan 1 1900 12:15PM
06/28/2023 | Alternative | RoutineScheduled | 04-142-0535 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Drainfield Solutions | 2705163102 | Michele | Ware | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/14/2023 | 12:00 AM
02/03/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank to Puraflo Modules | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NO | [17 empty] | Septic Tank-7"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Puraflo Peat turned in all 6 modules and dosing properly/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-8509 ETM-84h 39m/ Pump2-8484 ETM-84h 23m/ Peak-17/ High-18/ No breakout or spongy areas in the Pad Area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/09/2023 | Alternative | RoutineScheduled Component Maintenance | 179-13-0363-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection and routine maintenance completed. In the past 30 days, system averaged 3.5 discharge cycles per day (maximum allowed is 12). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
03/09/2023 | Alternative | Reportable Incident | 073-STS-104727 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | [18 empty] | COSS - Maintenance - GMP2018-02 Replaced damaged DBox with new concrete dbox. Replaced damaged header lines with new 4" PVC Spliced to existing conveyance line. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | 07:30 AM
06/14/2023 | Alternative | Routine/Scheduled | 159-02-198 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Aeration Tank - normal level - mixing present - compressor serviced. Pump tank - float sensors, pump and controls operating. DBox - plastic - deformed from ground pressure. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 11:00 AM
03/07/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"SludgeScum Accumulation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter" ,"Attached Growth Medium"] | NA | [7 empty] | 03/07/2023 |  | 74.000000 | [5 empty] | Will be sent separately | Inspected | Recommend pumping of fuji tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
11/14/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | Dec 30 1899 10:20AM
03/14/2023 |  | Initial Visit | 107-18-0354 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip |  |  | ["Attached Growth Medium","Auxiliary Filter","Septic Tank Baffles"] | ["Attached Growth Medium","Auxiliary Filter","Septic Tank Baffles"] | [18 empty] | vent pipe broken. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 12:00 AM
05/04/2023 | Alternative | RoutineScheduled | R18-180-0016 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | EZ Treat |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | [18 empty] | Annual inspection. Septic Tank - 4" solids crust, 6" of solids on the bottom. Recirculation tank - First section - 2" solids, second section - 10" solids. Discharge pump tank - 0" solids. Cleaned recirculation tank filter. Flushed spray manifolds. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | Jan 1 1900 7:03PM
03/02/2023 | Alternative | RoutineScheduled | SD-08-089 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | Upon arrival, the system did not appear to be properly programmed and the audible alarm was not operating. Reset system. Follow-up visit on 3/5 confirmed that audible alarm was operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
08/21/2023 | Alternative | Reportable Incident Component Maintenance | SWP-04-325 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to failed effluent pump for dosing drainfield. Replaced failed pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
07/12/2023 | Alternative | Routine/Scheduled | 550-STS-6335 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | Dec 30 1899 10:20AM
01/06/2023 |  | RoutineScheduled |  | Buckingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["SludgeScum Accumulation","Effluent Screens"] | ["Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/06/2023 | Jan 1 1900 3:00PM
04/12/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20RT |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | [16 empty] | Inspected | Scum 1 " and 10" Sludge in Septic tank, recirc zone 710in., discharge zone 14 in, Ran system in test mode, Alarm test well. Has monitoring connected, Pump working, flushed sprayers and manifold, Ran in test mode- Pulled out and flushed the recirc pump and improved the spray pattern Pump is a pf150311 and they reccomend to use the pf 300511 if replaced. Float switches test good. cleaning improved spray pressure after pulling out pump. Recirc pump 2780.2 hours and 74745 cycles on meter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
11/09/2023 | Alternative | Routine/Scheduled | 151-16-0016 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 10.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/09/2023 | 07:09 PM
06/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
04/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend evaluating distribution box later this year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | Dec 30 1899 11:24AM
03/29/2023 | Alternative | RoutineScheduled | 133-STS-96435 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/23/2023 |  | RoutineScheduled | 099-11-0040-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend moving small tree planted near header pipes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
11/17/2023 | Alternative | RoutineScheduled | 107-18-0077 | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | [18 empty] | FAST cleaned due to obstruction | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/17/2023 | 12:00 AM
08/07/2023 | Alternative | Initial Visit | 115-01-0441 | Campbell | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Central | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1500 | Septic Tank | Puraflo | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Other"] | [] | [18 empty] | All three pods full of effluent and draining to ground surface distribution box broke VDH site visit Sept. 26, 2023 no sewage on ground noted. GAG | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/22/2023 | 02:15 AM
03/30/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
08/07/2023 | Alternative | Reportable Incident | 115-12-0008 | Campbell | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | EcopodN |  | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | System was pumped out prior to our visit. Found one of the air relief valves in the drainfield had failed due to age and time. It was not sealing and flodded effluent onto the surface of drainfield. We replaced both the air relief valves and the system has rteturned to normal operation.. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/30/2023 | 09:30 AM
08/30/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
10/11/2023 | Alternative | RoutineScheduled Component Maintenance | 099-STS-87767 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation"] | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Roots in D-box coming from line # 3, removed roots and added Root-x. Recommend to add Root-x every year due to big tree close box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
08/09/2023 | Alternative | Follow-Up Component Maintenance | 179-17-0025-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [7 empty] | 08/09/2023 |  | 21.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
09/19/2023 | Alternative | RoutineScheduled | 075-STS-33138 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Carrington Pump & Irrigation | 1942001121 | John | Carrington | 1.000000 |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Effluent Screens","Control Operation"] | ["Effluent Screens","BlowerCompressorAerator Operation","Control Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 12:00 AM
10/26/2023 | Alternative | RoutineScheduled Component Maintenance | 175-15-0248 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Gravity | Gravity |  | UV |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 11/15/2023 | 02:02 PM
12/20/2023 | Alternative | Routine/Scheduled | 03-137-202 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Type of System Alternative Type of AOSS System Concrete ecoflo Septic Tank Condition of above Component Notes for above Component Normal level 4 in of sludge less than 1 in of solids Pulled and cleaned filter Filter housing is broken Riser showing signs of leaking Discharge/Pump Tank Pump chamber Condition of above Component Notes for above Component High level upon arrival due to pump being clogged with peat moss Tested floats all working properly Junction box is broken off from sidewall and free hanging Removed blockage from pump it is now working and moving properly All plumbing intact Returned to normal level Peat Moss Condition of above Component Notes for above Component Tipping bucket and dispersal trays intact and functional Peat moss has very minor ponding and deterioration Raked peat moss evenly No cracks nor breaks in module No signs of root intrusion Control Panel Condition of above Component Notes for above Component 120 volts coming in All visual and audible alarms functional Pump pulled 7.1 amps All components working as should Distribution Box Condition of above Component Notes for above Component Normal level 4 lines all intact and properly taking water Speed balancers intact and functional Minor hairline crack on the lid Drain Field Condition of above Component Notes for above Component No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | Dec 30 1899 8:36AM
12/08/2023 | Alternative | RoutineScheduled Component Maintenance | 179-10-0001-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Rountine inspection. Could not give contract due to septic water level being high due to a clogged pipe, tank elevation being wrong or tank installed backwards. Homeover did not want us to look into this further and asked if we could follow in a couple months. Septic tank being in high level like this can cause the sewer line to get clogged and cause a backup into the house. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
04/25/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 300 | Microfast |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Fast Septic Tank front 1-2: scum and 4-5" sludge in newish color Fast Septic side 1-2" scum and 8" sludge on bottom, Pump tank clear with a trace of sludge, Cleaned spin filter. Added rootx to system pump tank. New Blower motor on Fast Treatment unit working good, fully operational. Alarm test good, Pump test good 2 min cycles Pumped dec 2022 by Foutz. 77421 cycles 1,629.72 hours on pump time. Discharge meter reads 1,193,730 Gallons | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/25/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | System failed pods are holding water and tree roots growing in the pods. Also needs all three floats replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12:00 AM
04/12/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | A septic system inspection was done . The realtor and contract stated no digging up the d-box. So no d-box, header lines or drain field lines were looked at. There is a cleanout near the house that we ran the camera snake thru. The sewer line was clear. The septic tank has a riser on the inlet side of the tank. The top of the tank is 3 feet below the surface. The opening of the concrete tank is 1 foot by 2 foot. We were only able to stick our head in and look around. We did not see any leaks. The inlet and outlet T's are pvc We probed the drain field and it was dry. At this time the septic system appears to be in working condition. This inspection does not guarantee the life of any component. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
04/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/28/2023 | Alternative | RoutineScheduled | -STS-27085 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Septic Tank | Pura Flo | Pump | Gravity | Trenches | Not Applicable | 50.000000 | ["SludgeScum Accumulation","Control Operation"] | ["SludgeScum Accumulation","Control Operation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/01/2023 | 12:00 AM
09/13/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  | Norweco Trench |  | Pump | Pressure | Discharge | Not Applicable | 600.000000 | ["None"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 12:00 AM
03/07/2023 |  | RoutineScheduled | 124-STS-2379 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Norweco Singulair |  | Pump | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | 12:00 AM
09/13/2023 | Alternative |  | 179-14-0081-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
11/22/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/22/2023 | Alternative | RoutineScheduled | 150-06-116 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/23/2023 | 12:45 PM
04/19/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Effluent Screens" ,"Recirculation Pump" ,"Disinfection"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | UV bulb & chord needs replacement. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | Jan 1 1900 12:48PM
06/06/2023 | Alternative |  | 98-197-A2 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 06/06/2023 |  | 2.560000 |  |  | 1.400000 |  |  | Will be sent separately |  | BOD: 2.56 TSS: 1.40 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/06/2023 | 12:00 AM
02/23/2023 |  | Routine/Scheduled | 15-137-0170 | Goochland | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1250 | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [17 empty] | Effluent filter cleaned. Manifold flushed. Appears to be a lot of buildup on the sheets and spinners. System may not be breathing correctly and may need a vent on the septic tank. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 02/23/2023 | Jan 1 1900 11:25AM
11/16/2023 | Alternative |  | 09-184-5002 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/16/2023 |  | 2.960000 |  |  | 2.600000 |  |  | Will be sent separately |  | BOD: 2.96 TSS: 2.60 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | 12:00 AM
08/25/2023 | Alternative | Follow-Up | 121-STS-13299 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [18 empty] | Blower Service Call - Upon arrival breaker was turned off. Turned the breaker back on and the blower is working at this time. If the breaker cuts off agian may need further work. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
12/28/2023 | Alternative | RoutineScheduled | 03-163-0258 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 4.000000 |  | Advantex AX20 |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Control Operation","Auxiliary Filter","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 12:00 AM
09/06/2023 | Alternative | Routine/Scheduled | 11-160-0179 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | 02:45 PM
07/12/2023 | Alternative | RoutineScheduled |  | Shenandoah | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Multi flo |  |  | Gravity | Discharge | Chlorination |  | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | [17 empty] | Pumped Out | pumped out 7/18/23. No discharge at this time | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/18/2023 | 12:00 AM
02/24/2023 |  | Routine/Scheduled | 2009-143-0110 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Hoot |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Supervised pumpout of trash tank and pump tank by Commonwealth Waste Solutions. Serviced compressor and drip headworks while on property. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/27/2023 | 08:00 AM
03/09/2023 |  | RoutineScheduled | 101-12-0027 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
12/19/2023 | Alternative | Reportable Incident | 147-15-0096 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Pumped and cleaned the pump tank and pumped out the bottom and top of the Clearstream. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The timer is set to 8 minutes every 1 hour. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/19/2023 | Dec 30 1899 1:40PM
08/02/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
10/26/2023 | Alternative | Routine/Scheduled | 154-14-0002 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [17 empty] | Effluent filter cleaned. Manifold flushed. Discharge bottom float not working. Effluent filter was clogged. Recommend pump out and replace float. System appears to be operating normally. Just a reminder, the IP kit was installed earlier this year in the control panel. This upgrade was performed to provide a means of connecting remotely to the control panel using the Internet instead of a landline phone connection. At our last visit, the connection (wiring) to the control was still not performed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/26/2023 | 12:22 PM
09/12/2023 | Alternative |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 | 1250 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 4:00PM
08/07/2023 | Alternative | Routine/Scheduled | S 800-13-0161 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | Dec 30 1899 10:00AM
04/27/2023 |  | Routine/Scheduled | 550-STS-6576 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/27/2023 | Jan 1 1900 1:20PM
01/06/2023 |  | RoutineScheduled | 13-184-5001 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 16 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/06/2023 | 12:00 AM
02/09/2023 |  | Follow-Up | 234-18-242 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Control Operation","Disinfection"] | ["Control Operation","Disinfection"] | N/A | [17 empty] | Replaced Salcor bulb and cord | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/09/2023 | Jan 1 1900 1:00PM
02/07/2023 |  | RoutineScheduled | 099-12-0082-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We removed roots that were growing under a small section of the Advantex lid gaskets. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
12/19/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NO | [17 empty] | Arrived onsite and the system was in alarm. Found a leak in the basement ejector pump/ Septic Tank-4"sludge 3"scum/ EZ-Treat Recirculation Tank-2"sludge 0"scum/ All spray heads were clean and the recirculation pump intake were cleaned/ Media in good condition/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/23/2023 |  |  | 132-16-0030 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Virginia Soils Inc, dba VSI Supply / AG Onsite | 1942001291 | Archie | Arnold | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/15/2023 | 12:00 AM
04/26/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
07/27/2023 | Alternative | RoutineScheduled Component Maintenance | 033-STS-90537 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend replacing the EZ Set riser lid on the Pump Tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
10/17/2023 | Alternative | Reportable Incident | S 800-17-0240 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in both Clearstreams. Changed the diffuser in both Clearstreams and changed both aerator filters. Installed an aerator rebuild kit on one. Replaced pressure switch assembly on one aerator. The timer is set to 1.5 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/17/2023 | Dec 30 1899 10:00AM
02/14/2023 |  | RoutineScheduled | 153-STS-20264 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/14/2023 | 05:31 AM
07/07/2023 | Alternative | RoutineScheduled | 179-18-0099-SP | Fredericksburg | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock | Mckim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/20/2023 | 07:45 AM
01/20/2023 |  | RoutineScheduled | 17-100-0016 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1250 | Septic Tank | Ecopod E50N | Gravity | Pressure | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/22/2023 | 09:35 AM
03/13/2023 |  | RoutineScheduled | 18-100-0018 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | 12:00 AM
08/28/2023 | Alternative | RoutineScheduled | 107-05-0054 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  |  | Trenches | Not Applicable |  | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | 12:00 AM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/10/2023 | 11:17 AM
04/20/2023 |  | Follow-Up | 175-16-0066 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Service call only to replace faulty Blower VFC200P-5T. Tested new blower and now functioning properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
08/09/2023 | Alternative | RoutineScheduled Component Maintenance | SD-04-572 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | Annual inspection. Tried again to locate the older septic tank from the 80's. Probing was unsuccessful as the ground contains too many rocks. Could only find 1 clean-out. Sewer line should have them every 50'. Recommend using fiber optic camera and electronic locator to find old septic tank and additional clean-outs. Need to add a riser to grade to facilitate inspections and pump-outs. First pod on left is root-bound and peat is very dry compared to the other 2 pods. Recommend attempting to break up those roots and try to verify if the supply line is intact. Peat is still in okay shape as it has not gotten heavy use (roughly 200 cycles per year). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/24/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/21/2023 | Alternative |  | 04-197-A11 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/21/2023 |  | 9.900000 |  |  | 2.930000 |  |  | Will be sent separately |  | BOD: 9.92 TSS: 2.93 SV | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/21/2023 | 12:00 AM
12/05/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Disinfection","Dispersal System Operation","Distribution Pump Operation"] | ["Disinfection","Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Weir filter was clogged | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/05/2023 | Dec 30 1899 9:00AM
04/11/2023 |  | Pump-Out Only | 175-03-0761 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Aquarobic Mini Plant | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 09:48 AM
02/06/2023 |  | RoutineScheduled | 179-10-0142-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | As we noted on our last inspection, it appears that a concrete floor has been poured on the ends of the drainfield lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
11/27/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Control Operation","Dispersal System Operation","Level Sensor Operation"] | ["Control Operation","Dispersal System Operation","Level Sensor Operation"] | N/A | [17 empty] | Replaced float | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/27/2023 | Dec 30 1899 8:00AM
11/02/2023 | Alternative | Routine/Scheduled | 800-11-0074 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | Dec 30 1899 9:05AM
04/19/2023 |  | Routine/Scheduled | 2016-143-0199 | Henrico | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Henrico | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. There is visible wetness on the drainfield - needs to be addressed. The timer is set to 3 minutes every 3.5 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/19/2023 | 09:00 AM
11/15/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 11:30 AM
05/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Pump tank casing needs to be sealed. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | Dec 30 1899 12:05PM
12/31/2023 | Alternative | RoutineScheduled | 151-17-002 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | KC Forge Environmental Service, LLC | 1942001034 | Kent | Cuthbertson | 4.000000 | 45000 | 15000 | 15000 | Pump | Gravity | Trenches | UV | 19884.000000 | ["None"] | ["None"] | YES | [15 empty] | Attached to this report |  | The Holiday Season kept us from sampling the usual sampling schedule. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/28/2024 | 01:30 PM
02/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"Auxiliary Filter"] | ["Disinfection" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | Dec 30 1899 2:21PM
09/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and pumping | 1942001330 | Michelle | McKim | 3.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 3:40PM
02/02/2023 | Alternative | Pump-Out Only | 124-STS-2379 | Falls Church | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | [9 empty] | ["SludgeScum Accumulation"] | [] | NA | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/05/2023 | Dec 30 1899 1:45PM
06/05/2023 | Alternative |  | 18-100-0018 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
06/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower failed. New blower was installed and appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/27/2023 |  | RoutineScheduled | 175-17-0164 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Float for inside alarm stuck on during testing, replaced it. Drip rate for zone 2 initially was very high due to a broken air release valve (supply) that was hit by a mower. Replaced ARV and 6" valve box, flushed the zone. Septic tank will most likely need pumping before next year's inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/05/2023 | 07:56 AM
11/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend flushing and balancing the lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/02/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
10/23/2023 | Alternative | RoutineScheduled | 2007-143-0187 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1250 | EcoFlo |  | Pump | Pressure | Trenches |  |  | ["Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 12:00 AM
06/05/2023 |  |  | 033-07-0291-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | 12:00 AM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/07/2023 | Alternative | RoutineScheduled | 11-184-5001 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 12 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/07/2023 | 12:00 AM
03/24/2023 |  | Routine/Scheduled | 550-STS-5864 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - normal level Secondary septic tank? - normal level - recommend pump out. Aeration Tank - normal level - mixing present - compressor serviced. U.V. Disinfection - bulb and housing serviced. Pump tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | Jan 1 1900 7:30AM
08/23/2023 | Alternative | RoutineScheduled Component Maintenance | SD-02-193 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance | 099-07-0017-SR | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. 4 wet spots on drip field, repaired 2 and the water came above ground on 2 more spots try contacting customer but was able to. Will send proposal for chlorine flushing drip and repairing bad emitters. Recommend replacing air filter, will also send price for replacing that. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/19/2023 | Alternative | RoutineScheduled | 133-STS-97743 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | system checked - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/22/2023 | Alternative | RoutineScheduled | 13-173-009 | Prince Edward | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1500 | Septic | Norweco | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Effluent Screens","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/22/2023 | Dec 30 1899 9:00AM
12/27/2023 | Alternative | RoutineScheduled | 107-09-0162 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
02/13/2023 | Alternative | RoutineScheduled | 121-STS-13346 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 | 1000 | Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | Septic | Dark Brown | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/18/2023 | Alternative |  | 132-15-0022 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Richard | Yowell | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/23/2023 | Alternative | Routine/Scheduled | 06-103-0156 | Amelia | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Piedmont | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Best 1 |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/23/2023 | Dec 30 1899 9:14AM
05/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
09/14/2023 | Alternative | Routine/Scheduled | 093-13-0081 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Flushed and cleaned vortex filter -Aeration: Water level normal. Flushed and cleaned weir. Flushed and cleaned diffuser. Checked and confirmed high level alarm float is functioning properly. -Air Pump/Blower: Checked and confirmed aerator is functioning properly. Flushed and cleaned aerator air intake filter. -Control Panel: Checked and confirmed components within control panel are functioning. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Drip Field: Noted moist area towards the end of the dispersal area. Homeowner placed a shed on top of the dispersal field. Homeowner was informed not to place structures on top of the dispersal field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | Dec 30 1899 1:07PM
10/17/2023 | Alternative | RoutineScheduled Component Maintenance | SP-04-430 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
04/19/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 12:00 AM
08/29/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-4733 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Hoot |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/29/2023 | Dec 30 1899 10:05AM
03/13/2023 |  | RoutineScheduled | 181-01-0084 (LEGACY ALT. SYSTEM) | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 2.000000 | 1500 |  |  | Pump | Pressure | Trenches | Not Applicable |  | ["Auxiliary Filter","SludgeScum Accumulation"] | ["Auxiliary Filter","SludgeScum Accumulation"] | NA | [16 empty] | Pumped Out | Filter checked and cleaned. No apparent leaks in system or drain field area. Septic system pumped and cleaned. Control panel functioning properly. Lid properly secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/13/2023 | 08:30 PM
06/07/2023 | Alternative | Reportable Incident Component Maintenance | 175-13-0286 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Clearstream | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"SludgeScum Accumulation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Distribution Pump Operation" ,"Auxiliary Filter"] | NA | Septic | Cloudy | [13 empty] | Will be sent separately | Inspected | Owner noticed wet area by pump tank. Headworks was full of effluent which would leak out during a pump cycle. Glue joint had failed between flex pipe and 1" 45* elbow. Replaced flex pipe and 3 pvc fittings to make the repair. Replaced crushed, dirty spin filter and cleaned both solenoid valves. Did a quick check on tanks. Septic tank and pump tank both need pumped out. Owner made appointment with local pumper for June 20th. Blower was stone cold, not running. Blower needs replaced as well as the air filter and the air diffuser. The atu panel needs new switches, boots, alarm horn and light. Lid for zoner box is damaged and needs replaced. Owners were unaware of requirement for annual inspections. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
03/29/2023 |  | RoutineScheduled | {FIPSCode}-STS-15845 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Septic tank does not have risers. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
09/18/2023 | Alternative |  |  | Shenandoah | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  |  | Discharge | Chlorination |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | [18 empty] | replaced blower | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 11/06/2023 | 12:00 AM
06/28/2023 | Alternative | Routine/Scheduled | 033-STS-90329 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 600 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 10:30 AM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance | 033-18-0216-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/28/2023 |  |  | 113-18-074 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/09/2023 | 12:00 AM
02/14/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
01/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | Dec 30 1899 2:21PM
10/30/2023 | Alternative | RoutineScheduled | SD-05-74 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 65.600000 | ["SludgeScum Accumulation","Effluent Screens"] | ["SludgeScum Accumulation","Effluent Screens"] | YES | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/30/2023 | 09:00 AM
05/19/2023 | Alternative | Routine/Scheduled | 157-04-340 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation"] | [18 empty] | Serviced Eco-Flo. Pump, floats, and panel (ok). Raked out peat. Septic does not need pumping. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | 12:00 PM
10/19/2023 | Alternative | Routine/Scheduled | 166-11-088 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal Level 2 inches of sludge and 1 inch of solids Pulled and cleaned filter No signs of infiltration -Discharge/Pump Tank: Normal Level All floats and pump are functioning properly however they are Aged Junction box for floats and pump connections is buried -Peat Moss: Tipping bucket and dispersal trays are intact and functioning properly Peat moss was saturated but raked out good -Distribution Box: Unable to locate -Drain Field: No signs of surfacing Repair (10/24): -Installation of a Goulds Pump includes: - Removal & disposal of spent Pump - Manufacturer Warranty -Installation of 2 Floats | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/30/2023 | 11:48 AM
09/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 4:00PM
03/06/2023 | Alternative | Routine/Scheduled | SHUN-B7KMPL | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Drip | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - recommend pumpout next service event. Aeration Tank - normal level - mixing present - compressor serviced. U.V. - bulb and housing serviced. PUmp Tank - float sensors pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | Dec 30 1899 10:00AM
08/07/2023 | Alternative | Routine/Scheduled | 550-STS-6519 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | Dec 30 1899 12:45PM
02/20/2023 |  | Routine/Scheduled | 234-17-302 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | Jan 1 1900 12:45PM
10/13/2023 | Alternative | Routine/Scheduled | 093-02-0320 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | Dec 30 1899 7:30AM
12/13/2023 | Alternative | RoutineScheduled | 03-100-0606 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | ECOFLO |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | [] | [] | NA | [17 empty] | SLUDGE JUDGE SEPTIC TANK-4-5" FROM BOTTOM, 1" FROM TOP EVERYTHING WORKING AS IT SHOULD PEAT IN GOOD CONDITION | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | 01:50 PM
08/24/2023 | Alternative | RoutineScheduled | 043-05-0184 | Clarke | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lord Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [17 empty] | LPD septic system | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/01/2023 | 07:45 AM
07/06/2023 | Alternative | Follow-Up Component Maintenance | 175-14-0221 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Chemically treated and cleaned FAST unit per manufacturer protocol. Pump out tank by others. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
05/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/21/2023 | Alternative | Reportable Incident | 015-STS-336679 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation","Effluent Screens"] | ["Control Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | replaced control panel | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/09/2024 | 12:00 AM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/07/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-798 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
10/02/2023 | Alternative | Follow-Up | 128.02.042 | Essex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | replaced pump, system check - okay | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/02/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
09/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1200 |  |  | Pump | Gravity |  | Not Applicable | 600.000000 | ["None"] | ["None"] | NA |  |  | 7.800000 | 8.240000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | Dec 30 1899 2:20PM
10/04/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/04/2023 |  | RoutineScheduled | 2110-06-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | 6.900000 |  |  | 2.200000 |  | 03/06/2023 | Sample Chamber | 14.000000 |  |  | 24.000000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/18/2023 | 12:00 AM
11/04/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1000 | Septic | pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/20/2023 |  | RoutineScheduled | 003-STS-29925 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | E-Z Treat |  | Gravity | Pressure | Drip | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 12:00 AM
11/13/2023 | Alternative | RoutineScheduled | 107-17-0062 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
09/11/2023 | Alternative | Routine/Scheduled | 166-06-248 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [29 empty] | - Septic tank At normal level Has 1" of solids with 3" of sludge Pulled and cleaned filter - Pump tank At normal level Pump and floats working - Control Panel Visual and audible alarms working Discharge pump pulling 7.05amps - Distribution Box In good shape Has 8 lines all taking water properly - Drain field Showing no signs of surfacing or blowouts | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/03/2023 | 10:55 AM
06/28/2023 | Alternative | Routine/Scheduled | 151-07-0123 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Real Estate Inspection Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. BioFilter - 5 modules - peatmoss in good condition - raked / turned. Absorption Bed - no evidence of leaks - inspection chamber dry. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/29/2023 | 07:30 AM
03/07/2023 |  | RoutineScheduled | {FIPSCode}-STS-4677 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 2 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/07/2023 | 12:00 AM
07/07/2023 | Alternative | RoutineScheduled | 179-12-0203-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 0-3 | 0-3 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear |  |  | 5.000000 | [11 empty] | Inspected | discharge pipe dripping. will investigate further | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/07/2023 | 10:00 AM
01/16/2023 |  | Reportable Incident | 177-10-0281-SR | Spotsylvania | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Rebuilt failed compressor. | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | 12:00 AM
01/04/2023 |  | RoutineScheduled | 179-14-0303-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | As noted previously, the trees growing near the distribution box should be removed. The drainfield should be mowed and maintained in a mowed condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
05/03/2023 | Alternative | Reportable Incident | C 800-17-0369 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Property management called due to the light being on for 3 weeks and gurgling in the laundry room. Serviced system. Checked the panel and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Replaced the P-20 pump (new serial # 2204-137380), replaced the UV light bulb, and replaced the UV light cord. Meet with the pumping company and pumped and cleaned the Clearstream tank and pumped and cleaned the pump tank. There is visible wetness on the drainfield - most likely from rain - once it dries up need to keep an eye on it. The timer is set to 6 minutes every 2 hours. Disconnected the pressure switch on the aerator and cut the breaker off to the UV due to the pumping. Did not take samples due to the UV not working on arrival. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/03/2023 | Dec 30 1899 3:00PM
09/25/2023 | Alternative | Reportable Incident Component Maintenance | SWP-04-378 | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to inputs on recirc panel getting stuck on during a power surge. Corrected panel issues. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/01/2023 | 06:08 AM
02/28/2023 |  | RoutineScheduled | 177-11-0140-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/18/2023 | Alternative | RoutineScheduled | 06-197-168 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Eco Flo |  | Pump | Pressure | Drip | Not Applicable | 200.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation","Distribution Pump Operation"] | ["Attached Growth Medium","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation","Effluent Screens","Dispersal System Operation","Control Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/18/2023 | 12:00 AM
02/02/2023 | Alternative |  | 196-96-206 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
05/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/25/2023 | Alternative | RoutineScheduled | 061-STS-21663 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | UV |  | ["Disinfection","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["Disinfection","BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-8"sludge 12" scum/ Microfast-18"sludge 0"scum/ Pump Tank- 2"sludge 0"scum/ Pump out required on the Septic-Microfast Tank/ UV-Light bulb requires replacement and completed during inspection/ Controls, pump, floats and alarms functioning properly/ Counts: Pump- 2297 ETM-127h 59m/ Peak-0/ High-9 On-6m 26s Off-12h Dose 210 gal. / No breakout or spongy areas on the drip field. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/08/2023 | Alternative | RoutineScheduled | 023-STS-42917 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Western Virginia Water Authority | 1942001145 | Michael | Doss |  |  |  |  | Gravity | Pressure | Drip | Not Applicable |  | ["Other"] | ["Other"] | NA | None | Clear | [5 empty] | 06/08/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | Jan 1 1900 1:45PM
09/28/2023 | Alternative | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 540 | Multiflo FTB |  | Pump | Gravity | Trenches |  | 450.000000 | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | 02:17 PM
11/27/2023 | Alternative | Routine/Scheduled | 16-120-0243R | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | annual maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Due for pump out. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. -Aeration: Water level normal. Due for pump out. Refill is required for proper operation and to prevent damage to components -Air Pump/Blower: Checked and confirmed aerator is functioning properly. Flushed and cleaned aerator air intake filter -Control Panel: Checked and confirmed components within control panels are functioning properly. Checked and confirmed audible alarms are functioning properly. Checked and confirmed visual alarms are functioning properly -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | Dec 30 1899 1:03PM
05/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/22/2023 |  | Routine/Scheduled | 234-18-084 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | Jan 1 1900 1:55PM
03/28/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | 12:00 AM
04/17/2023 | Alternative |  | 101-07-0131 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Margurite | Murray | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/25/2023 | Alternative | Routine/Scheduled | 05-137-0189 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing tank - recommend pumpout - RSV, recirc pump, effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. Dbox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | Dec 30 1899 1:45PM
12/08/2023 | Alternative | Reportable Incident Component Maintenance | SD-13-058 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Blower was making howling/squealing noise from bearings going bad. Replaced blower with same make and model (Fuji 1/3 hp). New blower running at 3.30 amps (max is 3.60). Media shows no signs of clogging. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
07/20/2023 | Alternative | RoutineScheduled Component Maintenance | 175-05-0168 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/17/2023 |  | RoutineScheduled | 017-STS-333411 | Bath | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | Septic Tank Only | EZ-Treat | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was cleaned. The recirculating pump was pulled and cleaned. The pillow beads were sprayed off. The sprayers were spraying as designed. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/25/2023 | 05:35 PM
04/04/2023 |  | RoutineScheduled | 08-113-163 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/04/2023 | 12:00 AM
05/04/2023 | Alternative |  | 101-05-0018 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Damian | Metcalf | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/18/2023 | Alternative | Reportable Incident | 11-120-0365AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Upon arrival, I found the control panel was NOT in alarm condition and system in normal level. Checked and confirmed discharge pump and discharge floats are functioning properly. Checked and confirmed aerator is functioning properly. System had corrected itself. Noted that we had a lot of rain in the previous days but there has not been any rain related alarms in the past year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | Dec 30 1899 2:36PM
01/31/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim |  |  |  |  | Pump | Pressure | Drip | UV |  | ["SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [17 empty] | Septic/Atu needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/31/2023 | Dec 30 1899 3:55PM
03/29/2023 | Alternative | Reportable Incident | 153-STS-20345 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired UV unit & replaced UV buld. Replaced Step 20 pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
04/12/2023 |  | RoutineScheduled |  | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | alarm unplugged | This AOSS should now return to normal function after having provided the above state routine maintenance | 05/22/2023 | 11:15 AM
07/17/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | 12:00 AM
07/28/2023 | Alternative | RoutineScheduled |  | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/18/2023 | 12:00 AM
01/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
06/15/2023 | Alternative | RoutineScheduled Component Maintenance | SP-05-15 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Ecoflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | ["Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Roots in pod #4, added root destroyer. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
05/19/2023 | Alternative | RoutineScheduled | 047-18-124 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | routine inspection. Blower 2.87 amps. Tank needs pump out due to solids. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
04/08/2023 |  |  |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/09/2023 | 12:00 AM
04/12/2023 |  |  | 13-163-0041 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Norweco | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | 12:00 AM
12/22/2023 | Alternative | Routine/Scheduled | 05-160-0090 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/22/2023 | 10:30 AM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Effluent filter was clogged and caused the level to be high. Inlet side had a significant amount of grease. Recommend pumping | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/13/2023 | Alternative | RoutineScheduled | 04-160-0138 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 | 1000 | Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NO | [16 empty] | Inspected | Annual Inspection of Alternative Septic System This system is functioning but not as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Components are recommended to be repaired/upgraded. - recommend pumping/cleaning septic tank - inlet line is underwater and needs to be corrected, recommend pumping/cleaning tank to see if that will resolve issues - it was noted in last report that riser is buried and broke and recommended to bring to ground level, riser needs to be brought up to ground level for future maintenance services and broken piece replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 02/22/2023 | 12:00 AM
07/11/2023 | Alternative | RoutineScheduled | 061-15-470 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Mckim Septic and Pumping | 1942001330 | Michelle | McKim | 3.000000 |  |  |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/20/2023 | 07:30 AM
07/27/2023 | Alternative |  | 10-197-A1 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/27/2023 |  | 8.220000 |  |  | 6.400000 |  |  | Will be sent separately |  | BOD: 8.22 TSS: 6.40 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | 12:00 AM
02/24/2023 |  | RoutineScheduled | 175-12-0155 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 03/02/2023 | Sample Chamber | 56.000000 | [5 empty] | Attached to this report |  | Septic-5"sludge 2"scum/ Microfast-4"sludge 0"scum/ Pump Tank-3"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-8674 ETM-7908/ Zone1-3.5gpm CC-2881/ Zone2-3.5 CC-2891/ Zone3- 3.5 CC-2847 On-7.8m Off-1h 51m Watermeter-04173625/ No breakout or spongy areas on the drip area and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/09/2023 | Alternative | Routine/Scheduled | 151-14-0061 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 75.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 05:50 PM
12/01/2023 | Alternative | RoutineScheduled Component Maintenance | 177-06-0228-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
04/07/2023 |  | RoutineScheduled | 182-14-0021 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/08/2023 | 12:00 AM
02/28/2023 |  | RoutineScheduled | {FIPSCode}-STS-72966 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for rountine inspection. Home owner was using fabric softner went over do's and dont's with them. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
04/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/13/2023 | Alternative | Reportable Incident | 128-04-182 | Essex | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Arrived on site found system flooded. No power to pump. Called customer no answer. Text was sent, found a key and it would not unlock doors. Called customer again got no answer. Unplugged alarm so it doesn't keep going off. Need access to breaker panel to troubleshoot | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/14/2023 | 11:25 AM
05/12/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Mr earney went out to evaluate the septic system drain field and it was determine that it has failed. Home owner does not want to fix. Had sewage on the ground on friday when we backfilled d-box per owners request. Septic tank is in sunroom. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/17/2023 | 12:02 PM
05/15/2023 | Alternative | Routine/Scheduled | 093-12-0091 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | Dec 30 1899 11:37AM
12/18/2023 | Alternative |  | 13-184-5003 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/18/2023 |  | 14.300000 |  |  | 4.130000 |  |  | Will be sent separately |  | BOD: 14.3 TSS: 4.13 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 12:00 AM
07/28/2023 | Alternative | Reportable Incident | 05-163-0276 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Parsley Septic Tank , Inc. | 1942001106 | James | Parsley | 1.000000 | 1500 | Adavantex |  | Pump | Gravity | Trenches | Not Applicable |  | ["Other"] | ["Other"] | YES | [16 empty] | Pumped Out | Line from recirculating pump to Advantex broken. Repair broken pipe and cleaned filters. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/28/2023 | 12:00 AM
03/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
08/25/2023 | Alternative | Routine/Scheduled |  | Frederick | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Pressure | Drip |  | 450.000000 | ["Attached Growth Medium","Dispersal System Operation","Effluent Screens","Septic Tank Baffles"] | Effluent Screens | YES | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/28/2023 | 02:07 PM
10/18/2023 | Alternative | Routine/Scheduled | 07-160-0291 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable | 149.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | 02:00 PM
02/17/2023 | Alternative | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Pressure | Drip |  |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | YES | [17 empty] | Service call only: Alarm- Found trash in the drip filter valve #1. Cleaned & hydraulic unit now functioning properly. Recommend new septic tank filter. Returned on 2/20/2022 and installed new Zoeller-5000 filter | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/10/2023 |  | RoutineScheduled | 132-05-0151 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/12/2023 | 12:00 AM
05/10/2023 |  | Routine/Scheduled | 06-118-0094 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | NO | [17 empty] | System checked. System appears to be operating normally. Septic tank will need to be pumped out and refilled in the next 6 months. Drainfield needs to be maintained as mowed area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | Jan 1 1900 9:05AM
04/19/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/22/2023 | 11:15 AM
05/12/2023 | Alternative | Reportable Incident Component Maintenance | 175-15-0234 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Level Sensor Operation"] | ["BlowerCompressorAerator Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed EcoPod compressor & 4 control floats. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
07/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | [7 empty] | 07/21/2023 |  | 87.000000 | [5 empty] | Will be sent separately | Inspected | Repaired blower and blower panel Pump Supply line repaired | This AOSS should now return to normal function after having provided the above state routine maintenance | 08/23/2023 | 06:57 AM
06/14/2023 |  | RoutineScheduled | 2008-143-0149 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 5.000000 |  | Puraflo |  | Pump | Gravity | Mound |  |  | [] | ["Attached Growth Medium","Control Operation","Level Sensor Operation","Distribution Pump Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | 12:00 AM
01/13/2023 |  | Routine/Scheduled | 2015-143-0171 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump tank - float sensors, pump and controls operating. DBox - atgrade - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | 12:30 PM
08/30/2023 | Alternative | RoutineScheduled | 031-STS-28188 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Norweco |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Initial Visit in recently installed system - Good aeration in treatment tank. Pump runs good. Pump float is good and alarm float test good. Goulds effluent pump installed 220v | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | 09:30 PM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/05/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  | Microfast Trench |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 12:00 AM
06/15/2023 | Alternative | RoutineScheduled Component Maintenance | 175-05-0965 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/07/2023 | 06:25 AM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance | 177-09-0048-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | There are ants in the Puraflo module. We recommend treating the area around the modules for ants. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/07/2023 | 08:37 AM
04/12/2023 |  | RoutineScheduled | 177-06-0555-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Annual inspection. Good aeration pattern observed in atu, and effluent level is only about an inch above the media but treatment quality is poor. Suspect some household product contains quats. Had discussion with owner to try to identify those products. Inadequately treated effluent could eventually lead to problems in the mini-mound. Replaced cleanout for the last inspection port in the mound (furthest from the tanks). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
03/21/2023 |  | Initial Visit | VAG408238 | Rockingham | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Puraflo |  |  |  | Discharge | Chlorination |  | ["SludgeScum Accumulation","Attached Growth Medium"] | ["SludgeScum Accumulation","Attached Growth Medium"] | [17 empty] | Pumped Out | return for labs now that socks have been replaced. Septic pumped | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 04/05/2023 | 12:00 AM
01/06/2023 |  | Reportable Incident | 057-STS-94186 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 2000 | None | None | Pump | Pressure | Mound | Not Applicable | 450.000000 | Control Operation | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - STE - GeoMat Replaced leaking access riser Repalced controls with new 2 breaker control panel | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 10:00 AM
10/02/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20377 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
02/06/2023 |  | Routine/Scheduled | 234-15-305 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | Replaced UV ballast and UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | Jan 1 1900 12:15PM
07/26/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-92606 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
04/19/2023 |  | Routine/Scheduled | 041-STS-259656 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/19/2023 | Jan 1 1900 4:27PM
03/20/2023 |  | RoutineScheduled | 175-14-0399 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | EZ-Treat Recirculation Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NO | [17 empty] | Septic Tank-4"sludge 1"scum/ Recirc. Tank-2"sludge 0"scum- 2"sludge 0"scum/ No pump out needed at this time/ Pump intake cleaned/ Controls, pump, floats and alarms functioning properly/ Control box does not have any counts or ETM readings/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/17/2023 | Alternative | Reportable Incident | 154-04-0829 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | On site for several alarms over the weekend. House is a rental but only had 4 people at time of alarms. Electronic log in control panel confirmed they were high level alarms (as opposed to low level or other type of alert). Log showed that there were more high level alarms recorded in April. Owners said all toilets appeared to be adjusted and working properly. Next most likely cause of alarms would be groundwater infiltration. No active leaks seen today and tank was at normal level. Need to go when ground is wet if future alarms occur during or after rain. Advised owner that septic occupancy permit was limited to 8 people (or less, need to see plans). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
09/18/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-90399 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
04/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/13/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1875 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/03/2023 |  |  | 10-192-200 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/03/2023 |  | 3.030000 | [5 empty] | Will be sent separately |  | BOD: 3.03 TSS: BDL E.Coli: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2023 | 12:00 AM
04/21/2023 | Alternative | RoutineScheduled | SD-05-16 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/23/2023 | 12:00 AM
01/18/2023 |  | Routine/Scheduled | 550-STS-6328 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | Jan 1 1900 12:55PM
12/08/2023 | Alternative | RoutineScheduled Component Maintenance | 179-15-0247-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment looks way better than last year; media is visual, and it should get better as the antibiotics get deluded. Blower bearings a little noisy but 3.05 amps will replace when it stop working. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
08/08/2023 | Alternative | Routine/Scheduled | 093-14-0150 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | Dec 30 1899 12:04PM
01/12/2023 | Alternative | Reportable Incident | 073-STS-105217 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | Effluent Screens | YES | [16 empty] | Pumped Out | COSS - Maintenance - GMP2018-02 Installed access riser on primary septic tank. Installed cannister effluent screen in outlet of septic tank | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/16/2023 | 07:30 AM
10/27/2023 | Alternative | Routine/Scheduled | 157-14-0054 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the buzzer. The Clearstream tank needs to be pumped out as well as the septic tank. The timer is set to 3 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/27/2023 | 12:15 PM
03/18/2023 |  | RoutineScheduled | 133 05 1172 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 13" of accumulated solids in septic tank. Flushed treatment unit spray manifold. Cleaned recirculation pump basket filter. The passive charcoal air vent needs to be replaced. Tested floats, pump and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/09/2023 | 07:03 PM
03/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/13/2023 | Alternative | Reportable Incident Component Maintenance | {FIPSCode}-STS-74430 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alrm due to running toliets in the house. Outstanding proposal to be sent again. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
09/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | McKim Septic and pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Peat fiber needs replaced very broken down and sample came back bad | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/23/2023 | Dec 30 1899 3:10PM
09/13/2023 | Alternative | RoutineScheduled | 107-04-0549 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [15 empty] | fixed crack in blower line | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
10/30/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-21755 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.000000 | 7.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
05/23/2023 |  | Routine/Scheduled |  | Cumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Piedmont | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Bionest |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Inspected |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/23/2023 | Jan 1 1900 4:17PM
06/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/27/2023 | Alternative | Reportable Incident Component Maintenance | SD-14-243 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed N98 effluent pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
11/24/2023 | Alternative | Reportable Incident | 136-15-0333 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Found relay to be bad causing the pump to run constantly. Replaced relay for no charge. Customer wants an electrician to come out and see if they can put a current sensor on the Septic Breaker in the electrical panel that will notify her if the breaker trips | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 09:43 AM
03/14/2023 | Alternative | Routine/Scheduled | 17-190-015 | Surry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The septic tank needs additional risers on it to be properly inspected in the future. The timer is set to 2 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | Dec 30 1899 9:00AM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
06/07/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation","BlowerCompressorAerator Operation"] | ["Level Sensor Operation","BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-6"sludge 4"scum/ Microfast-6"sludge 0"scum/ Pump Tank-0"sludge/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ Replaced faulty redundant off float/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-1143 ETM-43h 20m/ Pump2-1113 ETM-42h 24m On-2m 18s Off-10h/ Peak-23/ High-18 / No breakout or spongy areas on the drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/15/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/12/2023 | Alternative | RoutineScheduled | SD-10-100 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1500 | BEST 1 | Sand filter | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | YES | Musty | Clear | [5 empty] | 03/12/2023 | Sample Chamber | 2.000000 |  |  | 2.500000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/20/2023 | 04:10 PM
02/20/2023 | Alternative |  | 128-18-0083 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Aquasafe |  | Gravity | Gravity | Pad | Not Applicable |  | ["None"] | ["None"] | [18 empty] | This system is not operational no power trailers have been removed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/01/2023 | 12:00 AM
03/08/2023 |  | Initial Visit |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  |  | Drip |  |  | ["Attached Growth Medium","Auxiliary Filter","Septic Tank Baffles"] | ["Attached Growth Medium","Auxiliary Filter"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/08/2023 | 12:00 AM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance | 177-16-0107-SP | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity |  | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection" ,"Effluent Screens" ,"Attached Growth Medium"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected | As noted previously, the Salcor UV unit is not working. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/03/2023 | 05:43 AM
05/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Sand filter zone is not functioning as designed. Emitters not functioning as designed. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
10/24/2023 | Alternative | RoutineScheduled Component Maintenance | 182-00-0229 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 10/24/2023 |  | 4.000000 | [5 empty] | Will be sent separately | Inspected | Replaced timer and base due to corrosion Recommend raising panel and replacing to help with constant issues Lab sample normal | This AOSS should now return to normal function after having provided the above state routine maintenance | 11/22/2023 | 09:18 AM
05/20/2023 | Alternative | Routine/Scheduled | 095-STS-6780 | Williamsburg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/20/2023 | Dec 30 1899 10:30AM
08/01/2023 | Alternative | RoutineScheduled | 154-06-0051 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2500 | Microfast |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [14 empty] | Pumped Out | Septic and Treatment Unit Pumped Effluent Pump Removed, screen unclogged and cleaned Drip Field Flushed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/01/2023 | 12:00 PM
09/07/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-5149 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | Dec 30 1899 12:25PM
07/19/2023 | Alternative | Initial Visit | 11-120-0020A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit Trash Tank - normal level - recommend pumpout. Aeration Tank - normal level - mixing present - aspirator serviced. Clarifier - normal level - effluent screen serviced. Pump Tank - float sensors, pump operating - control panel set for DEMAND dosing - Drip field requires TIMED Dosing - adjustments made. Drip Field - headworks serviced. diskfilter heavily clogged. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | Dec 30 1899 7:30AM
05/03/2023 |  | Routine/Scheduled | 234-02-6816 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Puraflo |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/03/2023 | Jan 1 1900 9:30AM
11/03/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Upon arrival, I found the UV control panel in alarm condition. Checked and found the UV bulb and power lead for UV bulb had failed. Homeowner gave approval for repair. Repaired power lead and UV bulb while on site. Checked and confirmed UV was functioning properly before departure | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | Dec 30 1899 9:33AM
05/15/2023 | Alternative | Routine/Scheduled | S15-180-0124 | Roanoke City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Aqua Klear |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | Jan 1 1900 4:30PM
06/23/2023 | Alternative | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Norweco Singulair ATU |  | Gravity | Gravity | Trenches |  | 450.000000 | ["BlowerCompressorAerator Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/27/2023 | 10:48 AM
03/29/2023 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Aquarobic Mini Plant |  | Pump | Pressure | Mound |  | 450.000000 | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | 12:27 PM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | Delta Environmental Products, DF Series | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | One air release valve is not functioning properly. Corrections in progress. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/15/2023 | Alternative | RoutineScheduled | 107-03-0424 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
07/13/2023 | Alternative | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [6 empty] | Dispersal System Operation | Dispersal System Operation | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/27/2023 | 12:28 PM
06/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 06/29/2023 |  | 26.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
09/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
10/10/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Mound | UV |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 10/10/2023 | Sample Chamber | 2.000000 |  | 13.000000 |  |  |  | Attached to this report |  | Septic Tank-0"sludge 0"scum/ Microfast-0"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pump/ floats and alarms are functioning properly/ Counts: Pump1 -count=9 ETM=20m/ Pump2-count=5 ETM=5m/ Peak count=11/ High count=5/ On=3m 31s Off=6h Peak Off=4h 48m/ No breakout or spongy areas on the mound area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/25/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
04/24/2023 |  | RoutineScheduled | 133 17 0196 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | Septic zone under1" scum 6" sludge- Recirc zone minimal scum and 6" sludge, Discharge Tank 3-4" sludge - Cleaned Biofilter, Flushed and Brushed spray manifold- Cleaned RSV, Flushed System, Ran in test mode. Tested Floats and alarm. Pump good, Recirc pump run time 1496.3hours 58530 cycles and discharge pump 177.2 hours and 3361cycles, start date 1-31-2017, 2304 days in memory, | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
07/11/2023 | Alternative | Reportable Incident Component Maintenance | 179-07-0181-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | High level alarm, effluent just into the riser in pump tank. Alarm largely due to a slow drip rate. Both control levers for the solenoid valves were found in the manually "on" position. Spin filter was very dirty and crushed. Closed levers, installed new filter and ran test cycle. Cleaned debris from under the filter flush valve diaphragm (twice). Drip rate was very low. Cleaned pump intake and tested again. Drip rate measured at 35% of design. Drip tubing emitters are most likely clogged (from improper and infrequent maintenance). A bleach flush is recommended to attempt to restore the drip rate. If unsuccessful, the drip tubing will have to be replaced. Advised owner to have the pump tank emptied to get rid of the sludge and speed up recovery time from the high level condition. Grass roots growing in around inlet (wedge) lid on septic tank, needs a plastic riser and lid to grade. Tanks may have other points of infiltration. Need to inspect when effluent levels are back to normal. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/18/2023 | 11:45 AM
11/20/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | Dec 30 1899 2:30PM
02/03/2023 |  | Routine/Scheduled | 04-120-0198A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - Media drapes sagging / ponding Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | Jan 1 1900 12:00PM
07/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1000 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/25/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | Dec 30 1899 9:30AM
10/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced 2 pressure gauges New owner please contact us as this is required annually for VDH | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/03/2023 | Alternative | Reportable Incident Component Maintenance | 177-STS-90024 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to 2 toliets out of adjustment and did rountine inspection. Also adjusted high level float to give homeowner more storage between cycles. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 04:50 AM
01/09/2023 | Alternative | Reportable Incident | 136-10-0094 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Changed the diffuser in the Clearstream and changed the filter in the aerator. Pumped out and cleaned the Clearstream tank and pumped and cleaned out the pump tank. Disconnected the pressure switch on the aerator due to the pumping. The septic tank needs a 6" or 12" riser. The timer is set to 6 minutes every 1 hour. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/09/2023 | 02:00 PM
12/27/2023 | Alternative | RoutineScheduled | 06-177-1208 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | 2.000000 | 1000 | ECOFLO |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | YES | Septic | Cloudy | [5 empty] | 12/27/2023 | [7 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 12:00 AM
05/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/29/2023 | Alternative | RoutineScheduled Component Maintenance | {FIPSCode}-STS-81773 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The squirt height coming from the Advantex recirculation pump is low. This is an indication that the system is not getting full treatment. The rods that hold the Advantex textile media sheets are beginning to fray. One has broken. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
07/18/2023 | Alternative | Routine/Scheduled | 157-09-0212 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the filter in the septic tank (was stopped up). Changed the diffuser in the Clearstream and changed the filter in the aerator. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/18/2023 | 08:00 AM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/05/2023 |  | RoutineScheduled | 099-STS-87978 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 1-3 0-0 | 0-0 | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | None | Clear |  |  | 3.000000 | [11 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/05/2023 | 10:00 AM
11/07/2023 | Alternative | RoutineScheduled Component Maintenance | 099-STS-89498 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. 2 bottom floats (on and off) were stock close, replaced and added water to pump tank. Check valve for zone 1 was taking long to shut, took it apart and cleaned. Treatment crystal clear. HL-10, ETM-0M. PEAK-14, ETM-1H17M. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
03/09/2023 |  | RoutineScheduled | 107-10-0017 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The blower and spin filters were both cleaned. The controls were operating as designed. There were no visible leaks in the drip field. The drip field was operating as designed. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | 10:20 AM
10/17/2023 | Alternative | RoutineScheduled Component Maintenance | 182-01-0072 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 10/17/2023 |  | 2.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample normal Repaired timer Replaced buzzer and float | This AOSS should now return to normal function after having provided the above state routine maintenance | 11/22/2023 | 09:18 AM
12/19/2023 | Alternative |  | 17-197-023 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/19/2023 |  | 3.790000 |  |  | 2.100000 |  |  | Will be sent separately |  | BOD: 3.79 TSS: 2.10 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | 12:00 AM
02/06/2023 |  | Reportable Incident | 095-STS-6270 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | COSS - Maintenance - GMP2018-02 Repalced deteriorated DBox with new 8 port concrete DBox. Spliced to existing conveyance line. Spliced to existing header lines. 5 laterals pressure washed - all laterals accepting effluent. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/07/2023 | Jan 1 1900 7:00AM
07/03/2023 | Alternative |  | SP-04-519 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
08/31/2023 | Alternative | Routine/Scheduled |  | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Supervised pumpout of processing tank by Commonwealth Waste Solutions. Refilled processing tank with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | 11:00 AM
08/12/2023 | Alternative | Reportable Incident |  | Middlesex | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Fuji |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | Gas company trenched gas line through absorption field - needs full evaluation as to damage and if can be repaired - effluent surfaces when pump is activated ... Damage to absorption field NOT seen during previous routine pump out. - Client agreed to being put on temporary pump and haul . | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/17/2023 | 06:00 AM
09/09/2023 | Alternative | RoutineScheduled | SD-00-695 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2000 | Septic | Whitewater | Gravity | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | 12:20 PM
05/24/2023 | Alternative | RoutineScheduled | 154-06-0835 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco | Sand Tank | Gravity | Pressure | Discharge | Chlorination | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/28/2023 | 12:00 AM
12/22/2023 | Alternative |  |  | Buckingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Piedmont |  |  | Eric | Wilkening | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/01/2023 |  | Routine/Scheduled | 06-120-0556A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/01/2023 | Jan 1 1900 9:25AM
06/05/2023 | Alternative | RoutineScheduled Component Maintenance | {FIPSCode}-STS-65461 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Roots in monster box, removed and added rootx. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
08/29/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-5382 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/29/2023 | Dec 30 1899 12:55PM
09/09/2023 | Alternative | RoutineScheduled | 2108-09-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.500000 |  |  | 1.600000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/11/2023 | 12:00 AM
12/20/2023 | Alternative | Reportable Incident | 166-09-331 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | flushed sewer, pumped out tank to clean inlet T | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
07/24/2023 | Alternative | RoutineScheduled | 06-142-0020 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/15/2023 | Alternative | Routine/Scheduled |  | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Hoot |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - sensor probe operating - pump and controls operating. Drip Field - 2 Zone - solenoids serviced - disk filter sserviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | Dec 30 1899 7:00AM
04/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The fuji tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20452 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
08/23/2023 | Alternative |  | 101-16-0498 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Christian & Rebecca | Hall | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/12/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/22/2023 | Alternative | RoutineScheduled | 003-STS-32495 | Albemarle | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Blue Ridge | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [9 empty] | [] | [] | [8 empty] | 05/22/2023 |  | 30.000000 |  |  | 46.400000 | 124.910000 |  |  |  | Engineer is still making adjustments to the system. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/14/2023 | 11:00 AM
01/18/2023 |  | Follow-Up | SWP-05-499 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pods 4 and 5 (furthest from the street) had ponding water, draining extremely slow. Moved peat over to access the 1" drain ports in bottom of pods and flushed with pressure washer. Poured 5 gallon buckets of water into pods, still very slow drainage. Dug up 2" common drain line, cut off the end cap and flushed that line while watching for flow into the sample box. Eventually got pretty good flow. Ran fiber optic camera down the 2" line and observed standing water about 4' prior to the sample box. Uncovered 2" drain line at that point and corrected a sag in the piping. The beginning of the 2" line has negative fall but could not be readily corrected because raising it would have put negative fall on the 1" drain line from the closest pod (#5). Second run with camera revealed no standing water and no other obvious problems such as separated pipe joints. All pods are draining now. Added a 2" pvc sweep and stand pipe at beginning of the 2" common drain line to facilitate future flushing and camera inspections. Assisted owner with installing a new pressure treated board for the control panel. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
12/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 02:30 PM
06/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1000 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/29/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | Jan 1 1900 7:20PM
03/29/2023 |  | Routine/Scheduled | 234-03-10703 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | Jan 1 1900 9:50AM
02/02/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:08 PM
02/06/2023 |  |  | 00-142-0688 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Puraflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Pumped Out | Install a new contactor in the Orenco control panel | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/08/2023 | 12:00 AM
05/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
11/28/2023 | Alternative | RoutineScheduled | 153-STS-20168 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank to Puraflo Modules | Pump | Gravity | Discharge | Chlorination |  | ["Attached Growth Medium","Other","Level Sensor Operation"] | [] | YES |  |  | 7.100000 |  |  |  | Ecoli 205 MPN/100mL | 11/28/2023 | Sample Chamber | 2.000000 |  | 130.000000 | 2.000000 |  |  | Attached to this report |  | Septic Tank-3"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Counts: Pump-038949 ETM-0117015/ All peat modules are bad, no fiber texture requires replacement/ Sample box riser broken, need top 12" extension and lid/ Septic tank riser is leaking and needs to be resealed (12"deep) Only the off and enable float and interior alarm is working and wired up/ Wire needs to be pulled wire for the exterior alarm/ Need 2" coupling for the Puraflo drain line/ Replaced the Off Float. Need Chlorine tablets/ Owner stated he is looking into a different treatment system instead of Puraflo Modules. | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
08/09/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
06/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Blue Ridge | SES Mid Atlantic, LLC | 1942001236 | Stuart | Lynn |  | 12600 | Whitewater ATU | Whitewater ATU | Gravity | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Disinfection" ,"BlowerCompressorAerator Operation"] | ["Disinfection" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation"] | NA | None | Clear | [5 empty] | 06/14/2023 | Pump Chamber | 8.000000 |  |  | 5.000000 | 45.000000 |  | Will be sent separately | Inspected | Q2 2023 Report 3-23-23 read water meters 3-24-23 Routine service rrothgeb - Robert Rothgeb - Mar 24, 2023 10:36 AM WWTP Secure and gates locked on arrival: Yes Unusual odors around plant: No Blowers working if present: Yes Any component in Alarm?: Yes - 3. Re-circ Pumps #1,#3, and #4. Pump Station Locked if present: Not Applicable Test telemetry system raise all floats for notice for office: Telemetry Not working Drive through community look for alarms and overflows: No alarms identified Community alarms or overflow detail: NA - 0 Completed Data Sheet: No 4-2-23 81 Mannie Court repair floats 55 Mannie court, needs pumping, 96 Mannie court needs pumping 4-323 Blowers - all are operational blower 4 is turned off per frank since it?s not needed Carbon drums - full and operational minimal smell at plant if standing at tanks but nothing from outside fence. Recirc pumps - 1, 3, 4 are not operational and are at office. Generator - DANGEROUS ?? Needs CAT Service A/C unit - operational emptied tray while on-site 5-9-2023 & 6-6-23 Advantage pump multiple STEP tanks 5-19-23 rrothgeb - Robert Rothgeb - May 19, 2023 7:38 PM Change air filters. Pump grease. WWTP Secure / Locked: Yes Unusual Odors?: No Alarms upon arrival?: No Blowers and ECOPODS all functioning: Yes Drianfield walkover: Yes - Okay 6-6-2023 Pump sludge from recirc tanks at WWTP 7200 gallons 6-14-23 rrothgeb - Robert Rothgeb - Jun 13, 2023 7:36 AM 7:22 AM at Oxford Hills. Influent Sampling Location: Other. INF Tank discharge. Effluent Sampling Location: Designated sampling point. Dosing Tank discharge. 9:35 AM from Oxford Hills. Samples Delivered to: Joiner Micro Labs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | 01:58 PM
07/17/2023 | Alternative | Reportable Incident | 159-12-104 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 4000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 1000.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Reported clog / back-up into restaurant. Pumped 1000g from primary septic tank - jetted sewer line, cleared clog. Flow Equal tank operating Aeration tank - mixing present. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/18/2023 | 06:45 AM
09/15/2023 | Alternative | Routine/Scheduled | 087-STS-6255 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Discharge | UV |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/15/2023 | 08:59 AM
05/17/2023 |  | RoutineScheduled | 175-15-0447 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
01/23/2023 |  | Routine/Scheduled | 08-120-0508A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Hoot |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/23/2023 | Jan 1 1900 3:48PM
11/27/2023 | Alternative | Initial Visit | 115-STS-92848 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm - float wires were wrapped around floats - re-secured them. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream (diffuser was stopped up with paint) and changed the filter in the aerator. The UV tube needs to be replaced - too stained. The timer is set to 3.5 minutes every 1.5 hours. Tank should be pumped and cleaned due to paint being in it. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/27/2023 | 10:45 AM
07/21/2023 | Alternative | Initial Visit | 165-STS-337453 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 2.000000 |  | Advantex AX20 |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | 05:30 PM
11/18/2023 | Alternative | RoutineScheduled | SD-02-499 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2000 | septic | LPD | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | YES | Musty | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/19/2023 | 08:40 AM
01/23/2023 | Alternative | Routine/Scheduled | 166-08-0180 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2023 | 07:13 PM
07/13/2023 | Alternative | RoutineScheduled | 150-07-055 | King William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 3.000000 | 2900 gallons | septic tank | Clearstream | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear |  |  | 15.000000 | [12 empty] | Septic tank 4" fog, 10" sludge. Clearstream 15% SS. Aerator replaced. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/25/2023 | 10:45 PM
06/03/2023 | Alternative | Routine/Scheduled | 041-STS-261058 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/03/2023 | Dec 30 1899 12:00PM
05/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | pump tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
09/19/2023 | Alternative | RoutineScheduled | 196-05-844 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | checked peat, cleaned filters | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/15/2023 |  | RoutineScheduled | 175-06-0525 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Blower had gotten noisy, typical of bearings beginning to fail. Replaced blower and cleaned the air filter. New blower running at 3.65 amps (4.9 amps maximum). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
05/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
06/27/2023 | Alternative | Routine/Scheduled | 09-120-0158A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Bionest |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Needs trash and treatment tanks pumped | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/27/2023 | Dec 30 1899 10:56AM
06/24/2023 |  | RoutineScheduled |  | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | trash/septic | Microfast | Gravity | Pressure | Drip | Not Applicable |  | [] | [] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/29/2023 | 08:40 AM
03/16/2023 | Alternative | Routine/Scheduled | 06-174-0180 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/16/2023 | Dec 30 1899 1:57PM
03/24/2023 |  | Routine/Scheduled | 550-STS-6463 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/24/2023 | Jan 1 1900 1:00PM
11/14/2023 | Alternative | RoutineScheduled Component Maintenance | 079-STS-32734 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [7 empty] | 11/14/2023 |  | 200.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample came back deficient. Would possible recommend replacing media and pumping tank to help with this | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
10/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
08/11/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 | 1000 | 1000 | Pump | Pressure | Drip | Not Applicable |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | 12:00 AM
06/07/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
05/27/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 16" of accumulated solids in septic tank. Cleaned septic tank solids filter. 2" of solids in recirculation portion of treatment unit. 2" of solids in discharge portion of treatment unit. Tested floats, pump and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 07:03 PM
05/30/2023 | Alternative | RoutineScheduled | SD-07-172 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 65.600000 | ["SludgeScum Accumulation","Effluent Screens"] | ["SludgeScum Accumulation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 03:00 PM
12/08/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | DeHaven's Backhoe Service Inc. | 1942001541 | Wayne | Edmonson | 1.000000 | 1500 | Advantex |  | Pump | Gravity | Trenches | Not Applicable | 225.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 10:00 PM
07/19/2023 | Alternative | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 |  |  | Pump | Pressure | Trenches |  | 600.000000 | None | None | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/21/2023 | 11:09 AM
11/01/2023 | Alternative |  | SWP-04-216 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was in the off position and not running. That was resolved at the time of inspection. Lower Distribution box orange blank is broken and had roots coming in. Recommend replacing pump tank lid. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
10/09/2023 | Alternative | RoutineScheduled | 07-125-176 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/06/2023 | Alternative | Reportable Incident | 07-137-0092 | Goochland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | All In Septic Services | 1942001442 | Dennis | Mitchell | 3.000000 | 4000 | Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Auxiliary Filter","Recirculation Pump","SludgeScum Accumulation","Septic Tank Baffles"] | NA | Septic | Cloudy | [14 empty] | Pumped Out | Septic Tank and Treatment Tank Pumped Outlet T Missing - Replaced Recirculation Pump Replace Recircultion Filter Cleaned | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/06/2023 | Dec 30 1899 2:00PM
11/15/2023 | Alternative | RoutineScheduled | 169-STS-26550 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 5.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
03/01/2023 |  | RoutineScheduled | 17-163-0027 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Aqua Klear |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","Dispersal System Operation","Control Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/01/2023 | 12:00 AM
03/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
11/20/2023 | Alternative | RoutineScheduled Component Maintenance | 015-STS-337277 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
08/15/2023 | Alternative | RoutineScheduled | 06-198-066 | Wythe | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Advantex |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","Distribution Pump Operation","Recirculation Pump","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Distribution Pump Operation","Recirculation Pump","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 12:00 AM
06/07/2023 | Alternative | Reportable Incident | 151-14-0122 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | N/A | [17 empty] | System alarming - Septic tank - normal level Aeration Tank - compressor diaphragm failure - repaired on property. Discharge tank - float sensors, pump and controls operating. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/19/2023 | 10:30 AM
10/19/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/19/2023 | Dec 30 1899 9:40AM
09/29/2023 | Alternative | Routine/Scheduled | 10-120-0295A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Inlet appears to be intact. Outlet tee appears to be intact. Not due for pump out -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly -Aeration: Water level normal. Flushed and cleaned effluent screen. Not due for pump out. -Air Pump/Blower: Checked and confirmed aerator is functioning properly. Removed debris from aspirator shaft. -Control Panel: Checked and confirmed components within control panels are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Distribution Box: Water level normal. Found no signs of standing water inside dispersal lines. Structural integrity of distribution box appears to be intact. -Drain Field: Noted surfacing at lower corner of dispersal field. Had hurricane the weekend before with sporadic rain throughout the week. Field is dry during dry weather | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | Dec 30 1899 10:51AM
08/25/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-90363 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
06/20/2023 | Alternative |  | 03-125-082 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 06/20/2023 | [7 empty] | Will be sent separately |  | BOD: BDL TSS: BDL | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/20/2023 | 12:00 AM
04/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was in the off position and not running. That was resolved at the time of inspection. Lower Distribution box orange blank is broken and had roots coming in. Recommend replacing pump tank lid. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
07/19/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Clearstream | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
08/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/15/2023 | Alternative | RoutineScheduled | 09-177-1091 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Eco Pure |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 12:00 AM
04/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [5 empty] | 04/20/2023 |  | 16.000000 | [5 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
10/04/2023 | Alternative | RoutineScheduled Component Maintenance | 175-10-0412 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter"] | ["Effluent Screens" ,"Auxiliary Filter"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | 180 Inspection with Sampling | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
07/26/2023 | Alternative |  | 12-160-0071 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | 2.000000 | 2000 | Eco Pod | [6 empty] | [] | ["Dispersal System Operation","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | [8 empty] | 07/26/2023 | Sample Tap | [6 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 12:00 AM
05/08/2023 |  | Reportable Incident | 234-12-128 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/08/2023 | Jan 1 1900 8:00AM
03/22/2023 | Alternative | Initial Visit | 136-01-331 | Gloucester | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | AOSS - Initial Visit - ALARM - Primary septic tank - overfull - effluent screen clogged - pumped out, effluent screen serviced. Aeration Tank - no mixing - compressor failed - control panel failed. Pump Tank - power to controls - pump failed - DBox - not located - need FOIA. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/23/2023 | 08:15 AM
04/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/19/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [18 empty] | No return from dripfield. Minimal pressure at gauge in valve box. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/18/2023 | 12:00 AM
07/21/2023 | Alternative | RoutineScheduled Component Maintenance | 154-01-0052 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Quarterly Inspection. Pump Station #3 - We recommend jetting lines due to clogging. Pump Station #5 - We recommend jetting lines due to clogging. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
02/21/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Pump 1 is bad and needs replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/13/2023 | Dec 30 1899 11:23AM
03/28/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
01/16/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
10/12/2023 | Alternative | RoutineScheduled | 09-160-0247 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | King's Alternative Septic | 1942001094 | David | King | 1.000000 | 1000 | Biomicrobics 0.5 Microfast |  | Gravity | Gravity | Pad | UV | 50.000000 | ["None"] | ["None"] | NA | [17 empty] | System is working correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/07/2023 | 12:00 AM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/31/2023 | Alternative | Reportable Incident Component Maintenance | 179-17-0275-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to failed override float in recirc tank. Replaced float. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
06/30/2023 | Alternative | RoutineScheduled | 136-90-0138 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Virginia Septic Solutions LLC | 1942001500 | Justin | Barker | 2.000000 |  | Conventional Septic Tank and Pump Chamber |  | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | None | Clear | [15 empty] | Conventional Septic System pumps to Lateral Groundwater Movement Interceptor drainfield. Field is located in a clearing in the woods. Light vegetation (Ferns mostly) found growing in the area. Walked the clearing and did not see signs of settling of ponding that would indicate drainfield issues. Septic tanks were pumped last year by Jerry's Septic Service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | 12:00 AM
08/16/2023 | Alternative | Follow-Up | 175-03-0881 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon |  |  |  |  | Pump | Pressure | Drip |  |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [18 empty] | Follow up service call only: Replaced 1" check valves for zones 1 & 2 Watermeter reading-1,143,246.5 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
09/12/2023 | Alternative | RoutineScheduled | 128-08-014 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | replaced uv ballast, bulb. checked sludge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/21/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Multiflo FTB | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
07/03/2023 | Alternative | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 |  | 1000 |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | 12:00 AM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance | -STS-20246 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"SludgeScum Accumulation"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/11/2023 | 11:24 AM
06/23/2023 | Alternative | RoutineScheduled | 163-STS-335681 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | AdvantexAX20RT | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The textile sheets were sprayed off. The recirculating and discharge pumps were both pulled and cleaned. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | 08:50 PM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/08/2023 | Alternative |  | 06-120-0622A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 3000 | 1250 | 1000 | Pump | Pressure | Mound | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Level Sensor Operation"] | YES | Pungent | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 12:00 AM
04/13/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 12:00 AM
06/09/2023 | Alternative | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Gravity | Gravity | Trenches |  | 450.000000 | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/16/2023 | 10:18 AM
11/30/2023 | Alternative | RoutineScheduled | 110-Discharge-6299 Wilderness Rd. | Bland | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 4 Chlorine 12 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/30/2023 | 12:00 AM
05/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/27/2023 | Alternative | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Aquarobic Mini Plant | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | 01:05 PM
11/07/2023 | Alternative | Routine/Scheduled | 041-STS-259836 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 750 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/07/2023 | Dec 30 1899 11:00AM
03/10/2023 |  | Routine/Scheduled | 14-172-0441A | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Delta Environmental Products, UC Series |  | Pump | Gravity | Trenches | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. UV - Salcor unit shows electrical singing - requires replacing. - ordered Norweco AT1500 unit for replacement. DBox - intact | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/13/2023 | Jan 1 1900 9:45AM
09/14/2023 | Alternative | Routine/Scheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Puraflo |  | Pump | Pressure | Pad |  | 600.000000 | ["Attached Growth Medium","Effluent Screens"] | Effluent Screens | YES | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/05/2023 | 12:18 PM
06/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/12/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Air pre-filter cleaned as preventative maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
04/18/2023 |  | RoutineScheduled | 175-16-0284 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [5 empty] | 04/18/2023 |  | 131.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 12:48 PM
07/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"Control Operation" ,"BlowerCompressorAerator Operation"] |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 08/15/2023 | 01:44 PM
08/03/2023 | Alternative | RoutineScheduled Component Maintenance | 107-07-0512 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired valve box | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
04/28/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1875 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/25/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 2.000000 | 3000 | EcoPod |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | 4th Quarter 2022 inspection. Grease trap, First section - 0" crust, 20" of solids on bottom, Second section - 3" crust, 22" of solids on bottom. Septic Tank - 0" crust, 18" of solids on bottom. EQ tank - 0" crust, 3" of solids on bottom. Denitrification tank- 0" crust, 0" of solids on bottom. Treatment Unit - 0" crust, 1" of solids on bottom. Clarifier - 0" crust, 20" of solids on bottom. Discharge tank - 0" crust, 0" of solids on bottom. Meter Reading - 226510, 260 gallons since 12-31-2022. Meter is either stuck or defective. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/07/2023 | 07:03 PM
01/11/2023 |  | RoutineScheduled | 087-STS-6145 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Norweco Singulair |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","Distribution Pump Operation","Control Operation","Effluent Screens","Level Sensor Operation","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/11/2023 | 12:00 AM
10/17/2023 | Alternative | RoutineScheduled Component Maintenance | 182-11-0107 | Rockingham | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Recommend removing trees near system, installing riser and pump primary tank Pumping of tank is required for passing inspection | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/06/2023 | 03:05 PM
11/21/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["Disinfection","BlowerCompressorAerator Operation"] | ["Disinfection","BlowerCompressorAerator Operation"] | NA | [7 empty] | 11/21/2023 | Sample Chamber | 5.000000 |  | 220.000000 |  |  |  | Attached to this report |  | Septic Tank-0"sludge 0"scum/ Microfast-0"sludge 0"scum/ Pump Tank-0"sludge/ No pump out needed at this time (Tanks were pumped out on 11/15/2023) Blower air filter cleaned and blower working correctly/ UV-Light sleeve cleaned and light is working correctly/ Counts: Pump-5404 ETM-1112h 38m/ Peak counts-44 ETM-5403h 5m/ High-519/ Controls, pump, floats and alarms are functioning properly/ No breakout or spongy areas on the drip field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/06/2023 | Alternative | Routine/Scheduled | 151-13-114 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 1600 | Clearstream |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 55.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/06/2023 | 04:46 PM
10/18/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | UV |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 11/15/2023 | Dec 30 1899 2:02PM
10/18/2023 | Alternative | Reportable Incident | 128-10-023 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm Call: -Microfast. Customer said the air blower made a louder like bad bearing noise in the night and was really hot. When I arrived the air pump was pretty hot and it would randomly get a louder high pitch noise. I sent Fred the estimate for the blower replacement and he said he will approve it when the blower finally goes bad completely | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 11:31 AM
03/30/2023 |  | RoutineScheduled | 14-197-A2 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Multiflo |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Control Operation","Auxiliary Filter","Attached Growth Medium","BlowerCompressorAerator Operation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/30/2023 | 12:00 AM
05/24/2023 | Alternative | Initial Visit |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | LP |  |  | Pressure | Trenches | Not Applicable |  | ["Septic Tank Baffles"] | ["Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/24/2023 | 12:00 AM
12/12/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Installed new Fuji CN5 per permit approval Annual completed at the same time | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 12:00 AM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
05/10/2023 |  |  | 033-07-0185-ST | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
09/29/2023 | Alternative | RoutineScheduled | 107-13-0345 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
06/14/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 12:00 AM
08/03/2023 | Alternative | Pump-Out Only |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | Dispersal System Operation | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Pumped trash tank and pump tank empty as recommended during previous service visit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | Dec 30 1899 9:15AM
02/27/2023 |  |  | SWP-05-05 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
06/08/2023 | Alternative | RoutineScheduled | 15-142-0028 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/13/2023 | Alternative | Initial Visit | 151-09-0012 | Lancaster | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 600.000000 | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit - no indications of previous service provider. Primary septic tank - root intrusion - effluent screen broken and requires replacing - cleaned best able. Pump Tank - float sensors, pump and controls operating. BioFilter - 5 modules - peatmoss has failed - inspection port holding effluent, appears that pad may have failed. Biofilter media saturated. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/21/2023 | 08:45 AM
08/12/2023 | Alternative | RoutineScheduled | 109-14-0218 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX-RT |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 16" of accumulated solids in septic tank. Cleaned septic tank solids filter. 16" in recirculation portion of treatment unit. 12" of solids in discharge portion of treatment unit. Flushed treatment unit spray manifold. Tested floats, pumps and alarm. The system may need to be pumped out next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/27/2023 | 07:03 PM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/11/2023 | Alternative | RoutineScheduled | VAG408413 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Gravity | Discharge | UV |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | small tree in ET bed needs to be removed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | 12:00 AM
01/19/2023 |  | Routine/Scheduled | 06-120-0667AR | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 2.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/19/2023 | Jan 1 1900 1:05PM
05/11/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty |  | 7.510000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/31/2023 | 11:45 AM
04/12/2023 |  | Pump-Out Only |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Pumped trash tank and aeration tank as recommended during last service event. Refilled aeration tank with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 08:45 AM
09/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001763 | Jessica | Young | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/18/2023 | 01:19 PM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance | 182-08-0338 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
03/22/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/16/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | UV bulb and ballast were replaced. The system should return to proper function. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/22/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/28/2023 | Alternative | Initial Visit |  | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | AOSE called due to an alarm. We found the pipe has settled between the Clearstream tank and pump tank. This is causing the weir filter to be cocked up in the Clearstream tank which is causing the septic tank to be flooded. The settled pipe is also causing the UV in the pump tank to be cocked up and not allowing the effluent to flow properly. The UV wires are too short - not enough wire to get housing off UV and should be stranded wires to access the bulb. The disconnect is not wired correctly - will not work. The return from the pump tank is in the outlet tee not in the inlet tee. There is no splice box in the pump tank. The grading and seeding on the drainfield and around the tanks needs to be addressed. All of these issues need to be addressed and/or corrected. At this point we do not have a maintenance contract with the homeowner nor did we receive the warranty paperwork from the installation contractor. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/28/2023 | Dec 30 1899 12:00PM
03/09/2023 |  | RoutineScheduled | 13-197-103 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Multiflo |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/09/2023 | 12:00 AM
03/04/2023 |  | RoutineScheduled | 2116-06-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination | 500.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] | YES | Musty | Clear | 7.400000 |  |  | 1.800000 |  | 03/06/2023 | Sample Chamber | 23.000000 |  |  | 10.600000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/17/2023 | 12:00 AM
01/24/2023 |  | Reportable Incident |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced DF-60 compressor. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 11:08 AM
02/06/2023 |  | RoutineScheduled | SWP-05-497 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. no water in pod. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
05/22/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-92920 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
07/21/2023 | Alternative | RoutineScheduled | 175-08-0495 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank | Pump Tank to Puraflo Modules to Drip Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-4"sludge 0"scum/ Pump Tank to Puraflo Modules-1"sludge/ Pump Tank to Drip Field-2"sludge/ No pump out needed at this time/ Puraflo Peat turned and in good condition/ Controls, pumps, floats, alarms and hydraulic unit functioning properly/ Counts: Puraflo Pump-38305 ETM-221920/ Hand-cnt-93/ High cnts-43/ Override cnt-43/ Drip Pump Counts-49424 Pump Run Time Hours-13687/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/01/2023 | Alternative | Initial Visit | 16-163-0108 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Advanced Septic |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit. Primary septic tank - normal level - effluent screen serviced. Aeration tank (Aquasafe) - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/07/2023 | Dec 30 1899 11:30AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance | 175-18-0075 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | UV |  | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | ATU needs pumped due to high scum and sludge levels. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/17/2023 | 12:46 PM
12/18/2023 | Alternative |  | 06-184-5006 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/18/2023 |  | 6.670000 |  |  | 6.200000 |  |  | Will be sent separately |  | BOD: 6.67 TSS: 6.20 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 12:00 AM
03/29/2023 |  | RoutineScheduled | 08-183-278 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/29/2023 | 12:00 AM
10/26/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-501 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Media showing its age 5" below manifold, recommend to replace it. Will send proposal. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
05/12/2023 |  | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Multiflo FTB |  | Pump | Gravity | Trenches |  | 600.000000 | None | None | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 02:58 PM
03/27/2023 |  | RoutineScheduled | 2014-143-0135 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1200 | Clearstream |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 12:00 AM
02/21/2023 | Alternative | RoutineScheduled | 150-08-0155 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 2.000000 | 2800 | Septic Tank | Premier Tech EcoFlo | Pump | Gravity | Pad | Not Applicable | 450.000000 | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Cloudy | [15 empty] | EcoFlo annual maintenance performed this date. EcoFlo had significant ponding under distribution panels, peat in middle significanlty deteriorated. Mixed deteriorated peat mixed in with good peat around perimeter, ponding drained. Cleaned distribution panels, tipping tray, reset panels and tray. Pump, floats, alarm operating properly. ST- 3" FOG, 2" sludge, cleaned effluent filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/26/2023 | 02:40 PM
11/06/2023 | Alternative | Routine/Scheduled | 136-05-0229 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal level 10 in of sludge 1 In of solids No signs of infiltration -Discharge/Pump Tank: Normal level 7 in of suspended solids Tested floats and pump all working as should All plumbing intact and pump moving water properly Riser is showing signs of leaking -Aeration: Normal level 8 in of suspended solids Pulled and cleaned diffuser Air line intact Pulled and cleaned weir Riser is showing signs of leaking -Air Pump/Blower: 120 volts coming in Air pressure sensor properly working Pulled and cleaned filter -Control Panel: 120 volts coming in All visual and audible alarms functioning properly Pump pulled 7.02 amps All components working as should -Distribution Box: Normal level 6 lines all intact and taking water Small crack on sidewall of Dbox Dbox is warped and lid won't fit properly -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 10:40 AM
06/15/2023 | Alternative | RoutineScheduled | 10-120-0254AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 2.000000 | 2250 | Clearstream |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Attached Growth Medium"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Attached Growth Medium"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 12:00 AM
11/08/2023 | Alternative | RoutineScheduled Component Maintenance | 033-STS-90115 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
01/27/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | blower panel replaced keep drainfield mowed | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
10/06/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-24251 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.500000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1875 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/24/2023 |  | RoutineScheduled | 175-07-0127 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | YES | [17 empty] | EZ-TREAT Recirculation Tank- Septic tank side 6"sludge 3"scum/ Recirc. side-2"sludge 0"scum/ Pump tank-0"sludge 0"scum/ No pump out required at this time/ Controls, pumps, floats and alarms functioning properly/ Pump intake cleaned/ Counts: Pump-257 ETM-32h 20m/ High-9/ Recirc. - On-3m Off-12m/ Discharge Pump-On-7m 37s Off-12h/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/12/2023 | Alternative | Follow-Up Component Maintenance | 177-11-0121-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to disassemble components in recirc tank and assist pumper with a proper pump out. Reassembled components and filled recirc tank back to proper levels. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
12/21/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | Dec 30 1899 1:00PM
09/21/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation"] | ["Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Broken Air Release Valve in drianfield. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | Dec 30 1899 12:58PM
02/15/2023 |  | RoutineScheduled | 175-02-0079 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump"] | ["Dispersal System Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Effluent surfacing at distribution boxes. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/13/2023 | 11:23 AM
08/22/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-106 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Annual inspection. Recommend cut down tree that is growing on top of the pump tank, and also a cherry (?) tree that is about 8 feet from the end of the pump tank - large roots can be seen growing towards the tanks. Effluent in d-box looks the same as it does in the pump tank (no treatment). Heavy channeling in first pod, heavy ponding in pods #2 and #3. Recommend replace all the peat. Distribution grid in pod #4 needs shimmed to be level. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
11/27/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/27/2023 | Dec 30 1899 2:15PM
10/09/2023 | Alternative | Routine/Scheduled | 175-06-0015 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | Dec 30 1899 3:30PM
05/25/2023 | Alternative | RoutineScheduled | 023-STS-42981 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke |  | 1942001505 | John | Burch | 1.000000 | 1000 | Infiltrator ATL |  | Gravity | Gravity | Pad | Not Applicable | 150.000000 | ["None"] | ["None"] | NA | None | Clear | [15 empty] | Insufficient volume in sample port to sample - | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/25/2023 | Jan 1 1900 5:00PM
08/09/2023 | Alternative | RoutineScheduled | 166-04-007 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Elite Onsite | 1942001726 | Drew | Saunders | 3.000000 | 2000 | 1000 | 1000 | Pump | Pressure | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Effluent Screens","Attached Growth Medium"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | 05:45 PM
04/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend servicing advantex in the near future | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/15/2023 |  | RoutineScheduled | `177-19-0019-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"Attached Growth Medium"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
07/11/2023 | Alternative | RoutineScheduled |  | Culpeper | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-12"sludge 6"scum (THICK LAYER OF SCUM AND WIPES) Microfast- 4"sludge/ Pump Tank- 2"sludge/ PUMP OUT AND CHEMICAL CLEANING REQUIRED DUE TO CLOGGED MICROFAST MEDIA AND WIPES WHICH IS CAUSING THE BLOWER TO RUN HOT/ Controls, pumps, floats and alarms are functioning properly/ Blower air filter cleaned/ Counts: Pump1-14423 ETM-251h 7m/ Pump2-14302 ETM-248h 48m/ Peak-52/ High-57/ On-85s Off-2h/ No breakout or spongy areas on the drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
08/15/2023 | Alternative | RoutineScheduled | 035-STS-37285 | Carroll | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | ECOPURE |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 12:00 AM
05/02/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/23/2023 | 09:32 AM
09/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | ["None"] | ["None"] | NA | None |  | 7.200000 | 8.040000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | Dec 30 1899 2:00PM
12/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Gravity | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 12/28/2023 |  | 142.000000 | [5 empty] | Will be sent separately | Inspected | supply and return gauge filter o ring | This AOSS should now return to normal function after having provided the above state routine maintenance | 01/15/2024 | 10:39 AM
12/05/2023 | Alternative | Reportable Incident | 027-STS-15637 | Buchanan | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | CLEARSTREAM |  | Pump | Pressure | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 15 - Bio Max tablets installed Aerator down, left loaner aerator in system | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 12/05/2023 | 12:00 AM
02/22/2023 |  | Routine/Scheduled | {FIPSCode}-STS-4989 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | Jan 1 1900 11:25AM
01/23/2023 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2023 | Jan 1 1900 3:40PM
01/03/2023 |  | RoutineScheduled | 133 04 1026 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | BioWhee |  | Gravity | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [7 empty] | 12/15/2022 | Sample Chamber | 0.000000 |  |  | 4.600000 | 12.700000 |  | Will be sent separately |  | Monthly Report. Total flow for month of December 2022 - 24,839 gallons. Average daily flow - 801gallons | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/12/2023 | 07:03 PM
02/09/2023 |  | RoutineScheduled | 175-16-0450 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank | Pump Tank | Pump |  | Discharge | Chlorination |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NO | [17 empty] | Septic-6"sludge 2"scum/ EZ-Treat Recirculation Side-3" sludge 0"scum/ Pump Tank-2"sludge/ No pump out needed at this time/ Controls, pump, floats and alarms functioning properly/ Recirculation pump intake cleaned and media spray heads are clean/ Chlorination & Dechlorination tablet holders are full and functioning properly/ Counts: Pump-46484 ETM-120766 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/13/2023 | Alternative | RoutineScheduled | 01-197-416 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
04/05/2023 |  | Reportable Incident | 19-120-0054A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm/red light on - installed an aerator rebuild kit. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Replaced the UV light bulb. Could not locate vacuum breakers - no valve boxes. The timer is set to 8 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/05/2023 | Jan 1 1900 12:00PM
03/06/2023 | Alternative | Routine/Scheduled | 157-18-0073 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Biofilter - peatmoss in good condition - raked / turned. Pump Chamber - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | 09:45 AM
02/17/2023 | Alternative | RoutineScheduled Component Maintenance | 175-06-0341 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | 11:24 AM
03/19/2023 |  | Reportable Incident | 179-STS-90038 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system alarming due to failed transducer. Replaced transducer. Will send updated proposal to change the pump while onsite to replace the panel door. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
07/25/2023 | Alternative | RoutineScheduled Component Maintenance | SD-14-117 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Sulphitic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
10/16/2023 | Alternative | RoutineScheduled | 06-197-A3 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 6.000000 |  |  | 0 | [10 empty] | Aerator working, effluent clear, no odor, tablets stocked. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
09/09/2023 | Alternative | RoutineScheduled | 2129-10-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | ATU | Polishing Sand Filter | Pump | Gravity | Discharge | UV | 250.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Level Sensor Operation"] | ["Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | 7.000000 | [15 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
04/27/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Lower line was cameraed and there were no signs of an issue. DSS adjusted dial flows and releveled the box. The field appears to be evenly distributed. Advise homeowner to monitor and notify if there are any changes | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/21/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | Dec 30 1899 9:35AM
02/15/2023 |  | RoutineScheduled | 11-118-0070 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1000 | Clearstream |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/15/2023 | Jan 1 1900 1:55PM
10/24/2023 | Alternative | RoutineScheduled | 06-192-065 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | WHITEWATER |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Level Sensor Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/24/2023 | 12:00 AM
07/17/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-90172 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"Recirculation Pump" ,"Control Operation" ,"Attached Growth Medium"] | NA | None | Clear | [5 empty] | 07/17/2023 |  | 19.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Bad R.0 float in discharge tank, replaced. Couple wet spots, AOSE was contacted he will stop by to look at it. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:19 PM
10/24/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
06/16/2023 | Alternative | RoutineScheduled | 2016-143-0031 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["Control Operation","BlowerCompressorAerator Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/14/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | 12:00 AM
05/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
07/27/2023 | Alternative |  | 09-113-236 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/27/2023 |  | 7.130000 |  |  | 20.800000 |  |  | Will be sent separately |  | BOD: 7.13 TSS: 20.8 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/27/2023 | 12:00 AM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Disinfection"] | ["BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | The owner did not want us to touch the UV light. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
12/12/2023 | Alternative | RoutineScheduled Component Maintenance | SD-05-623 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Big tree fell over drainfield, but most of the limbs are being held up by the large root ball. Owner looking into getting tree milled into lumber. Peat has lost a lot of its texture, but otherwise in good shape for its age (17 years). Recommended pump out of both tanks, owner to make arrangements with local pumper. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
06/30/2023 | Alternative | Reportable Incident | 157-06-0336 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | AOSS - Alarm Event - compressor failure - blown diaphragms - repaired on property - restored to proper operation. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/05/2023 | 08:30 AM
04/10/2023 | Alternative | RoutineScheduled | 08-100-0949 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 750 | BIOCOIR |  | Pump | Gravity | Mound | Not Applicable | 300.000000 | [] | [] | YES | [16 empty] | Pumped Out | PUMPED SEPTIC TANK. INSTALLED A NEW 20" TUFF TITE LID. REPLACED FIBER. REPLACED DISCONNECT EVERYTHING WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | 02:15 PM
09/06/2023 | Alternative | RoutineScheduled Component Maintenance | SD-15-053 | Orange | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Clearstream | none | Pump | Gravity |  | UV |  | ["Attached Growth Medium" ,"SludgeScum Accumulation" ,"Disinfection" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | NA | Pungent | Discolored | [13 empty] | Will be sent separately | Inspected | As noted previously, the UV light is not working and should be replaced. We had also noted that the ClearStream control panel door had been damaged. The inside of the control panel is corroding and may need to be replaced in the near future. Additionally, both air pumps for the ClearStream ATU have stopped working and should be replaced. We also recommend pumping the septic tank and Microfast ATU due to sludge accumulation in the tanks. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/02/2023 | 06:05 AM
03/11/2023 | Alternative | Routine/Scheduled | 036-STS-34037 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 1250 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/11/2023 | Dec 30 1899 9:00AM
01/05/2023 | Alternative |  | 099-17-0074 SR | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
07/17/2023 | Alternative | Reportable Incident | 157-10-0210 | Mathews | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | UV | 450.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service inspection for contract renewal! Trash Tank - normal level Aeration tank - compressor diaphragm failure - requires replacing. U.V. Disinfection - bulb blown - requires replacing. Pump Tank - pump enable float sensor stuck ON - requires replacing. Drip Field - Vacuum breaker damaged (lawn care) and requires replacing. Discrepancies reported to owner - need to be addressed prior to renewal of service agreement. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/18/2023 | 07:45 AM
07/06/2023 | Alternative | Reportable Incident | 234-17-0032 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the disc filter. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. Replaced the UV Ballast and bulb. The timer is set to 8 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/06/2023 | Dec 30 1899 10:00AM
10/11/2023 | Alternative | Reportable Incident | 10-142-0081 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm Call: -Upon arrival, I found the pump control panel in alarm condition indicating discharge in high level. Float status indicated that the timer enable float was in the "OFF" position. Checked and confirmed discharge tank was in high level. Checked and confirmed discharge timer enable float had failed in the "OFF" position. Homeowner gave written approval to upgrade all discharge floats. Discharge floats were upgraded while on site. Checked and confirmed discharge floats are functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | Dec 30 1899 4:01PM
06/29/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-5319 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/29/2023 | Dec 30 1899 3:25PM
07/05/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-1832 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | Dec 30 1899 2:09PM
08/17/2023 | Alternative | RoutineScheduled | 107-98-0292 (LEGACY ALT. SYSTEM), | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
07/12/2023 | Alternative | RoutineScheduled | 175-15-0073 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 07/12/2023 | Sample Chamber | 8.000000 | [5 empty] | Attached to this report |  | Septic Tank-4"sludge 0"scum/ Microfast-6"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working properly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-004633 ETM-0045236 On-5m 24s Off-11h 54m/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/25/2023 | Alternative | Follow-Up | SD-13-221 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Cleaned FAST media. FAST tank pumped out by others. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
11/24/2023 | Alternative | RoutineScheduled | 2073-05-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Recirculating Sands Filter |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation"] | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] | NA | Musty | Clear | 7.800000 |  |  | 1.900000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/27/2023 | 12:00 AM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-87577 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001682 | Frank | Hogan | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Disinfection" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Auxiliary Filter"] | NA | Musty | Cloudy | [5 empty] | 06/27/2023 | Pump Chamber | 61.000000 |  | 2420.000000 | 59.000000 | 47.000000 |  | Will be sent separately | Inspected | rrothgeb - Robert Rothgeb - Jun 27, 2023 8:45 AM Finished qtr samples . rrothgeb - Robert Rothgeb - Jun 20, 2023 12:13 PM WWTP Secure and gates locked on arrival: Yes Unusual odors around plant: Yes. Faint odor. Blowers working if present: Not Applicable Any component in Alarm?: No - 0 Pump Station Locked if present: Not Applicable Test telemetry system raise all floats for notice for office: Telemtry working Drive through community look for alarms and overflows: No alarms identified Community alarms or overflow detail: NA - 0 Completed Data Sheets: No Peak Flow Last 7 Days: 7729 gal. 6/14/23 Low Flow Last 7 Days : 5757 gal. 6/18/23 AVG Flow Last 7 Days : 6518 gal. From 6/13/23 To 6/19/23 rrothgeb - Robert Rothgeb - Jun 25, 2023 11:48 AM Next dooR neighbor reports water shooting to the sky from one of the tanks, arrived on site and found broken ARV on drip discharge tank pump broken, effluent shooting out durinp pumP cycle. Lid not secured, blew lid off. Went to VAMAC, in Fredericksburg, picked up two replacement ARVs. Went to Tractor Supply Co. for lime. Removed stub left from ARV, in discharge of Dosing Pump #1, and replace ARV on discharge of Dosing Pump #2. Back in service. Applied lime to fence line and ground beyond fence. mrlynn - Makenzie Lynn - 6/26/2023 4:59:49 PM - RR return to GZ to fix broken ARV at discharge pump - bought and replaced 2 both in the tank PPLIED LIME APPROX LOSs 300 GALLONS mrlynn - Makenzie Lynn - 6/5/2023 4:24:52 PM - customer called and said area wet around tank and grass high around tank - no alarm light is active. Please check and let me know what is needed. Rrothgeb - Robert Rothgeb - Jun 06, 2023 9:57 AM Pump replaced, alarm had been silenced. All working upn completion, Limed affected area. Lot 35 800 - 5035 Frederick Rehbein Alarm Call/USV Alarm rrothgeb - Robert Rothgeb - Apr 14, 2023 7:47 PM Leaving rrothgeb - Robert Rothgeb - Apr 14, 2023 7:34 PM Replaced pump. Pumping down. Put two BIO-PAK pills in pump suction. Peak Flow Last 7 Days: 10366 gal. 3/11/23 Low Flow Last 7 Days: 0 gal. 3/8/23 and 3/9/23 AVG Flow Last 7 Days: 5372.9 gal. From 3/7/23 To 3/13/23 Dosing pump 1 amps are ok and pump is dosing as it should. Recirc pump 1 connections were burned not allowing it to run. Made fresh connections and pump is ok. Pressure gauge in ez treat 1 was broken and has been replaced while on site. Moved gateway to plant and connections are now strong. Checked field there is still spots with water on the surface but when you dig down it is dry below the surface. Fields are meeting dosing rates not simulating leaks. Recirc tank that contains pumps 1- 3 needs pumped due to high levels of sludge. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
09/08/2023 | Alternative | RoutineScheduled | 115-05-0384 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Other conventional maintenance performed | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 12000 | Biomicrobics Fast 2.5 |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Group meeting with engineers and contractors to discuss the new school addition | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/30/2023 | 09:30 PM
02/11/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 2.000000 | 2000 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 3" of solids crust in septic tank. 4" of accumulated solids in bottom of septic tank. Recirculation tank has 16" of accumulated solids. The discharge pump tank has 0" of solids. Cleaned recirculation pump basket filter. Flushed treatment unit spray manifold. Sprayed solids off of treatment unit sheets. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 07:03 PM
07/19/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Pumped septic tank and parged inlet tee | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | 12:00 AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
11/22/2023 | Alternative | RoutineScheduled | 101-STS-96147 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/17/2023 |  | RoutineScheduled | 08-163-0036 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Advantex |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Control Operation","Recirculation Pump","Distribution Pump Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | 12:00 AM
05/14/2023 |  | Reportable Incident | 177-STS-87442 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to a toliet constantly in the detached garage. Turned water supply to toliet off and pumped down system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
07/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired leaks in drainfield Recommend removing water softner off of septic due to high amounts of grease on media | This AOSS should now return to normal function after having provided the above state routine maintenance | 08/23/2023 | 06:57 AM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/17/2023 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  | 600.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/18/2023 | 02:00 PM
05/17/2023 | Alternative | RoutineScheduled | 121-STS-12162 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000 | Aqausafe |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | [] | NA | Septic | Dark Brown | [5 empty] | 05/17/2023 | Sample Tap | [6 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/23/2023 | 12:00 AM
03/31/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
08/24/2023 | Alternative | Routine/Scheduled | 166-12-031 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 5.000000 | 4200 | Clearstream |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 75.000000 | [11 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/24/2023 | 05:40 PM
02/27/2023 |  | RoutineScheduled | 2010-143-0124 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C & E Mechanical Corporation | 1942001339 | Louis | Timberlake | 1.000000 | 1500 | Norweco Singulair |  | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Level Sensor Operation","Distribution Pump Operation","Effluent Screens","Dispersal System Operation","BlowerCompressorAerator Operation","Control Operation"] | YES | [6 empty] | Recommend pumping next year | [9 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 02:30 PM
11/22/2023 | Alternative | Routine/Scheduled | 166-08-138 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Puraflo |  | Pump | Pressure | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 10.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/22/2023 | 03:42 PM
11/30/2023 | Alternative | Follow-Up | 00-197-088 | Wise | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | Musty | Clear | 6.000000 | 5.000000 |  | 0.000000 | [12 empty] | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | 12:00 AM
11/02/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-90521 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
03/02/2023 |  | RoutineScheduled | 061-STS-25944 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [8 empty] | 03/02/2023 | Sample Chamber | 30.000000 |  |  | 8.000000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/20/2023 | Alternative | RoutineScheduled Component Maintenance | 033-17-0197-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/10/2023 | 10:02 AM
10/13/2023 | Alternative | Reportable Incident Component Maintenance | SD-13-404 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | Septic | Cloudy | [13 empty] | Will be sent separately | Inspected | No alarm, but tank was full to the lids in all compartments. Alarm had been muted at an earlier date and never reset. Alarm bulb was burnt out, replaced it. Compressor was not running. Replaced blown out diaphragms, air filter and diffuser element in the atu. Verified power getting to the pump, but no response from the pump. Ordered same pump model from Clearstream distributor. Clamps had come loose on high level float and override float. Override float was stuck on, probably eventually caused pump to fail. Junction box cover missing (box mounted inside pump riser). Will need to replace wire nuts and the cover, or install an entirely new box. Installer did not pull wires for the pressure switch. If he had, the control panel would have (attempted to) alarm. Note: tank was pumped out the next morning by a local pumper (Butler's Septic). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
02/01/2023 |  | Routine/Scheduled | 810-STS-3895 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/01/2023 | Jan 1 1900 12:40PM
08/16/2023 | Alternative | RoutineScheduled | 136-15-0197 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001302 | Charles | Langford | 2.000000 | 1000 |  |  | Pump | Pressure |  |  |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/25/2023 | 12:00 AM
11/01/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | Dec 30 1899 12:05PM
07/26/2023 | Alternative | RoutineScheduled | 16-120-0154AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Ecoflo |  | Pump | Gravity | Trenches |  |  | [] | ["Level Sensor Operation","Attached Growth Medium","Control Operation"] |  | Musty | Clear | [15 empty] | IFFC determined that system is lawful, see file for more details | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
11/25/2023 | Alternative | Routine/Scheduled | 05-160-0446 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable | 25.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/25/2023 | 12:30 PM
10/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | Septic | Septic | pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [18 empty] | Needs one off float replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12:00 AM
07/31/2023 | Alternative |  | 10-192-191 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/31/2023 |  | 2.510000 |  |  | 10.400000 |  |  | Will be sent separately |  | BOD: 2.51 TSS: 10.4 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/31/2023 | 12:00 AM
08/07/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | 12:00 AM
10/20/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | Dec 30 1899 2:00PM
01/06/2023 |  |  | 06-142-0515 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Puraflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Inspected | Peat is in okay condition, there are some roots present in the pods. Recommended homeowner treat with root killer. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | 12:00 AM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | Dec 30 1899 11:24AM
11/29/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-90121 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
09/01/2023 | Alternative | RoutineScheduled | 00-192-350 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/01/2023 | 12:00 AM
02/16/2023 | Alternative | Reportable Incident | 159-88-143 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | COSS - Maintenance - GMP2018-02 Replaced distribution box with new 8 port concrete DBox Spliced to existing conveyance line. Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 06:45 AM
03/28/2023 | Alternative |  | 139-03-0064 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Edward & Tanya | Prachar | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/05/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | [] | [8 empty] | 10/05/2023 | Pump Chamber | 105.000000 | [7 empty] | 5 year BOD sample | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/10/2023 | Dec 30 1899 10:40AM
12/07/2023 | Alternative | RoutineScheduled | 07-184-5007 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | [17 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/04/2023 | Alternative | RoutineScheduled | 12-197-076 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | CLEARSTREAM |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","SludgeScum Accumulation","Effluent Screens","Level Sensor Operation","Control Operation","Dispersal System Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | 12:00 AM
09/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 | 1500 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Pods are full of effluent Need to unclog | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/23/2023 | Dec 30 1899 4:40PM
09/13/2023 | Alternative | Routine/Scheduled | 08-137-0191 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Recirculation pump has exceeded life expectancy. Recirculation pump plumbing has exceeded life expectancy. Recirculation floats have exceeded life expectancy. -RSV: Flushed and cleaned RSV. Checked and confirmed it's clear of debris and functioning properly -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Removed roots from discharge outlet. Discharge pump has exceeded life expectancy. Discharge pump plumbing has exceeded life expectancy. Discharge floats have exceeded life expectancy -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Checked and confirmed spray height is good. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Control panel has exceeded life expectancy. -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact. Removed root infiltration. One dispersal line is clogged with roots -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | Dec 30 1899 4:19PM
11/08/2023 | Alternative | Routine/Scheduled | 07-160-0046 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable | 269.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/08/2023 | 12:00 PM
11/28/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Fairfax | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | ATU | Polishing Sandfilter | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | 7.300000 |  |  | 1.900000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/01/2023 | 12:00 AM
04/05/2023 | Alternative | Follow-Up | SD-10-208 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001236 | Stuart | Lynn |  |  | Whitewater ATU | Whitewater ATU | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | None | [14 empty] | Will be sent separately | Inspected | UG-1 Total N 1.211 ppm Chlorides 19.9 ppm MW-2 Total N .654 ppm Chlorides 2.48 ppm MW-1 Total N 4.73 ppm Chlorides 8.31 ppm | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
02/19/2023 |  | Routine/Scheduled | 041-STS-260005 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [16 empty] | Recommend pump out | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/19/2023 | Jan 1 1900 10:30AM
03/29/2023 |  | RoutineScheduled | 179-STS-87577 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001682 | Frank | Hogan | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  |  |  | NA | Musty | Cloudy | 7.200000 | 4.000000 | [11 empty] | Will be sent separately | Inspected | 1-12-23 Sewage Backup in house, float stuck 218 Southern View Drive. Found: force main in the tank is broken Items that need to be addressed: force main needs to be repaired and system need two floats both ones are sending a false signal back to the panel. ( black ones ) dcrespin - Darwin H Crespin Cortez - Jan 13, 2023 2:40 PM The reason for our site visit today was:: Alarm Call Investigation The condition of the system on arrival was:: System was in alarm Actions taken today were:: Issue identified that needs further work Items needing repair or repalcement are:: Floats repaired / replaced / force main in the tank Controls left in: OFF Are all lids secure and screws installed: Yes 1-16-23 Repair Force main hid by Verizon repaired and two floats replaced Lot 41 mcox - Michael Cox - 1/19/2023 4:16:39 PM - Clean all spray heads at EZ Treat Pull Discharge Pump Check Wet Spots at Drainfield, Repaired 2 broken air release valves check pump at 218 Southern View Drive and make sure it is all working Cleared stuck float rrothgeb - Robert Rothgeb - Jan 24, 2023 2:17 PM WWTP Secure and gates locked on arrival: Yes Unusual odors around plant: Yes. Wash down EZ-Treat contact surface. Blowers working if present: Not Applicable Any component in Alarm?: Yes - 5. Filter Pressure Differential. Zones #7and #8 Catastrophic Flow and Flow Variance. Reset. Pump Station Locked if present: Not Applicable Drive through community look for alarms and overflows: No alarms identified Community alarms or overflow detail: NA - 0 Completed Data Sheet: No Peak Flow Last 7 Days: 7867 gal. 1/21/23 Low Flow Last 7 Days: 0 gal. 1/20/23 AVG Flow Last 7 Days: 5029.4 gal. From 1/17/23 To 1/23/23 2-6-2023 Flushed all zones manually Rigo, Steven , Johnni rrothgeb - Robert Rothgeb - Feb 21, 2023 8:01 AM WWTP Secure and gates locked on arrival: Yes Unusual odors around plant: Yes. Hosed down EZ-Treat units #1 and #4.(half) Blowers working if present: Not Applicable Any component in Alarm?: Yes - 1 Dosing Pump #2 removed. Pump Station Locked if present: Not Applicable Drive through community look for alarms and overflows: No alarms identified Community alarms or overflow detail: NA - 0 Completed Data Sheet: No Peak Flow Last 7 Days: 7474 gal. 2/20/23 Low Flow Last 7 Days: 6054 gal. 2/19/23 AVG Flow Last 7 Days: 6609.9 gall. From 2/14/23 To 2/20/23 rrothgeb - Robert Rothgeb - Mar 14, 2023 8:33 AM Arrived rrothgeb - Robert Rothgeb - Mar 14, 2023 9:47 AM WWTP Secure and gates locked on arrival: Yes Unusual odors around plant: Yes, Leftover from overflow earlier in week. Blowers working if present: Not Applicable Any component in Alarm?: No - 1. Dosing Pump #2 not working. Bad capacitor. Pump Station Locked if present: Not Applicable Drive through community look for alarms and overflows: No alarms identified Community alarms or overflow detail: NA - 0 Completed Data Sheet: No Peak Flow Last 7 Days: 10366 gal. 3/11/23 Low Flow Last 7 Days: 0 gal. 3/8/23 a | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
06/09/2023 | Alternative |  | 11-142-0002 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/05/2023 | Alternative | RoutineScheduled | 2086-04-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens"] | YES | Musty | Clear |  |  |  | 1.600000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
12/11/2023 | Alternative | RoutineScheduled | 05-184-5004 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | [17 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
02/14/2023 |  | RoutineScheduled | 179-STS-90510 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
09/12/2023 | Alternative | RoutineScheduled | 057-STS-95893 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/17/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
11/10/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | Dec 30 1899 2:15PM
05/02/2023 |  |  | 179-18-0247-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
08/29/2023 | Alternative | Routine/Scheduled |  | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. Dbox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | 07:30 AM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend removing tree closest to lower line | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/05/2023 |  | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Repair service call only: Replaced E-75 Ecopod Blower Wired and tested, functioning properly at this time. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
12/21/2023 | Alternative |  | 132-10-0111 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Andrew | Sheridan | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/05/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [7 empty] | 04/05/2023 |  | 2.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
04/19/2023 | Alternative | RoutineScheduled | 43-STS-32156 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 12:00 AM
06/16/2023 | Alternative | Reportable Incident | 199-13-0034 | York | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 4000 | Norweco Singulair ATU | Norweco Singulair ATU | Pump | Pressure | Pad | Not Applicable | 1200.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | Have been evaluating failure of absorption bed serving multiple households. Located distal end of LPP laterals - flushed and cleaned. Conducted TERRALIFT on absorption pad that is hydraulically overloaded. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/22/2023 | Dec 30 1899 9:15AM
05/17/2023 |  | Reportable Incident | {FIPSCode}-STS-251765 | Chesterfield | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Sandfilter, High rate |  | Gravity | Gravity | Discharge | Chlorination | 450.000000 |  | ["Control Operation","Disinfection","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - normal level Buried sand filter - not accessible Liquid chlorinator - functioning. Lab samples obtained. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/30/2023 | Jan 1 1900 9:10AM
05/27/2023 |  | RoutineScheduled | SD-03-189 | Madison | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | septic | FAST | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | YES | None | Clear | [15 empty] | Informal | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/01/2023 | 12:50 PM
06/20/2023 | Alternative | Reportable Incident | 061-STS-25899 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Blower failure. Replaced blower. Replaced faulty time relay. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/20/2023 | 12:00 AM
06/13/2023 | Alternative | RoutineScheduled | 163-STS-334194 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | ["Septic Tank Baffles","Dispersal System Operation","Auxiliary Filter","Attached Growth Medium"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/13/2023 | 12:00 AM
12/19/2023 | Alternative | Reportable Incident | 095-STS-5670 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Came out to take a look at the clearstream. Alarm was not on. Verified all components working as they should. There are some leaking risers and customer is getting in touch with the installer to get it fixed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/22/2023 | Dec 30 1899 8:24AM
04/26/2023 | Alternative | RoutineScheduled | 10-100-0496 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1250 | Septic Tank | Puraflo | Gravity | Pressure | Pad | Not Applicable | 450.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/25/2023 | 02:15 PM
04/21/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 11:24 AM
11/14/2023 | Alternative | RoutineScheduled |  | Shenandoah | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/06/2024 | 12:00 AM
01/23/2023 | Alternative | Routine/Scheduled | 166-06-493 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 4.000000 | 6000 | Microfast |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 45.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2023 | 07:09 PM
06/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/20/2023 |  | Reportable Incident |  | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | ["Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | System upgrades Replaced failed effluent screen with new. Replaced dosing pump plumbing with new. Replaced concrete riser with new plastic riser | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/24/2023 | 07:30 AM
04/05/2023 |  | RoutineScheduled | 103-STS-93039 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1500 | Microfast |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 12:00 AM
04/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/25/2023 | Alternative | RoutineScheduled | 09-183-029 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 10 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/25/2023 | 12:00 AM
04/11/2023 | Alternative | RoutineScheduled | SD-10-152 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | Chlorination |  | ["Disinfection"] | ["Disinfection"] | NA |  |  | 6.900000 | 9.200000 |  | 0.000000 | [9 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 04/17/2023 | 12:44 PM
06/30/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-2724 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | Dec 30 1899 10:15AM
03/07/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
04/04/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | NO | [17 empty] | Septic Tank-5"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ No pump out needed at this time/ Controls, pump, floats and alarms functioning properly/ Counts: High-000089/ Peak-999957 On-7m 45s/ Zone1-4.6 gpm/ Zone2-3.9gpm/ Zone3-4.6gpm/ No breakout or spongy areas on the drip field and dosing correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/17/2023 | Alternative | Routine/Scheduled | 234-18-004 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | Dec 30 1899 10:40AM
03/28/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Peat fiber is badly broken down and sandy. Peat fiber needs replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
03/09/2023 |  | RoutineScheduled | 03-197-048 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Multiflo |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/09/2023 | 12:00 AM
10/03/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1875 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/06/2023 | Alternative | Reportable Incident Component Maintenance | 179-10-0163-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for panel beeping and flashing because it was not getting proper signal from the transducer. Replaced failed transducer. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
01/12/2023 |  |  | 04-142-0379 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Puraflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Control Operation","Distribution Pump Operation","Effluent Screens","Attached Growth Medium"] | [17 empty] | Inspected | Replaced contactor and replaced on/off float switch | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/01/2023 | 12:00 AM
07/12/2023 | Alternative | Follow-Up Component Maintenance | 179-17-0442-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"SludgeScum Accumulation"] | ["Control Operation" ,"SludgeScum Accumulation"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Met local pumper (Marshall's Septic) on site, assisted with removal of tank components to allow for a complete pump-out of the Advantex recirculation tank. Tank refilled afterwards with fresh water from a pool water truck. Reviewed design and settings for drip system. Confirmed that drip pump settings do NOT include an override setting. Ran a test cycle. Drip and flush rates reasonably close to design. No wet or spongy areas observed in drip field. Previous inspection may have been done after rain or heavy use. Asked owner to call back if he sees any wet spots appearing in the dripfiled. Reset all "R" counts to zero. Total in recirc tank: 6 H/L and 24 L/L alarms. Total in drip tank: 3 H/L and 75 L/L alarms. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/18/2023 | 11:45 AM
03/07/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Effluent Screens"] | ["Control Operation" ,"Effluent Screens" ,"Auxiliary Filter"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
04/10/2023 |  | Routine/Scheduled |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Basin - plastic - deformity in side wall - float sensors, pump and controls operating. BioFilter - C2 & C3 Fracture noted - peatmoss in fair condition - raked / turned. Pump Basin - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/11/2023 | Jan 1 1900 6:15AM
03/17/2023 |  | RoutineScheduled | 177-18-0399-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Auxiliary Filter"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | There is a child's playhouse sitting on the dispersal area. If this is to convey with the house, we would recommend that it be moved to a different area in the yard. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
07/14/2023 | Alternative | Routine/Scheduled | 234-18-097 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | Dec 30 1899 8:40AM
04/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/05/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | ["None"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 12:00 AM
05/12/2023 | Alternative |  | 047-19-068 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 12:00 AM
01/20/2023 |  | RoutineScheduled | 003-STS-33059 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 12:00 AM
04/26/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The advantex and pump tank need pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
09/28/2023 | Alternative | Reportable Incident | 151-07-0172 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm call: -Alarm went off the day after heavy rain Opened system and found signs of leaks under both septic and pump tank risers as well as signs of leaks around outlet pipe in septic and around forcemain Repair 10/03/23: --Installation of 30" Riser on the Septic Tank -Installation of 24" Riser on the Pump Tank -Reseal the force main Pipe: - Manually excavate the exterior of the Tank up to 36" to access the force main Pipe - Parge the interior and exterior of the Tank around the force main Pipe - Backfill excavated area -Reseal the outlet Pipe: - Manually excavate the exterior of the Tank up to 36" to access the outlet Pipe - Parge the interior and exterior of the Tank around the outlet Pipe - Backfill excavated area Completed repairs per signed proposal. Tested all components upon completion and everything is working as it should | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/12/2023 | 10:03 AM
11/03/2023 | Alternative | RoutineScheduled | 019-STS-29338 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 2000 | Puraflo Peat Moss |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Alarm call due to Septic alarm sounding. Upon arrival system was in normal automatic mode and levels were normal. Checked float switches and Pump, All testing operational. Pump pulled between 9.8 and 10.2 amps in normal range. Alarm call possible due to the switch panel being in off position. System is operational. Pump run time 189.78 hrs and 19,705 Cycles on meters. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
02/27/2023 |  | RoutineScheduled | SD-12-174 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001682 | Frank | Hogan | 2.000000 | 22800 | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | NO | Musty | Cloudy | 6.400000 | 3.900000 |  |  |  | 02/10/2023 | Sample Tap | 106.000000 |  |  | 131.000000 | 30.200000 |  | Will be sent separately | Inspected | Alkalinity in final effluent 30.2, recirc 299, 2-1 & 2-6 Flushed lines, repaired leaks, serviced filters and spread lime 2-6 sent deip design to Geoflow, recommended changing dosing to 2 zones at once but flush one zone at a time. difficult since cant have diff run times for each zone 2-15 Spread Lime 2-17-22 reached out to Geoflow and American to evaluate current drip design American, loading rates extremely high for that soil and not enough tubing installed to cover. At less than peak flow, would require pump's to run 31 hours per day Geoflow pressure was in excess of 120 psi delivered to the zones. This likely the reason fittings blew apart in the first few years of operation, tubin likely permanently damaged before pressure regulators were added. 2-24 Spread Lime, check doing rates, adjusted zones being dose remotely 2-25 through 2-26. Pump 7 broken and high level alarm failed, approximately 2,000 gallons of treated sewage discharged around plant, cleaned up and limed, pump and alarms fixed | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/14/2023 | 03:49 PM
04/18/2023 |  | RoutineScheduled |  | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Quanics |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation","Control Operation"] | ["Level Sensor Operation","Control Operation"] | NA | [16 empty] | Inspected | Called due to an alarm- found the Float switch wires and floats had failed up, Noticed high water in the tank and suspected root maybe blocking pipe or dbox. Replaced bottom and middle float and system returned to normal operation Called back and returned 4-20 23- Called back due to High level alarm in tank after water use, i added 4 lbs of ROOTX treatment to the system and since then the alarm have gone away, owener is looking for Dbox to check for roots. We have noticed pump cycle increases over the past year. and adjusted, i suspected roots maybe blocking pipe rasining level in the tank,. counter 373191 cycles vs 364076 in decmber 9,115 cycles Pump Run time - Hour meter 4207;33 vs 3751:49 about 455 hours since my last visit. To reduce the number of pump cycles we increased run time to 5 min on and 15 min off after the second visit on 4-20-23. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/30/2023 | 09:30 AM
03/28/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 2.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Water Meter Readings: 03/06/2023 7624400 03/28/2023 7641300 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
11/27/2023 | Alternative | Routine/Scheduled | 228-05-0605 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Ecoflo |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None |  | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/27/2023 | Dec 30 1899 11:03AM
03/17/2023 | Alternative | Routine/Scheduled | 159-06-0208 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1250 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. BioFilter - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/20/2023 | 09:15 AM
08/28/2023 | Alternative | RoutineScheduled Component Maintenance | 061-18-111 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation" ,"Auxiliary Filter"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Recirc tank was in high level due to recirc pump not running. Repaired poor hot wire connection in Orenco splice box, verified recirc pump working again normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
08/08/2023 | Alternative | Initial Visit | S19-180-0004 | Roanoke | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 500 | Delta Whitewater |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Initial annual inspection. 16" of accumulated solids in septic tank. 24" of solids in treatment unit with 4" solids crust. Septic tank and treatment unit need to be pumped out. Broken PVC airline from blower to treatment unit was broken underground. Repaired and blower now aerating treatment unit. Cleaned blower air filter. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/17/2023 | Jan 1 1900 7:03PM
09/15/2023 | Alternative | Pump-Out Only | 16-160-0141 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [17 empty] | Pumped Out | Pumping & Cleaning Septic Tank (1000 gallons) JOB SCOPE: Pumped/cleaned septic tank; septic system is functioning at this time but not as designed as there are components that are recommended to be repaired/replaced. - recommend inlet line repair/upgrade as line is swagged - outlet line filter broke off from line and needs to be replaced - annual alternative inspection needs to be completed - customer would like to proceed with estimate | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/15/2023 | 12:00 AM
04/07/2023 |  | Follow-Up | 175-15-0419 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Attached Growth Medium","SludgeScum Accumulation"] | ["Attached Growth Medium","SludgeScum Accumulation"] | [18 empty] | Microfast Unit chemical cleaning and pump out completed. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/13/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/20/2023 | 12:00 AM
06/02/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
02/20/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | new audible alarm | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
12/06/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | [9 empty] | ["None"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 12:00 AM
11/10/2023 | Alternative | RoutineScheduled Component Maintenance | 177-11-0009-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
10/23/2023 | Alternative |  |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/23/2023 | 12:00 AM
02/14/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | roots d box solution to dbox change media and add shocks recommended | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
01/16/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Hott's Septic Service LLC | 1942001301 | Joshua | Hott | [8 empty] | 0.000000 | ["None"] | ["None"] |  | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | 12:00 AM
02/16/2023 |  |  | 179-STS-87934 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
05/02/2023 |  |  | 033-11-0074-SR | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 12:00 AM
03/23/2023 |  | Pump-Out Only | {FIPSCode}-STS-3222 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/23/2023 | Jan 1 1900 1:00PM
03/15/2023 | Alternative | RoutineScheduled | 159-17-0220 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Aquasafe |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | [] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
04/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/08/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 1.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/22/2023 | 12:00 AM
09/11/2023 | Alternative | RoutineScheduled | 109-04-0018 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Multiflo ATU |  | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | Blower Alarm sensor had scum on the sensor causing a false alarm. Rinsed off the sensor as best possible but would not stop alarming. Air pump is new, System has good aeration and fully operational but alarm is a nusiance. It was disconnected per owner request | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/30/2023 | 12:30 PM
11/07/2023 | Alternative | Routine/Scheduled | 041-STS-261049 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/07/2023 | Dec 30 1899 12:09PM
09/06/2023 | Alternative | RoutineScheduled | 195-Discharge-29122 Jeb Syuart Hwy | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 2 - Blue Crystal tablets installed 4 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/06/2023 | 12:00 AM
05/15/2023 | Alternative | Follow-Up Component Maintenance | SR-98-350 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Control Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | Short in main motherboard was preventing zone 3 from being dosed. Installed latest version of control panel from American Mfg onto taller post with Trex type backer boards. Removed both junction boxes at the tanks for the pump and float connections. Boxes were previously mostly buried and suffered from ground water penetration. New junction boxes were mounted about a foot above ground on pressure-treated posts with new wire in conduit. Zone 3 (top zone) is now dosing but has no increase in flow rate while flushing. Dripfield will need cleared of all downed trees, saplings and brush before it can be inspected for kinked tubing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
01/02/2023 |  |  | 06-125-048 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/02/2023 |  | 6.050000 |  |  | 3.000000 |  |  | Will be sent separately |  | BOD: 6.05 TSS: 3.00 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/02/2023 | 12:00 AM
03/08/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/31/2023 | Jan 1 1900 12:26PM
01/17/2023 |  | RoutineScheduled |  | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Payment | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1250 | BIOCOIR |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | [] | [] | YES | [17 empty] | EVERYTHING WORKING PROPERLY. DISCHARGE PUMP AND FLOAT RECENTLY REPLACED, SEWAGE RECENTLY PUMPED, AND FIBER RECENTLY REPLACED. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/18/2023 | 11:50 AM
04/05/2023 | Alternative |  | 101-09-0405 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Faye | Taylor | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/10/2023 | Alternative | Routine/Scheduled | 093-16-0061 | Isle Of Wight | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Discharge | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service - lab samples obtained. Primary septic tank - normal level - recommend pumpout - effluent screen serviced. Aeration Tank - normal level - mixing present - compressor serviced. UV Disinfection - bulb and housing serviced. Pump Tank - float sensors, pump and controls operating. Discharge Point - clear of debris and free flowing. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/11/2023 | Dec 30 1899 7:30AM
05/25/2023 | Alternative | RoutineScheduled | 159-04-012 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Ecoflo |  | Gravity |  | Pad | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [18 empty] | Septic tank needs pumping. Pete moss needs replacement. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 12:00 AM
11/01/2023 | Alternative | RoutineScheduled | 136-18-0034 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | peat good, sludge okay, cleaned filters, system check okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/20/2023 |  | RoutineScheduled | 181-05-0105 | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NO | [17 empty] | The system did not need to be pumped. The blower and spin filters were cleaned. The control timer was not working at the time of inspection so a new timer was installed. There were no visible leaks in the drip field. The drip field was operating as designed. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/03/2023 | 10:30 AM
08/24/2023 | Alternative | RoutineScheduled Component Maintenance | 107-18-0099 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 | 1500 | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Septic Tank Pumped | This AOSS should now return to normal function after having provided the above state routine maintenance | 09/20/2023 | 01:07 PM
12/22/2023 | Alternative | RoutineScheduled | -STS-20548 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 01/02/2024 | Sample Chamber | 23.000000 | [5 empty] | Attached to this report |  | Septic Tank-3"sludge 4"scum/ Microfast-0"sludge/ Pump Tank-0"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-409 ETM-9h 48m/ Peak-0/ High-6/ On-1m 27s/ Off-6h/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/03/2023 | Alternative | Routine/Scheduled | 136-15-0333 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash Tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | 01:00 PM
11/06/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.300000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | 02:30 PM
06/16/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Puraflo |  | Pump | Pressure | Drip |  | 600.000000 | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 11:03 AM
03/10/2023 |  |  | 043-05-0100 | Clarke | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lord Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | LPD | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/14/2023 | 05:20 PM
03/15/2023 | Alternative | RoutineScheduled | 159-02-402 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | [null] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
12/05/2023 | Alternative | Routine/Scheduled | 228-11-0212 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | EZ Treat Sandfilter |  | Pump |  |  | UV |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 2.000000 | [13 empty] | Replaced UV control panel | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | Dec 30 1899 3:00PM
02/21/2023 |  | RoutineScheduled | SWP-04-661 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Panel was alarming when we arrived, biotube filter was clogged up causing low level alarm on recirc tank. Cleaned biotube filter, sheets and pump intake. Recirc tank needs pumping asap. Water softener connecter to sewer line, spoke to customer about it. Will send proposal for pump out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
04/13/2023 |  | RoutineScheduled | 101-04-0080 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Trenches | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/16/2023 | 12:00 AM
04/11/2023 |  | Pump-Out Only |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Pumped septic tank as recommended during last service event. Serviced effluent screen. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 07:45 AM
04/13/2023 |  | Reportable Incident | 2105-11-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced compressor. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 04:23 AM
04/25/2023 |  |  | {FIPSCode}-STS-14210 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 04/25/2023 |  | 7.970000 |  |  | 15.100000 |  |  | Will be sent separately |  | BOD: 7.97 TSS: 15.1 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | 12:00 AM
10/17/2023 | Alternative | Routine/Scheduled |  | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Annual Maintenance: -Septic Tank: Water level high upon arrival due to clogged effluent screen. Flushed and cleaned effluent screen and water level normal upon departure. Inlet tee appears to be intact. Not due for pump out. -Discharge/Pump Tank: Water level normal. Structural integrity of tank appears to be intact. Checked and confirmed pump is functioning properly. Checked and confirmed floats are functioning properly. -Peat Moss: Raked and tilled peat moss. Structural integrity of tank appears to be intact. Peat moss is in good condition. Structural integrity of tipping bucket appears to be intact. Checked and confirmed tipping bucket is functioning properly. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | Dec 30 1899 10:32AM
04/03/2023 | Alternative |  | 101-15-0114 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Danial | Mann | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/04/2023 |  | Routine/Scheduled | 228-18-0308 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/04/2023 | Jan 1 1900 12:30PM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-89663 | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Auxiliary Filter"] | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Auxiliary Filter"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Effluent is surfacing in the dispersal area due to broken plumbing near the air released valve. The drip dispersal laterals are settling. This area should be regraded, adding topsoil if necessary, and reseeded to establish good grass cover. Currently this area is inaccessible for mowing. This area must be maintained in a mowed condition. Owners also shared pictures of the pump line exposed due to erosion. Pump line needs to have sufficient soil cover to prevent freezing. The Advantex module has settled. It needs to be releveled. Additionally, the sewer line is coming into the tank uphill. This should be excavated and releveled. We are providing a copy of this report to Pruitt Contracting Groups so they can contact the installer for repairs. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/03/2023 | 05:43 AM
01/18/2023 |  | Initial Visit | 128-02-262 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 | Control Operation | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit - unknown service provider. Processing tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. System requires TLC - multiple leaks present - controls have issues. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/19/2023 | 08:15 AM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Module closest to the house is ponding. Module second from the house has severe roots. The tank structure appears to be good from the surface view through the risers. The distribution box appeared lower than dialflow openings. Drainfield lines are saturated but not surfacing. Recommend homeowner contact AOSE regarding options for replacement of peat and field. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/12/2023 | 03:17 AM
07/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
09/22/2023 | Alternative | Reportable Incident Component Maintenance | 175-19-0166 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced recirculation pump PF20-05-1-1. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
07/25/2023 | Alternative | RoutineScheduled | 12-163-0002 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Pad | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-10"sludge 6"scum/ Microfast ATU-18"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ Pump out required on the Septic-Microfast ATU Tank/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-495 ETM-38h 9m/ Pump2-480 ETM-36h 57m/ Peak-19/ High level-14/ No breakout or spongy areas on the LPD Pad Site. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/21/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | advantex needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
03/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Valve box riser cover needs to be replaced as it is broken. Low pressure does not appear to be functioning as designed. Homeowner is contacting company for repairs. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/04/2023 | 06:02 AM
05/17/2023 | Alternative | Routine/Scheduled | 136 05 264 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Real Estate inspection. Processing tank - rsv, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - plastic - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:45 AM
05/05/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Septic recirc zone 2 " Scum and 12-14" sludge- and 10" sludge on discharge zone. Recirc pump operational. Alarm operational. Tested All floats - all good. Cleaned Biofilter, flushed and brushed spray manifold, pulled and cleaned rsv, ran system in testmode while flushing.. Date history on computer is corrupt but operational, Pump run time indicates 279.9 hours and 52,961 cycles on recirc pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
01/26/2023 |  | Routine/Scheduled | 234-19-210 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | Jan 1 1900 12:10PM
06/28/2023 | Alternative | Pump-Out Only | 159-17-0096 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | UV | 450.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Pump out of trash tank side of AOSS only - as recommended during last service visit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/29/2023 | 06:30 AM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/08/2023 | Alternative | Routine/Scheduled | 161-STS-42790 | Roanoke City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/08/2023 | Dec 30 1899 3:00PM
11/20/2023 | Alternative | RoutineScheduled Component Maintenance | 107-17-0106 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | replaced buzzer | This AOSS should now return to normal function after having provided the above state routine maintenance | 01/15/2024 | 10:39 AM
09/29/2023 | Alternative | RoutineScheduled Component Maintenance | 179-11-0142-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. 35 psi. Clogged up septic tank filter, cleaned. 1 out of 8 spray heads was half clogged, cleaned. Everything working good. HL-347104. PEAK CNT-650201. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
11/09/2023 | Alternative | RoutineScheduled | 2017-143-0200 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/27/2023 | Alternative | RoutineScheduled | 10-163-0063 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Advantex AX20 |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","Effluent Screens","Control Operation","Dispersal System Operation","Recirculation Pump"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/25/2023 | Alternative | Reportable Incident | 175-18-0523 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Recirculation Pump","SludgeScum Accumulation"] | ["Recirculation Pump"] | [18 empty] | Alarm Service Call Only: Found the Step 30 Recirculation pump was faulty. Replaced with a Zoeller Turbine pump per EZ-Treats recommendation. Counts: Pump-0122847 ETM-0498460/ Recirculation tank has 12"sludge and 3"scum recommend pump out. To be pumped out on 10/6/2023 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
09/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 4:00PM
01/17/2023 |  | RoutineScheduled | 177-15-0199-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Clogged media, recommend chemical clean. Recommend to dig up dbox to camera snake line between tank and dbox also would be good to check drainfield lines. Blower pulling 3.2 amps. Customer added vent back to outlet lid. Sewer still not fixed but not clogged up. Will send proposal. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
10/11/2023 | Alternative | RoutineScheduled | 18-142-0187 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/06/2023 |  | RoutineScheduled | SP-05-05 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 1-9 0-5 | 0-2 | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear |  |  | 18.000000 | [11 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/06/2023 | 11:00 AM
04/19/2023 |  | RoutineScheduled | 179-STS-92102 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation" ,"Recirculation Pump"] | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation" ,"Recirculation Pump"] | NA | None | Clear | [5 empty] | 04/19/2023 | Pump Chamber | [6 empty] | Will be sent separately | Inspected | Annual inspection. Collected BOD sample from drip pump tank. Owners do not use much water. Recirc timer enabler float was open on arrival. If BOD sample does not pass, an adjustment to the ratio box may be needed. The field flush valve was stuck open due to residual peat fines being stuck under the valve diaphragm (a common problem when a peat pretreatment is used in front of a drip system). High level count in drip panel is at 162. Owners said no new alarms since converting to EZ Treat system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
08/14/2023 | Alternative | RoutineScheduled | 139-12-0019 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | Septic needs to be pumped out. Customer to schedule. Intermittent alarm per customer...possible float issue | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/14/2023 | 12:00 AM
12/07/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/27/2023 | 01:45 PM
12/08/2023 | Alternative | RoutineScheduled | 175-19-0030 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Advantex Recirculation Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | [17 empty] | Septic Tank-12"sludge 1"scum/ Pump Tank-12"sludge 0"scum/ No pump out needed at this time but may be necessary by next year/ Repaired recirculation pipe/ Recirculation pump intake cleaned/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump-1464h ETM-1876h 57m/ High-25/ On-2m 47s Off-3h 52m/ Watermeter-0,574,099.3/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/22/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/11/2023 | 01:03 PM
01/18/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [7 empty] | 01/18/2023 |  | 42.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
12/28/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-88336 | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. System was on high level due to clogged recirc pump intake being clogged plus a couple spray nozzles, cleaned all and got it out of high level. Recommend getting recirc tank pumped due to so much trash in tank. Garbage disposal being used, recommended not to use. 3 top lines ponding need to camera snake them on a dry week. line number 4 was bleeding due to taking more water, adjusted dial flows should dry out. will send proposal for installing a sim-tech filter to recirc pump and to camera snake lines. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 01/02/2024 | 07:39 AM
06/07/2023 | Alternative | Routine/Scheduled | 18-142-0184 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Treatment Module - recirc - recirc pump, media drapes & spray grid serviced. Treatment Module - discharge - float sensors, pump and controls operating. Pumps to community pump station and absorption field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | Dec 30 1899 11:00AM
01/03/2023 |  | Routine/Scheduled | {FIPSCode}-STS-5319 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2023 | Jan 1 1900 2:35PM
07/20/2023 | Alternative |  | 127-STS-31720 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Clearstream |  | Pump | Pressure | Drip |  |  | [] | ["Control Operation","BlowerCompressorAerator Operation","Distribution Pump Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | 12:00 AM
03/15/2023 | Alternative | RoutineScheduled | 159-17-0216 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Aquasafe |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | [] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
07/31/2023 | Alternative | RoutineScheduled | 04-177-1258 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 | 1000 | Retrofast |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Septic | [6 empty] | 07/31/2023 | [7 empty] | Will be sent separately | Inspected | - collected sample onsite - installed riser onsite | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/03/2023 | 12:00 AM
03/07/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | A septic inspection of a conventional pump system. The state requires that every 5 years the septic tank must be pumped out and filed with the state and county. The septic control panel in an interior demand dose. There is 1 cleanout near the house. We camera snaked the sewer line and it was clear to the septic tank. The tanks are behind big boxwood bushes. The septic tank has a plastic riser on the inlet side of the tank. The tank was at working level when opened. The septic tank was pumped and no visible leaks or cracks were seen. The pump tank has a plastic riser on the outlet side. When lid was removed we noticed the alarm float had been pulled up on top of float tree. We tested all 3 floats all were working. At this time not sure reason for it to have been put there. The 6 port concrete surge box was dug up it was 4" under the ground. It was full of mud and roots and will need replaced. The 10 port concrete d-box was dug up it was 4" under the ground. Lid is broken and box is deteriorating. All 7 header lines were clogged with roots. Header lines will need replaced. Drain field was probed and was dry. At time of inspection the septic system was not in working condition. This inspection does not guarantee the life of any component or the drain field | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
07/27/2023 | Alternative | RoutineScheduled | 109-16-0195 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 300 | Best1 |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Control Operation","BlowerCompressorAerator Operation"] | ["Effluent Screens","Control Operation","BlowerCompressorAerator Operation"] | NA | [16 empty] | Inspected | Replaced blower motor, cleaned clogged effluent filter. This fillter needs cleaned every 3 months to prevent backups. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/30/2023 | 09:30 AM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Fittings that connect blower to downshaft are damaged | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
03/29/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/21/2023 | 03:35 PM
07/26/2023 | Alternative | RoutineScheduled | 031-STS-24458 | Campbell | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Central | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1500 | Septic Tank | Aquaklear | Gravity | Gravity | Discharge | UV | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Other"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Other"] | NA | None | Clear | 7.100000 |  |  |  |  | 07/26/2023 | Sample Tap | 4.200000 |  | 14.000000 | 8.000000 | 33.300000 | 3.900000 | Will be sent separately |  |  | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 08/21/2023 | 03:30 PM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/02/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/05/2023 | Alternative | RoutineScheduled | 067-STS-38687 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 2000 | BioMicrobics MicroFast |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | Second Quarter 2023 inspection. 11" solids in septic tank. 10" solids in MicroFast septic tank. 13" intreatment unit. 2" solids in discharge pump tank. Aeration is adequate. No sign of smell that has been an issue. Cleaned blower air filter. There is no pump out required at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | 07:03 PM
08/17/2023 | Alternative | Routine/Scheduled | 08-120-0494A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Hoot |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/17/2023 | Dec 30 1899 2:43PM
05/03/2023 | Alternative | Routine/Scheduled | 093-14-0064 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/03/2023 | Dec 30 1899 10:16AM
12/05/2023 | Alternative | Routine/Scheduled | 166-12-058 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2500 | Clearstream |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 40.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 07:21 PM
07/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 3.000000 |  | Biomicrobics MicroFAST | Whitewater ATU | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
03/14/2023 |  | Routine/Scheduled | {FIPSCode}-STS-3222 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Hoot |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/14/2023 | Jan 1 1900 3:00PM
04/21/2023 | Alternative | RoutineScheduled | 154-03-0453 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We strongly recommend removing the bushes that are near the risers & access pipe to ensure access to the system and prevent root intrusions into the tanks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
05/31/2023 | Alternative | RoutineScheduled | VAG408436 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  |  | Discharge | UV |  | ["Septic Tank Baffles"] | ["Septic Tank Baffles"] | [18 empty] | No disharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/31/2023 | 12:00 AM
09/07/2023 | Alternative |  | 033-08-0103-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
08/24/2023 | Alternative | Reportable Incident |  | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | System in alarm / having issues since pumpout. Trash Tank - normal level Aeration tank - normal level - mixing present - compressor serviced. UV Disinfection - Norweco AT1500 - serviced bulb and housing. Pump Tank - float sensors, pump and controls operating. Drip Field - headworks serviced - field flushed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | Dec 30 1899 7:45AM
05/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | pump is not working will need replaced and pump tank will need pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
01/23/2023 |  | RoutineScheduled |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith |  |  | Orenco Advantex | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/27/2023 | 07:00 PM
06/05/2023 |  | Routine/Scheduled | 04-142-0297 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1250 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | Cleaned effluent filter. Raked Peat. Tested floats and pump. System appears to be operating normally. There are some roots coming through the riser on the septic tank and around the force main of the pump tank, we used the hydroprobe to test watertightness and found no leaks at this time but could be a problem in the future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | Jan 1 1900 10:23AM
10/12/2023 | Alternative | Routine/Scheduled | 041-STS-260606 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] |  | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/01/2023 | Dec 30 1899 1:00PM
03/14/2023 |  | Follow-Up | 175-05-0899 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced timer enable float. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
06/13/2023 |  |  | SP-03-187 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
07/05/2023 | Alternative | RoutineScheduled Component Maintenance | 177-16-0364-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
05/22/2023 | Alternative | RoutineScheduled | SD-05-268 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Air filter and brush filters were replaced by others, Cleaned both this year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
10/23/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/23/2023 | Dec 30 1899 1:55PM
08/07/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | Western Virginia Water Authority | 1942001145 | Michael | Doss |  |  |  |  | Gravity | Pressure | Drip | UV |  | ["None"] | ["None"] | YES | None | Clear | [5 empty] | 08/07/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | 12:35 PM
06/28/2023 | Alternative | Routine/Scheduled | 234-16-443 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | Replaced UV Bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | Dec 30 1899 11:40AM
11/28/2023 | Alternative | Initial Visit | 228-19-0052 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 2.000000 |  | 26.000000 | [5 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Replaced the UV light bulb, replaced the UV circuit board, and replaced the UV cord. There is no weir filter - needs to be one. Need to pump and clean the pump tank, replace the gauge on the return, set pressures, and perform a draw down test. Could not locate vacuum breakers - no valve boxes. The whole backyard is wet - need to keep an eye on the drainfield once it dries up. The timer is set to 25 minutes every 1 hour. Took initial BOD and Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | Dec 30 1899 4:30PM
04/06/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | MicroFast | Pump | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | The septic tank has 3' overall depth with 1" of scum and 8" of sludge. The blower, blower alarm, pump, and pump alarm are all working. Cleaned the filter on blower. D-box was uncovered. D-box is in good shape with no signs of deterioration. Speed levelers in the d-box are there and look good. Inspected the drainfield area. The area is dry with no signs of failure. Everything is working as designed. Pump run time - 132hr- 21 min. Doses - 5991. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/06/2023 | 01:30 PM
03/31/2023 |  | Routine/Scheduled | {FIPSCode}-STS-5536 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/31/2023 | Jan 1 1900 11:25AM
09/15/2023 | Alternative | Follow-Up Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed D 80 Compressor & PUTURB20FE05-P4 effluent pump & repaired leak in hydraulic unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
03/23/2023 | Alternative | Follow-Up | 07-160-0147 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [18 empty] | - replaced Tuff-tite lid | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/27/2023 | 12:00 AM
05/10/2023 |  | RoutineScheduled |  | Buckingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Septic | Advantex | Gravity | Gravity | Discharge | UV | 350.000000 | ["Effluent Screens"] | ["Effluent Screens","SludgeScum Accumulation","Disinfection","Recirculation Pump"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | Jan 1 1900 7:15AM
04/12/2023 |  | RoutineScheduled | 175-18-0298 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Bio Barrier | none | Gravity | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | MicroFast needs pumping. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/02/2023 | 04:23 AM
12/14/2023 | Alternative |  | 14-100-0361 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
09/19/2023 | Alternative | RoutineScheduled | 182-10-0105 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/19/2023 | 12:00 AM
11/06/2023 | Alternative | Routine/Scheduled | 151-18-0051 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 85.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | 01:25 PM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/27/2023 | Alternative | Reportable Incident | 166-12-104 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Replaced failed compressor. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
11/23/2023 | Alternative | RoutineScheduled |  | Page | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Air pipe repaired. All tanks pumped out | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/23/2023 | 12:00 AM
07/05/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-89593 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | 11:26 AM
12/13/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 09:45 AM
02/16/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/01/2023 | Dec 30 1899 2:21PM
02/27/2023 |  | RoutineScheduled | 195-Discharge-34616 Fleet Rd. | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/27/2023 | 12:00 AM
07/05/2023 | Alternative | RoutineScheduled Component Maintenance | SWP 03-769 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | There may be trees growing along the upper side of the dispersal area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
05/18/2023 | Alternative | Reportable Incident | 550-STS-6944 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream, cleaned the disc filter, and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed a filter in the septic tank. Need to install a buzzer. Meet with the pumping company and pumped and cleaned the Clearstream tank and pump tank. Disconnected the pressure switch on the aerator and disconnected the UV power and alarm due to the tanks being pumped. Need to hook up the pressure switch, UV power and UV alarm once there is enough water in the tanks. The timer is set to 8 minutes every 2 hours | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/18/2023 | Dec 30 1899 12:30PM
05/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | the norweco tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
07/17/2023 | Alternative | RoutineScheduled Component Maintenance | SSHN-9LCKJ2 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump" ,"Effluent Screens"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
08/10/2023 | Alternative | RoutineScheduled | 107-18-0205 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter | [9 empty] | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
11/01/2023 | Alternative | RoutineScheduled | VAG401352 | Bath | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Gravity | Discharge | Chlorination |  | ["None"] | ["None"] | NA | Musty | Cloudy | [15 empty] | no discharge during visit . clorine in dispenser | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
06/13/2023 | Alternative | RoutineScheduled Component Maintenance | 154-03-0062 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
05/01/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Issues with the distribution boxes were fixed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/07/2023 | Alternative |  | ST-05-162 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/15/2023 |  | RoutineScheduled | 2115-06-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura flo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | 6.600000 |  |  | 1.700000 |  | 06/01/2023 | Sample Chamber | 18.000000 |  |  | 15.200000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/11/2023 | 12:00 AM
07/15/2023 | Alternative | RoutineScheduled | 11-100-0287 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | BIOCOIR |  | Pump | Pressure |  | UV | 300.000000 | [] | [] | YES | [17 empty] | INSTALLED A NEW UV LIGHT UNIT AND VALVE BOX FOR DRAIN FIELD MOUND. EVERYTHING WORKING AS IT SHOULD. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/14/2023 | 01:30 PM
11/20/2023 | Alternative | Routine/Scheduled | 08-120-0457A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Hoot |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/20/2023 | Dec 30 1899 9:31AM
09/01/2023 | Alternative | Routine/Scheduled | 14-120-0178AR | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Bionest |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/01/2023 | Dec 30 1899 1:33PM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | Delta Environmental Products, DF Series | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | One air release valve is not functioning properly. Corrections in progress. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/11/2023 | Alternative | RoutineScheduled Component Maintenance | 175-16-0378 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Compressor & effluent needs replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 09/15/2023 | 02:41 PM
11/20/2023 | Alternative | Reportable Incident Component Maintenance | 177-STS-90219 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | High level alarm for both tanks. Steady inflow obseved at septic inlet tee. Advised owner how to check toilets. She found two with fill valves improperly adjusted and turned them off until she got help correcting them. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
08/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
09/08/2023 | Alternative | RoutineScheduled | 163-STS-333731 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | AdvantexAX20RT | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The recirculating and discharge pumps were both pulled and cleaned. The textile sheets were sprayed off. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/26/2023 | 04:20 PM
01/06/2023 |  | RoutineScheduled | 099-14-0049-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Effluent Screens"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Replaced control panel during this inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
11/13/2023 | Alternative | RoutineScheduled | 04-184-5004 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 15 Chlorine 18 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/13/2023 | 12:00 AM
02/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
10/12/2023 | Alternative | Reportable Incident Component Maintenance | 175-03-0523 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced textile sheets in Advantex unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
11/02/2023 | Alternative |  | 177-18-0083-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/04/2023 | Alternative | RoutineScheduled | 08-125-089 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Pump | Gravity |  | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection"] | ["BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | 7.900000 | 21.100000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 11/15/2023 | 02:02 PM
03/21/2023 |  | Routine/Scheduled | 085-STS-32139 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip | UV | 450.000000 | Distribution Pump Operation | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | 180 day service inspection. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. UV - bulb and housing serviced. Pump Tank - float sensors, pump and controls operating - minor surfacing (broken plumbing) noted outside of pump tank riser. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/22/2023 | Jan 1 1900 9:00AM
11/13/2023 | Alternative |  | 132-07-0051 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Robert | Allen | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/02/2023 | Alternative | Routine/Scheduled | 13-163-0140 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Found above normal level, 1in of sludge and less than 1in of solids. Pulled and cleaned filter. -Aeration: Found at normal level, less than 1in of sludge and solids. Pulled and cleaned diffuser and weir. High level alarm float working. -Air Pump/Blower: 120 volts. Air pressure sensor working as it should. Cleaned air filter. -Control Panel: 120 volts. Air pump pulled 1.3 amps. Audio and visual alarms working as they should. -Distribution Box: Normal level, 3 lines balanced and taking water. Dbox lid has hairline crack that you can only see from the bottom. -Drain Field: No surfacing in drainfield area Repair: -Installation of a 24" riser lid | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | Dec 30 1899 12:19PM
05/27/2023 |  | RoutineScheduled | 067-STS-38685 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | Modified Extended Aeration |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | YES | [16 empty] | Pumped Out | Total flow to drain fields May 2023 -189,320 gallons. Average 6,528gallons per day. All aspects of the system are operational. Wasting of settled mixed liquor from the clarifier to the digester and decanting of supernatant from digester are occurring regularly. Digester pumped out on 5-27-2023. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/02/2023 | 07:03 PM
03/30/2023 |  | RoutineScheduled |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 3.000000 | 1500 | 2-6 0-12 | 0-3 | Pump | Pressure | Drip | UV |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","Disinfection"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","Disinfection"] |  | None | Clear |  |  | 16.000000 | [11 empty] | Inspected | soft spot in Field looks better | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 04:00 PM
10/01/2023 | Alternative | Routine/Scheduled | 041-STS-261184 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/01/2023 | Dec 30 1899 12:00PM
08/17/2023 | Alternative | Routine/Scheduled | 041-STS-257885 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/17/2023 | Dec 30 1899 2:00PM
03/28/2023 | Alternative | Routine/Scheduled | S 800-17-0074 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | Dec 30 1899 3:30PM
03/23/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
01/11/2023 | Alternative | RoutineScheduled | 061-17-095 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | septic | Microfast | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | 10:15 AM
03/27/2023 |  | Routine/Scheduled | 085-STS-34627 | Hanover | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1250 | Orenco Advantex |  | Gravity | Gravity | Discharge | UV | 350.000000 | Disinfection | Disinfection | NO |  |  | 6.500000 | 4.100000 |  |  |  | 03/27/2023 | Pump Chamber | 3.000000 |  |  | 1.300000 |  |  | Will be sent separately |  | Ecoli Sample Lab Test results = 1.0 MPN/100 mL. The Orenco local representative was met onsite to advise on uv ballast securement. He has ordered the correct part. Once we have received the part we will return to install. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/10/2023 | Jan 1 1900 12:29PM
04/19/2023 | Alternative | Reportable Incident | 104-10-0160 | Amherst | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Central | Acres of Virginia, Inc. |  | Melvin | Collins | 1.000000 | 1000 | Septic Tank | Microfast | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation"] | [] | [18 empty] | Clients alarm is going off. After a visit to home found the regenerative blower is not functioning. Gave estimate to client to fix. Customer purchased new pump and fixed themselves. A follow up inspection will be performed at a later date. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/10/2023 | 10:30 AM
11/17/2023 | Alternative | Routine/Scheduled | S 800-13-0238 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 1 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/17/2023 | Dec 30 1899 1:45PM
09/20/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
09/18/2023 | Alternative | RoutineScheduled | 015-STS-335675 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 RT |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/18/2023 | 12:00 AM
08/16/2023 | Alternative | Reportable Incident |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Multiflo FTB | [6 empty] | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/12/2023 | 02:26 PM
12/29/2023 | Alternative | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/29/2024 | 02:28 PM
11/03/2023 | Alternative | RoutineScheduled | 02-197-A6 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination | [22 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/10/2023 | Alternative | RoutineScheduled | 12-120-0099AExt. | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1750 | 1000 | 750 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","SludgeScum Accumulation","Distribution Pump Operation"] | YES | Pungent | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/10/2023 | Dec 30 1899 7:00PM
03/13/2023 |  | RoutineScheduled | 17-100-0507 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | 12:00 AM
05/22/2023 | Alternative | RoutineScheduled | SD-11-258 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | [8 empty] | 62.500000 | ["Attached Growth Medium","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/22/2023 | 05:45 PM
06/14/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Gravity | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | Dec 30 1899 12:05PM
01/20/2023 |  | RoutineScheduled | 175-04-0666 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Force main broken outside of pump tank. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/02/2023 | 11:08 AM
12/14/2023 | Alternative | Routine/Scheduled | C 800-17-0078 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | Dec 30 1899 2:10PM
12/04/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/19/2024 | 12:00 AM
08/23/2023 | Alternative | Routine/Scheduled | 151-11-0166 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 35.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/23/2023 | 05:21 PM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Middle Module is fully saturated and has standing water to the lip of the module | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/04/2023 | 06:02 AM
02/15/2023 | Alternative | Routine/Scheduled | 2009-126-155 | Dinwiddie | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/15/2023 | Dec 30 1899 10:28AM
01/26/2023 |  | Routine/Scheduled | 234-08 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | Jan 1 1900 1:20PM
10/26/2023 | Alternative | RoutineScheduled Component Maintenance | SD-96-497 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection and maintenance completed today. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
09/21/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/21/2023 | Dec 30 1899 7:55AM
08/04/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-89031 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Media has filamentus bacteria but is not plugged and treatment looks very good. Blower 2.80 amps. Pump rate slowed down is below 20 gallons per minute, recommend to upgrade pump if it fails or it slows down more. Increase run time to get rid of full dose, new run time 5m7s. Drain field is overgrown, left note to customer to mow it. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
09/18/2023 | Alternative | RoutineScheduled Component Maintenance | 182-15-0160 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 09/18/2023 |  | 68.000000 | [5 empty] | Will be sent separately | Inspected | Lid cracked repaired recommend riser on septic tank | This AOSS should now return to normal function after having provided the above state routine maintenance | 10/13/2023 | 01:07 PM
10/05/2023 | Alternative | RoutineScheduled Component Maintenance | 175-02-0864 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
12/08/2023 | Alternative | RoutineScheduled | 06-197-A8 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.000000 | 4.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/08/2023 | 12:00 AM
01/30/2023 |  |  | 19-142-0050 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | EZ Treat | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | 12:00 AM
08/23/2023 | Alternative | RoutineScheduled Component Maintenance | 061-17-219 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["SludgeScum Accumulation" ,"Distribution Pump Operation"] | ["Distribution Pump Operation" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | EZ Treat pump tank needs pumping New Step 30 115 volt EZ Treat Pump | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 08/29/2023 | 03:58 AM
01/18/2023 |  | Routine/Scheduled | 800-STS-14317 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Raised the aerator. The timer is set to 1.5 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | Jan 1 1900 3:45PM
05/25/2023 |  | Routine/Scheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Aquarobic Mini Plant |  | Pump | Pressure | Mound |  | 450.000000 | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/01/2023 | 11:04 AM
02/14/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
04/25/2023 |  | RoutineScheduled | {FIPSCode}-STS-12817 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Chlorination |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 05/15/2023 | 12:48 PM
01/04/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced pressure guage | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
01/04/2023 |  | RoutineScheduled | {FIPSCode}-STS-24675 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/04/2023 | 12:00 AM
09/08/2023 | Alternative | RoutineScheduled | 09-125-077 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 3 - Blue Crystal tablets installed 14 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/08/2023 | 12:00 AM
06/29/2023 | Alternative | RoutineScheduled | SD-10-169 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Septic tank | Pura-flo | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation","Effluent Screens"] | ["SludgeScum Accumulation","Effluent Screens","Attached Growth Medium","Other"] | YES | Musty | Clear | [14 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | 03:20 PM
12/29/2023 | Alternative | RoutineScheduled | 19-142-0129 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/12/2024 | 12:00 AM
02/28/2023 | Alternative | Pump-Out Only | 087-STS-6137 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/06/2023 | Alternative | Reportable Incident Component Maintenance | 175-16-0436 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | High level alarm in both tanks. Drip pump would run on schedule, but no effluent being delivered to the drainfield because the Siemens Logo processor was locked up. Contacted Orenco technical support, then ordered a micro SD card with a firmware update. Cycling the control breaker temporarily restored panel operation. Return trip made and update completed (firmware 1.81.03). Put panel in test mode and let system run some shortened cycles to verify operation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
05/09/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1200 |  |  | Pump |  | Trenches | Not Applicable | 600.000000 | [] | [] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | Dec 30 1899 3:30PM
03/21/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1875 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/08/2023 |  | RoutineScheduled |  | Page | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 1.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/22/2023 | 12:00 AM
10/26/2023 | Alternative | RoutineScheduled Component Maintenance | SD-05.225 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation"] | ["Control Operation" ,"Distribution Pump Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Considering its age, the peat is in very good shape. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
09/13/2023 | Alternative | Initial Visit | 157-17-0123 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the aerator. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. Replaced the UV light bulb and replaced the UV light cord. The timer is set to 6 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/13/2023 | 05:30 PM
02/15/2023 |  | RoutineScheduled | 153-STS-20263 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["Disinfection","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | [7 empty] | 03/02/2023 | Sample Chamber | 34.000000 |  | 1600.000000 |  |  |  | Attached to this report |  | Septic-3"sludge 2"scum/ Microfast-0"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working properly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-302 ETM-46h 51m/ Peak-3/ High-19/ Watermeter-0,014,888.4 On-11m Off-2h 40m/ Drip Counts: Zone1-89 FF-13/ Zone2-89 FF-11/ Zone3-85 FF-14/ The UV-Light was faulty and repaired during inspection, will return at a later date to take a sample/ No breakout or spongy areas on the drip field and dosing properly. Returned on 3/2/2023 for the sample. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/23/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced d-box backfilled. Septic system is in working condition at this time | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
10/25/2023 | Alternative | RoutineScheduled | 109-11-0246 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1000 | Multiflo |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["None"] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | 12:00 PM
05/05/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Aqua Klear |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge level- trace amount of sludge in treatment, Good aeration, Discharge 1" scum and 16" sludge- Does not need pumping, cleaned airfilter. Good aeration. Clear airfilter and Effluent filter. System is operational | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
06/05/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/01/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.010000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/01/2023 | 01:30 PM
02/24/2023 |  |  | 033-17-0092-SR | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
07/31/2023 | Alternative | RoutineScheduled | 179.05.140 | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | replaced alarm float | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/28/2023 | Alternative | RoutineScheduled | 175-02-0035 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic/ Aquarobic Pump Tank |  | Pump | Pressure | Mound | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic-Aquarobic Tank-0"sludge 0"scum/ Tanks were pumped out prior to inspection/ Blower air filter cleaned and blower is working properly/ Controls, pump, floats and alarms are functioning properly/ No breakout or spongy areas on the Aquarobic Mound area and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/25/2023 |  |  | 2009-143-0118 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 2000 | 1000 | 1000 | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Level Sensor Operation","Distribution Pump Operation"] |  | Septic | Discolored | 6.000000 |  | 6.000000 | [13 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/25/2023 | 12:30 PM
06/06/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | Shared system with 187 Shady Oak Ln | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/06/2023 | 12:00 AM
01/11/2023 |  | Follow-Up | 177-STS-87529 | Spotsylvania | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Repaired tree damaged control panels. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
07/18/2023 | Alternative | RoutineScheduled | 109-06-0493 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | Trouble Shooting .Replaced 2 floatd and ran new wire above grade to test and see if issue clears. Ran in test mode system appear to work as it should. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/30/2023 | 09:30 AM
11/15/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0266-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Distribution Pump Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Distribution Pump Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Conduit settled bad and broke out the bottom of the control panel. Patched panel, dug up and raised flex conduit, reconnected conduit to panel. Tested floats and pump again. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
06/22/2023 | Alternative | Reportable Incident | 228-15-0026 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/22/2023 | Dec 30 1899 7:00AM
07/26/2023 | Alternative | RoutineScheduled | 121-STS-11934 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","SludgeScum Accumulation"] | [8 empty] | 07/26/2023 | Pump Chamber | [6 empty] | Will be sent separately |  | - tuff tite riser and lid need to be repaired/replaced due to crack in lid and warp in riser ring - pump chamber shared with neighboring house | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/14/2023 | 12:00 AM
08/02/2023 | Alternative | Routine/Scheduled | 132-07-0087 | Fluvanna | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Blue Ridge | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Filters cleaned, manifold brushed and flushed. Replaced discharge floats. Alarm float was bad and middle float was intermittently working. System should return to normal operation. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/02/2023 | 09:48 AM
04/04/2023 |  | Routine/Scheduled | 2006-143-0205 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | NO | [17 empty] | Checked system operation and system appears to be operating normally. Averaged. 3 overrides per day. Replaced vents on both units | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | 11:40 AM
03/25/2023 |  | RoutineScheduled | 133 07 0946 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Ortenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. Septic tank - 2" crust, 2" of solids in bottom. 4" in discharge pump tank. Flushed treatment unit spray manifold. Cleaned recirculation pump basket filter. Cleaned solids that were blocking several spray heads. Sprayed off treatment unit fabric sheets. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/09/2023 | 12:00 AM
04/14/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
12/11/2023 | Alternative | RoutineScheduled Component Maintenance | 179-18-0002-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | There are roots growing in the first, fourth and sixth header lines. This is not currently showing signs of being a problem, but water is not flowing evenly to the drainfield lines. We would recommend excavating by machine in the spring to remove roots and repair or replace header lines as necessary to restore even flow to the drainfield lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/15/2023 | Alternative | RoutineScheduled Component Maintenance | 2032-96-153 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity |  | Chlorination |  | ["Control Operation" ,"Disinfection"] | ["Disinfection"] | NA | Septic | Cloudy | 7.200000 | [12 empty] | Will be sent separately | Inspected |  | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 07/07/2023 | 06:25 AM
06/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | [7 empty] | 06/13/2023 | Sample Chamber | 4.000000 |  | 1600.000000 |  |  |  | Attached to this report |  | Septic Tank-2"sludge 0"scum/ Microfast-0"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ Blower air filter cleaned and blower working correctly/ Controls, floats, pump and alarms functioning properly/ Counts: Pump-2901 ETM-821h 56m/ Peak-16 ETM-122h 43m/ Watermeter-0,347,859.8/ uv-light sleeve cleaned/ No breakout or spongy areas on the drip field. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend replacing discharge pump chamber lid. Peat is showing signs of its age. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/01/2023 | Alternative | Routine/Scheduled | 157-89-328 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Pump | Pressure | Mound | Not Applicable | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Primary septic tank - normal level Pump Tank - float sensors, pump and controls operating. Mound / LPP - no indications of surfacing or bleed out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/02/2023 | 07:30 AM
06/30/2023 | Alternative |  | 149-STS-10671 | Dinwiddie | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1750 | 1000 | 750 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation","Effluent Screens","Level Sensor Operation","Distribution Pump Operation","Recirculation Pump"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | 12:00 AM
01/06/2023 | Alternative | RoutineScheduled | SD-09-310 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | PuraFlo |  | Pump | Gravity | Trenches | Not Applicable | 62.500000 | [] | ["Attached Growth Medium","SludgeScum Accumulation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/07/2023 | 08:15 AM
06/20/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-27007 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 2.000000 | 2000 | Puraflo |  | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [17 empty] | Pump alarm checked. Pump operation checked. Peat checked. System appears to be operating normally. Etm 542.11, ct 27593. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | Dec 30 1899 10:42AM
04/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/15/2023 | Alternative | RoutineScheduled Component Maintenance | 175-16-0065 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | 01:58 PM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
09/21/2023 | Alternative | RoutineScheduled Component Maintenance | 2032-96-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity |  | Chlorination |  | ["Control Operation" ,"Disinfection"] | ["Control Operation" ,"Disinfection"] | NA | Musty | Clear | 7.600000 | 29.600000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 10/16/2023 | 12:58 PM
08/31/2023 | Alternative | Reportable Incident | 234-16-118 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/31/2023 | Dec 30 1899 3:30PM
12/05/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | Dec 30 1899 7:30AM
04/18/2023 |  |  | 2018-143-0014 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 2.000000 |  | Advantex |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Recirculation Pump","Control Operation","Dispersal System Operation","Level Sensor Operation","Distribution Pump Operation"] | NA | Musty | Cloudy | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/18/2023 | 12:00 AM
05/12/2023 | Alternative | RoutineScheduled | RRAR-9ZHLSM | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Whitewater ATU |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge levels-- Septic tank no Access- Treatmentunder 1-2" Scum on top and trace of sludge on bottom in Septic tank-Paul at affordable septic pumped following my visit last year. system much improved, reccomend to add a full size accses riser to tanks, Cleaned blower air filter, Good aeration in treatment. Drainfield looked unremarkable. Treatment tank is slightly sunken in and reccomend to regrade soil near top/lid to divert rain runoff from leaking into system causing premature failure of drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | Jan 1 1900 9:30AM
02/07/2023 | Alternative | RoutineScheduled Component Maintenance | {FIPSCode}-STS-16479 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
08/16/2023 | Alternative | RoutineScheduled Component Maintenance | 154-10-0221 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Recirculation Pump" ,"Level Sensor Operation"] | ["Control Operation" ,"Recirculation Pump" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection and maintenance completed today. Replaced damaged Advantex vent cap and removed debris from the vent pipe. Redundant off float was stuck partially on in the recirc tank, replaced it. Lake house gets very little use. Tanks are not even close to needing a pump-out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
05/12/2023 |  | RoutineScheduled | 177-18-0199-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
07/17/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | 12:27 PM
10/07/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20RT |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","SludgeScum Accumulation"] | ["Auxiliary Filter","SludgeScum Accumulation"] | NA | [16 empty] | Pumped Out | Annual inspection. Homeowner is selling home soon and requested a pump out. The septic tank and treatment unit were pumped out on 10-25-2023. During inspection - Cleaned septic solids filter. Cleaned drip manifold spin filter. Flushed treatment unit spray manifold. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 07:03 PM
08/11/2023 | Alternative | Follow-Up Component Maintenance | 175-06-0218 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced enable & ATU floats. Removed tree roots from distribution box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
01/20/2023 |  | Follow-Up | 07-100-0777 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1250 | Septic Tank | Ecoflo ST 650 | Pump | Pressure | Pad | Not Applicable | 600.000000 | ["Attached Growth Medium"] | ["Attached Growth Medium"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | 03:15 PM
09/06/2023 | Alternative | RoutineScheduled | 12-192-126 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | WHITEWATER |  | Gravity | Gravity | Discharge | UV | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Level Sensor Operation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/06/2023 | 12:00 AM
07/05/2023 | Alternative | Routine/Scheduled | 228-09-0208A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | Dec 30 1899 9:34AM
03/17/2023 |  | Routine/Scheduled | {FIPSCode}-STS-2537 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/17/2023 | Jan 1 1900 10:00AM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/05/2023 |  | Pump-Out Only | 175-08-0349 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | pumped out septic and pump tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | 11:00 AM
04/13/2023 |  | RoutineScheduled | 02-192-142 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 12:00 AM
03/17/2023 |  |  | 2015-143-0045 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
04/27/2023 |  |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/16/2023 | Alternative | Routine/Scheduled | 073-STS-92610 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Found above normal level due to clogged bio conetic Filter. Found 18in of sludge and less than 2in of solids -Discharge/Pump Tank: Found at normal level, fou d less than 1in of solids and sludge. Tested floats and pump. All working as they should. -Aeration: Found above normal level due to clogged bioconetic filter. Found less than 1in of sludge and solids. Pulled and cleaned debris off aspirator. Aspirator pulled 4.1 amps BIOCONETIC FILTER, pulled and cleaned filter and filter housing -Control Panel: 120 volts, audio and visual alarms working as they should. Pump pulled 9.2 amps. -Distribution Box: Found at normal level, found 6 lines balanced taking water. Removed grass roots on site -Drain Field: No signs of surfacing in drainfield area | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 09:32 AM
02/21/2023 |  |  | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
01/13/2023 |  | Routine/Scheduled | 147-14-0104 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Multiflo FTB |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Aeration Unit - socks in fair condition - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | Jan 1 1900 12:00PM
06/29/2023 | Alternative | RoutineScheduled Component Maintenance | SD-04-516 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter"] | ["Effluent Screens" ,"Auxiliary Filter"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
06/19/2023 | Alternative | Routine/Scheduled | 04-142-0060 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Real Estate Inspection - Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump tank - float sensors, pump and controls operating. DBox - intact - all laterals accepting effluent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | Dec 30 1899 11:30AM
02/28/2023 | Alternative | RoutineScheduled | 047-16-224 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2000 | septic | EZ-Treat | Gravity | Pressure | Discharge | UV |  | [] | [] | YES | None | Clear | [15 empty] | No Discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/07/2023 | 09:40 AM
02/02/2023 |  | Routine/Scheduled | 2009-143-0110 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Hoot |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash Tank - normal level - recommend pump out. Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - sensor probe operating, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | 07:45 AM
05/18/2023 |  | Routine/Scheduled | 15-142-0139 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1250 | Orenco Advantex |  | Pump | Pressure | Drip | UV |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] | [18 empty] | Flushed drip field. Cleaned uv crystal and housing. Changed recirc off time from 12 to17 minutes. No overrides in last 30 days. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/18/2023 | Jan 1 1900 9:58AM
06/13/2023 | Alternative | RoutineScheduled Component Maintenance | 154-04-0966 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
09/08/2023 | Alternative | Reportable Incident Component Maintenance | 175-02-0601 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Blower panel alarmed, circuit breaker kept tripping off. Bad bearings, flywheel would barely move. Installed new blower, running well below the max amp rating (3.66/ 4.6 amps). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
06/20/2023 | Alternative | RoutineScheduled Component Maintenance | SR-98-350 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation"] | ["Control Operation" ,"Distribution Pump Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Removed weeds and roots from sand filters, flushed H-pipes, and then raked sand. Old tech sand filters are providing excellent treatment. The flapper for check valve on zone1 (bottom zone) was seized in a partially open position. Replaced it with a plastic check valve. Tested drip and flush rates. Zone 3 rates were noticeably slower than the other zones. Exposed portions of the top zone drip tubing run to show the owners. Plans called for a 3" install in the woods, which have not been kept clear. Owner to remove all fallen trees and brush. Rates on zone 3 are probably low due to some of the runs being crushed or kinked. If owner approves, zone 3 tubing will be uncovered at both ends and inspected for kinks. Adjusted down run times for drip pump and sand filter pump to get closer to dosing design and daily flow maximum. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["SludgeScum Accumulation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | ATU needs pumped out. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | Dec 30 1899 12:58PM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/07/2023 | Dec 30 1899 7:43AM
09/11/2023 | Alternative | Routine/Scheduled | 02-120-0603A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/11/2023 | Dec 30 1899 10:07AM
07/26/2023 | Alternative | RoutineScheduled | 154-17-0144 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2250 | Norweco |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Auxiliary Filter"] | NA | Septic | Discolored | [14 empty] | Inspected | Sludge Scum Accumulation - Septic 8", ATU 8", pump station 2" Light Brown Discoloration in ATU , septic smell when aerator running | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 03:00 PM
05/05/2023 | Alternative | Routine/Scheduled | 136-05-0494 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The pressure switch on the aerator is not hooked up. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/05/2023 | 12:00 PM
03/15/2023 | Alternative | RoutineScheduled | 159-10-012 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | [null] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
09/22/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | UV |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [17 empty] | Alternative septic inspection was done. The sludge level in the septic / atu was 4" scum 7" sludge. At time of inspection the level did not require the tank to be pumped out. 2 people live in this home full time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/15/2023 | Dec 30 1899 10:05AM
04/28/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Jessica | Young | 1.000000 | 1250 | Septic | Micro-fast | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/26/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 12:00 AM
02/14/2023 |  |  | 181-10-0160 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  |  | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | 12:00 AM
10/03/2023 | Alternative | RoutineScheduled | 02-142-0951 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/19/2023 |  | RoutineScheduled | VAG408450 | Rockbridge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | SEPTIC TANK ONLY | ADVANTEX AX20RT | Gravity | Gravity | Discharge | UV |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | SYSTEM DID NOT NEED TO BE PUMPED. SEPTIC FILTER WAS CLEANED. EFFLUENT SCREEN WAS CLEANED. UV LIGHT WAS PULLED AND CLEANED. TEXTILE SHEETS WERE SPRAYED OFF. CONTROLS WERE OPERATING AS DESIGNED. NO VISIBLE LEAKS IN THE CONVEYENCE LINES. THERE WAS NO DISCHARGE AT TIME OF VISIT. LIDS WERE SECURED | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/01/2023 | 09:55 PM
02/28/2023 |  |  | 11-142-0157 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
07/31/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["SludgeScum Accumulation" ,"Disinfection"] | ["Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Microfast needs pumping. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 08/15/2023 | Dec 30 1899 1:44PM
07/25/2023 | Alternative | Routine/Scheduled | 17-172-0330A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 5.700000 | [7 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Meet with the pumping company and pumped out the septic tank. The timer is set to 5 minutes every 2 hours. Took 5 year BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/25/2023 | Dec 30 1899 8:30AM
12/21/2023 | Alternative | RoutineScheduled | 175-05-0024 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation","Attached Growth Medium"] | ["Distribution Pump Operation","Attached Growth Medium"] | YES | [17 empty] | Septic Tank-4"sludge 0"scum/ Pump Tank to Puraflo Modules-1"sludge 0"scum/ Turned the Puraflo Peat and it's in good condition at this time/ Forcemain is broken 20' from the pump tank and requires repair/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-034703 ETM-0039198 On-39 sec Off-2h/ Replaced faulty 2" brass check valve/ No breakout or spongy areas on the drainfield. Returned on 1/3/2024 to repair the broken forcemain. Completed and tested, repair complete. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/10/2023 | 11:17 AM
03/28/2023 |  | RoutineScheduled | 154-07-0418 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | MicroFast | Sand Tank | Gravity | Pressure |  | Chlorination | 500.000000 | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 12:00 AM
05/30/2023 |  | RoutineScheduled | 177-12-0094-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Septic tank filter was clogged, cleaned. Thick liquid in septic tank as if liquid softeners are being used in the house, left copy of Do's and don'ts. Broken riser for spider valve. Will send proposal for replacing it. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
10/11/2023 | Alternative | RoutineScheduled Component Maintenance | 175-17-0370 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Microfast needs pumping. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/15/2023 | 02:02 PM
06/30/2023 | Alternative | Routine/Scheduled | 234-16-29 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | Dec 30 1899 2:55PM
12/02/2023 | Alternative | Initial Visit |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20RT |  | Pump | Gravity | Trenches |  |  | ["Control Operation","Recirculation Pump"] | ["Control Operation","Recirculation Pump"] | NA | [17 empty] | Initial start-up inspection. Verified proper installation. Tightened several loose unions in treatment unit. Programmed recirculation pump timers. Set recirculation pump flow rate. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/04/2023 | 07:03 PM
08/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Required to pump primary tank and a follow up inspection to be performed Repaired air supply | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 09/20/2023 | 01:07 PM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, UC Series | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air line from blower to the Whitewater unit appears to be obstructed. No aeration is occurring. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
04/05/2023 |  | Routine/Scheduled |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - recommend pumpout. Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/06/2023 | 07:45 AM
12/19/2023 | Alternative | Routine/Scheduled | 041-STS-261602 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 2.000000 | 1500 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | Dec 30 1899 10:00AM
11/27/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-92222 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | ["Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | NA | Musty | Clear | [5 empty] | 11/27/2023 |  | 44.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Very strong musty smell. Hard grease was clogging RSV valve, cleaned valve and left a copy of do's and don'ts. RECIRC: HL-1, LL-3, OVERRIDE-34. DISCHARGE: HL-1. "R" COUNTS BACK TO ZERO. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
06/13/2023 | Alternative | RoutineScheduled | WRAE-APPH6W | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 13" of accumulated solids in septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. 12" of solids in recirculation portion of treatment unit. 12" of solids in discharge portion of treatment unit. Tested floats, pumps and alarm. The septic tank and treatment unit may need to be pumped out next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/13/2023 | 07:03 PM
04/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower breaker had tripped. It was reset and the blower is working as designed now. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/17/2023 | Alternative | RoutineScheduled | 17-160-0191 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [18 empty] | - pretreatment tank needs to be pumped/cleaned - have attempted to schedule, it appears customer does not want to proceed | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/18/2023 | 12:00 AM
09/07/2023 | Alternative | Initial Visit | C 800-17-0071 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The septic tank needs additional risers on it to be properly inspected in the future. The timer is set to 3 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | Dec 30 1899 10:15AM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | There are four small trees planted near the end of the lines. Advised homeowner of potential issues and recommended moving them. Lower corner of the field on the house side appears to be evenly nitrified. Recommend homeowner monitor for changes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/09/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [7 empty] | 03/09/2023 |  | 13.000000 | [5 empty] | Will be sent separately | Inspected | Dbox cracks need sealed owner to repair | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
03/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 270505173 | Joshua | Hott | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/07/2023 | Alternative |  | 154-13-0155 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Bob | Miller | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/22/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/22/2023 | Dec 30 1899 11:50AM
10/20/2023 | Alternative | RoutineScheduled Component Maintenance | 175-04-0594 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Recirculation Pump" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Recirculation Pump" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
08/16/2023 | Alternative |  | 025-STS-13191 | Brunswick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Southside | Paul Small LLC | 1942001402 | Paul | Small | 3.000000 | 1000 | 1000 | NA | Pump | Pressure | Drip | Not Applicable | 200.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","None"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","None"] | YES | [16 empty] | Pumped Out | Replaced defective recirculation pump in recirc tank. Tested all switches. System functioning normally now. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/22/2023 | 09:00 AM
04/19/2023 |  | Reportable Incident |  | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 4.000000 | 9000 | None | None | Pump | Pressure | Trenches | Not Applicable | 4000.000000 | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Follow-Up - installed second pump - upgraded float sensors, system at normal /operating level on arrival. Ran pump #1 - did not see any indication of "surfacing" that was reported ... may take a day or two since the field has been idle since Monday and no flows. Follow-up being scheduled. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/20/2023 | Jan 1 1900 6:45AM
02/09/2023 |  | RoutineScheduled | VAG401478 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Sand |  |  | Gravity | Discharge | Chlorination |  | ["None"] | ["None"] | [18 empty] | no discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/09/2023 | 12:00 AM
06/15/2023 | Alternative | Routine/Scheduled | C-05-111-0182 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/15/2023 | Jan 1 1900 2:00PM
02/25/2023 |  | RoutineScheduled | {FIPSCode}-STS-1948 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 2 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/25/2023 | 12:00 AM
06/14/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 06/14/2023 |  |  |  | 1600.000000 |  |  |  | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/07/2023 | Dec 30 1899 6:25AM
07/27/2023 | Alternative | RoutineScheduled Component Maintenance | 033-STS-90100 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
02/11/2023 |  |  | 2051-98-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination |  | ["Attached Growth Medium","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 6.600000 |  |  | 1.800000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/14/2023 | 12:00 AM
04/18/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/07/2023 |  | RoutineScheduled | 051-STS-16169 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 3 Chlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/07/2023 | 12:00 AM
04/21/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
06/02/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | YES | [17 empty] | System in alarm at time of inspection: Found trash in the blue valves at the hydraulic unit, removed and system now dosing correctly/ Septic Tank-6"sludge 0"scum/ Pump Tank-2"sludge/ No pump out needed at this time/ Counts: High-124/ Peak-1411/ Watermeter-128,766.3/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/26/2023 | Alternative | RoutineScheduled | VAG401965 | Rockingham | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Sand |  |  | Pressure | Discharge | Chlorination |  | ["Septic Tank Baffles"] | ["Septic Tank Baffles"] | [18 empty] | Baffle clogged | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 10/26/2023 | 12:00 AM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/21/2023 | Alternative | RoutineScheduled | 115-01-0016 | Campbell | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Biomicrobics Micro Fast |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Auxiliary Filter"] | ["BlowerCompressorAerator Operation","Auxiliary Filter"] | NA | [16 empty] | Inspected | Sludge levels-Septic tank 10-14" in. sludge and 8" sludge in treatment zone. Does not need pumping this year, Pump tank 5-8", Cleaned blower filter. Blower connection to plumbing was leaking air and worn from vibration and no aeration getting to treatment tank the pump. We worked to reduce the air leak to minimum but needs replumbing. Owner said he will repair the leaking air pipe. Return to normal operation after we addressed the leak. The Blower, pump and Control panel working correctly. years records: Pump run count 4135 vs 2235 vs 909 last 2 years = 1900 pump cycles this year., Pump hours 291.34 vs 144.75 hours last year = 146.5 hours run time. Alarm is operational on both control boxes. Float switches are good. Cleaned and flushed the spin filter, ran and flushed drain field drip line. no leaks observed in drip drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/28/2023 | 09:30 AM
01/20/2023 |  | RoutineScheduled | SWP-04-345 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation" ,"Effluent Screens"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Roots in wedge lids hasn't grow any. No leaks. Trees still close to tanks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
04/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/07/2023 |  | RoutineScheduled | 10-142-0017 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1250 | Clearstream |  | Pump | Pressure | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
04/11/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | EcoPod | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The blower was repaired. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/14/2023 | Alternative | RoutineScheduled | 13-184-134 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Not Applicable | [22 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
05/03/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/03/2023 | 12:00 AM
02/27/2023 |  | RoutineScheduled | 09-100-0560 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1250 | Septic Tank | PuraFlo | Gravity | Pressure | Pad | Not Applicable | 300.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/27/2023 | 12:55 PM
03/23/2023 | Alternative | Routine/Scheduled | 166-04-586 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Basin - plastic - bulging noted - float sensors, pump and controls operating. BioFilter - peatmoss some compaction - poor condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | 07:00 AM
10/05/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/30/2023 | 12:00 AM
04/17/2023 |  | Reportable Incident | 18-137-0070 | Goochland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. The timer is set to 3 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/17/2023 | Jan 1 1900 12:30PM
08/08/2023 | Alternative | RoutineScheduled Component Maintenance | 182-09-0238 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 | 2500 | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"SludgeScum Accumulation"] | NA | [7 empty] | 08/08/2023 |  | 43.000000 | [5 empty] | Will be sent separately | Inspected | Installed rebuilt blower, visual alarm, Discharge pump, Valve Box lid Pumped primary tank Repaired pump tank riser | This AOSS should now return to normal function after having provided the above state routine maintenance | 09/20/2023 | 01:07 PM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/15/2023 | Dec 30 1899 2:02PM
03/30/2023 |  | RoutineScheduled |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 2-6 | 0-2 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear |  |  | 15.000000 | [11 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 02:00 PM
10/30/2023 | Alternative | RoutineScheduled | 145-97-0072 (LEGACY ALT. SYSTEM) | Highland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 2.000000 | 2000 | Septic Tank Only | Sand Filter | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [7 empty] | 10/30/2023 | Pump Chamber | 17.700000 |  |  | 3.300000 |  |  | Attached to this report |  | The system did not need to be pumped. The sand filter was in good operating condition. The samples were within permitted limits. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/27/2023 | 08:45 PM
04/20/2023 |  | RoutineScheduled | 95-113-169 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation"] | NA | Musty | Clear | [15 empty] | 2 Chlorine 5 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/20/2023 | 12:00 AM
12/15/2023 | Alternative | RoutineScheduled | 157-10-0202 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Virginia Septic Solutions LLC | 1942001500 | Justin | Barker | 3.000000 | 600gpd | Clear stream 600N |  | Pump | Pressure | Drip | UV |  | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | YES | None | Clear | [14 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/15/2023 | 12:00 AM
03/15/2023 | Alternative | RoutineScheduled | 159-11-158 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
08/01/2023 | Alternative | RoutineScheduled | 166-13-148 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters, replaced UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/08/2023 |  | RoutineScheduled | 133 06 0436 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Western Virginia Water Authority | 1942001145 | Michael | Doss | [9 empty] | ["Other"] | ["None"] | NA | None | Clear | [5 empty] | 03/08/2023 | Sample Chamber |  |  |  | 0.000000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/12/2023 | 05:55 AM
08/30/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
05/05/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Septic zone 1" scum 12" sludge- Recirc zone minimal scum and 8" sludge, Discharge Tank 24" sludge - Cleaned Biofilter, Flushed and Brushed spray manifold- Cleaned RSV, Flushed System, Ran in test mode. Tested Floats and alarm all good. Pumps good but weak from age, Recirc pump run time 92hours 180140 cycles and discharge pump 33.2 hours and 602cycles, start date 8-28-2022, 250 days in memory on new circuit board (old pumps) No alarms or alerts since installed in history. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"SludgeScum Accumulation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 12/21/2023 |  | 132.000000 | [5 empty] | Will be sent separately | Inspected | Repaired timer Replaced pump, middle float gauges and valve box Required pumping and add riser | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 01/15/2024 | 10:39 AM
07/12/2023 | Alternative |  | 179-14-0010-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
05/17/2023 |  | Reportable Incident | SWP-04-119 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to failed pump. Replaced pump under warranty. Replaced failed timer float. Will follow up to fully inspect the system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
10/23/2023 | Alternative | RoutineScheduled | 08-172-0124A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1500 | Advantex |  | Pump | Pressure | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 12:00 AM
05/18/2023 |  | RoutineScheduled | 003-STS-31331 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | MicroFast |  | Gravity | Gravity | Trenches | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | 12:00 AM
09/12/2023 | Alternative | Follow-Up Component Maintenance | 179-14-0243-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Chemically and physically cleaned FAST media. Pump out of both tanks by others. Resealed pump tank outlet riser. Installed proper float tree bracket. Adjusted floats best as we can since cords are too short and owner declined replacement. Seed and strawed disturbed areas. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
05/17/2023 | Alternative | Routine/Scheduled | 179-09-0028 | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [5 empty] | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | 04:33 PM
06/12/2023 |  | Initial Visit | 033-19-0032-SP | Caroline | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to a red light on and the aerator not running. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. The septic tank needs to be pumped as well as the Clearstream tank. The timer is set to 5 minutes every 1 hour. Did not take sample due to the aerator not working on arrival. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/12/2023 | 01:15 PM
07/12/2023 | Alternative |  |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Wetlands |  |  | Pressure | Trenches | Not Applicable |  | ["Septic Tank Baffles"] | ["Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | 12:00 AM
12/07/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/07/2023 | Dec 30 1899 1:55PM
10/04/2023 | Alternative | RoutineScheduled | SD-10-319 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity |  |  | 67.000000 | ["SludgeScum Accumulation","Attached Growth Medium","Control Operation"] | ["SludgeScum Accumulation","Attached Growth Medium"] | YES | Sulphitic | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | 12:00 AM
06/19/2023 | Alternative | RoutineScheduled | SD-12-149 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 63.000000 | ["Attached Growth Medium","SludgeScum Accumulation"] | ["Attached Growth Medium","Effluent Screens","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 05:00 PM
06/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend removing tree closest to lower line | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/25/2023 | Alternative | RoutineScheduled Component Maintenance | 099-STS-92267 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Blower 3.08 amps. Treatment is crystal clear. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 07:01 AM
06/05/2023 | Alternative |  | 17-100-0422 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
10/18/2023 | Alternative | RoutineScheduled Component Maintenance | SP-05-641 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Media showing its age but still ok. Dbox still needs new lid. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
04/30/2023 | Alternative | RoutineScheduled | 151-11-0091 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | KC Forge Environmental Service, LLC | 1942001034 | Kent | Cuthbertson | 4.000000 | 45000 | 15000 | 15000 | Pump | Gravity | Trenches | UV | 27100.000000 | ["None"] | ["None"] | YES | [8 empty] | Sample Chamber | [6 empty] | Attached to this report |  | The very first TSS was 7 mg/L over the limit but the remainder of all samples were within limits. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | 08:30 AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/24/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [5 empty] | 01/24/2023 |  | 34.000000 | 540.000000 |  |  |  |  | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2023 | Dec 30 1899 8:47AM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
02/08/2023 | Alternative | RoutineScheduled | SD-15-177 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. High level count at 10 after testing. Panel alarms for low level but does not track them. Fuji blower running at 2.99 amps, sounds normal. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
07/25/2023 | Alternative | RoutineScheduled | 2006-143-0021 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1250 | Clearstream |  | Pump | Pressure | Trenches |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | 12:00 AM
02/23/2023 | Alternative |  | 101-07-0115 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Rick | Byron | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-90353 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The dispersal area is across the creek and is currently not accessible. This area should be maintained in a mowed condition to prevent roots from growing into the drainfield lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
01/30/2023 |  | RoutineScheduled | 10-183-016 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Attached Growth Medium","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/30/2023 | 12:00 AM
11/13/2023 | Alternative | Reportable Incident | C 800-15-0034 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Arrived on site went through system. System is functioning as it should. Tested all floats and pumps. Panel working properly. There were no alarms whe we arrived. Used 1 alarm call | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/15/2023 | Dec 30 1899 8:56AM
04/25/2023 |  |  | 03-125-154 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 04/25/2023 |  | 2.660000 |  |  | 0.000000 |  |  | Will be sent separately |  | BOD: 2.66 TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | 12:00 AM
06/15/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | [14 empty] | Pumped Out | Replaced aerator and diffuser | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/15/2023 | Dec 30 1899 2:00PM
08/17/2023 | Alternative | RoutineScheduled | 10-173-089 | Prince Edward | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 5.000000 | 9500 | Delta |  | Pump | Gravity | Trenches | Not Applicable | 900.000000 | ["Effluent Screens","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/17/2023 | 12:00 AM
03/14/2023 | Alternative |  | 150-05-126 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 12:00 AM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/24/2023 | Alternative | RoutineScheduled | 061-18-390 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Advantex |  | Pump | Gravity | Discharge | UV | 500.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] | NA | Musty | Clear | 6.800000 |  |  |  |  | 07/05/2023 | Pump Chamber | 9.000000 |  | 1.000000 | 8.000000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
12/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 02:30 PM
05/05/2023 | Alternative | Routine/Scheduled | 136-03-0296 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - fractured in bottom - recommend replacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | 08:45 AM
05/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pods are full of effluent | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
04/18/2023 |  | RoutineScheduled | 05-184-5001 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | ["Septic Tank Baffles","Disinfection","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/18/2023 | 12:00 AM
03/17/2023 |  | RoutineScheduled | SWT-03-344 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Found pump running consistently due to contractor coil stock close, cut power off and checked all wires for bad insulation or lose wire and didn't find anything wrong, reset power and tested contactor on automatic 11 times and didn't stick so left everything in auto. Spoke to customer about issues and he want us to put in a new contactor, will come back next week to replace it. Small root in wedge lids but no water infiltration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
05/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/07/2023 |  | Reportable Incident | 033-13-0086-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump"] | ["Level Sensor Operation" ,"Recirculation Pump"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Complaint inspection. Recirc high level alarm was going off due to a bad alarm float, replaced. Treatments looks bad due to pump intake plus spinners being clogged, cleaned them and tested and everything started working. RT tanks does not have much sludge so treatment should get better. RT tank has 7 inches of sludge inlet side and 5 inches of sludge in outlet side no scum. If treatment doesn't get better will need pump out. Will check next visit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
07/25/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Trenches |  | 450.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 02:00 PM
01/03/2023 |  |  | 07-197-A12 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/03/2023 |  | 10.600000 |  |  | 6.400000 |  |  | Will be sent separately |  | BOD: 10.6 TSS: 6.40 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2023 | 12:00 AM
01/10/2023 |  | Routine/Scheduled | S 800-14-0021 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 2 minutes every 3 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | Jan 1 1900 10:00AM
10/31/2023 | Alternative |  | 154-17-0274 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Kathy | Parrish | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/17/2023 |  | Reportable Incident | 175-13-0067 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Ecopod | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NO | [17 empty] | Service call only: Alarm due to faulty pump. Replaced Zoeller E-185 Pump 230 Volts/ Counts: Pump-1914 ETM-66297 Now properly dosing. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
09/01/2023 | Alternative |  | 17-120-0527AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | [] | [] | [18 empty] | We replaced a SBR syphon pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 12:00 AM
05/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
11/17/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-17787 | Scott | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.500000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
01/30/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 2000 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [18 empty] | Inspection failed because they need to install a solenoid switch. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12:00 AM
10/30/2023 | Alternative | RoutineScheduled | 179-98-015 | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | checked peat, system check okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/05/2023 | Alternative | RoutineScheduled | 182-04-0599 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [18 empty] | No return | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | 12:00 AM
10/09/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 2000 | Septic | pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/30/2023 | Alternative | Reportable Incident | 02-163-0175 | New Kent | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | ["Control Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] |  | NO | [17 empty] | Arrived to conduct routine maintenance. Found system flooded and control panel PLC not operating. Requires replacement of control panel and pumpout of pump tank for storage. Panel / PLC requires ordering & programming from manufacturer. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/31/2023 | Dec 30 1899 8:00AM
07/26/2023 | Alternative | RoutineScheduled Component Maintenance | 108-15-0020 | Bath | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 4.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 07/26/2023 |  | 153.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
05/31/2023 | Alternative | Routine/Scheduled | 196-06-0321 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 40.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/31/2023 | 06:29 PM
10/18/2023 | Alternative | RoutineScheduled | 03-197-A9 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.500000 | 7.000000 |  | 0.000000 | [11 empty] | Clear, both tablets stocked, aerator working, no odor. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
07/03/2023 | Alternative | Initial Visit | 136-18-0327 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Visit - Real Estate Inspection Primary septic tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - concrete - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | 01:00 PM
11/25/2023 | Alternative | Routine/Scheduled | 121-STS-13342 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Ecoflo |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["Attached Growth Medium","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/25/2023 | 01:30 PM
02/09/2023 |  | Routine/Scheduled | 2004-143-0139 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - recommend pumpout & refill - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/13/2023 | 07:00 AM
08/03/2023 | Alternative | Routine/Scheduled |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Delta Environmental Products, UC Series |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Aeration Tank - normal level - mixing present - compressor serviced. Pump tank - float sensors, pump and controls operating. DBox - plastic - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | 09:00 AM
03/18/2023 | Alternative | RoutineScheduled | SD-04-741 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1000 | septic | puraflo | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/20/2023 | 08:40 AM
03/21/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
10/31/2023 | Alternative | RoutineScheduled | 027-STS-17360 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 15 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/31/2023 | 12:00 AM
06/14/2023 |  |  | 179-12-0118-SA | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance | SD-05-416 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity |  | Chlorination |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
08/24/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip |  | 600.000000 | ["Auxiliary Filter","Dispersal System Operation","Effluent Screens"] | ["Auxiliary Filter","Dispersal System Operation","Effluent Screens"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/12/2023 | 02:06 PM
05/15/2023 |  | RoutineScheduled | 2000-91-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | ATU | Polishing Sand Filter | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.500000 |  |  | 1.800000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/17/2023 | 12:00 AM
04/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/15/2023 | Alternative | Routine/Scheduled | 136-12-0287 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Secondary septic tank - normal level - recommend pumping next service. Pump Tank - float sensors, pump and controls operating. Aeration Tank - normal level - mixing present - compressor serviced. DBox - plastic - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | 06:45 AM
11/11/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-11126 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Recirculating Sand Filetr |  | Pump | Gravity | Discharge | Chlorination | 1000.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] |  | Musty | Clear | 6.800000 |  |  | 1.700000 |  | 11/15/2023 | Sample Chamber | 18.000000 |  |  | 12.300000 | [5 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/01/2023 | 12:00 AM
05/26/2023 | Alternative | Initial Visit | 550-STS-6742 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the lawnmower hitting a valve box top - replaced 1 valve box. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. There is paint in the tanks - should be pumped and cleaned out. The UV is not working - quartz tube is broken and bulb is bad - needs to be fixed and/or replaced. The timer is set to 5 minutes every 2 hours. Did not take BOD and Fecal samples due to the UV not working. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/26/2023 | Dec 30 1899 9:15AM
11/20/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected | 1. I was not able to test pumps operation due to no water in the tank they need to be checked when water gets to it normal level 2. Puraflo modules holding water also sample box is holding water 3. Need uncover distribution box and video camera lines to find out why sample box is holding water | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/06/2023 | Dec 30 1899 9:34AM
12/13/2023 | Alternative | Routine/Scheduled | 127-STS-35229 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 600 |  |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 9:00AM
09/22/2023 | Alternative | RoutineScheduled | 087-STS-6581 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/24/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity |  | UV |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | 6.900000 | 18.000000 |  | 0.000000 | [9 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/15/2023 | Dec 30 1899 12:05PM
01/23/2023 |  | Routine/Scheduled | 10-142-0158 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Hoot |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash Tank - normal level - recommend pumpout. Aeration tank - compressor diaphragm failure - repaired on property - mixing present on departure. Pump tank - sensor probe, pump and controls operating. Drip - headworks serviced. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/24/2023 | Jan 1 1900 7:30AM
04/18/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
01/04/2023 |  | RoutineScheduled | 15-100-0236 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | Aquasafe |  | Pump | Gravity | Mound | UV | 600.000000 | [] | [] | NA | [17 empty] | Everything working properly. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/05/2023 | 01:55 PM
12/18/2023 | Alternative |  | 07-184-5003 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/18/2023 |  | 4.850000 |  |  | 6.830000 |  |  | Will be sent separately |  | BOD: 4.85 TSS: 6.83 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 12:00 AM
06/20/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20467 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
11/15/2023 | Alternative | RoutineScheduled | 2004-143-0183 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/14/2023 |  | RoutineScheduled | 179-STS-87634 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Effluent Screens"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
02/23/2023 | Alternative | RoutineScheduled | SD-02-53 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Override function working fine this year. No ants seen in any of the pods. Remote drainfield site is well maintained. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
08/18/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | ["Level Sensor Operation","SludgeScum Accumulation"] | [] |  | None | Clear | 7.350000 | [14 empty] | Recommended the system be pumped and will return to replace floats. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/15/2023 | 12:00 AM
02/23/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | At time of inspection it appeared as though the owners were moving out | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/19/2023 | Alternative | RoutineScheduled | 128-09-0050 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Gravity |  |  |  |  | ["None"] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/29/2023 |  | Routine/Scheduled | 196-08-144 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 1500 | Ecoflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 05:39 PM
05/19/2023 | Alternative | RoutineScheduled | 161-STS-42602 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20RT |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Auxiliary Filter"] | ["Effluent Screens","Auxiliary Filter"] | NA | [16 empty] | Inspected | Septic Tank minimal scum and 6-10 in trace sludge, Recirculation zone no scum 8"sludge trace and discharge zone 10" sludge trace, Pump tank had a trace of sludge and was clear. Cleaned effluent filter, Cleaned drip filter, Sprayed off the media, discharge pressure 30 psi on drainfield. Drainfield irrigated well. Discharge pump PF200511. Checkall all 6 floats agood, Recirc pump has 913 hours and 83,260 cycles and the discharge pump has 305 hours and 10306 cycles. One alarm on 3-9-23 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | Jan 1 1900 9:30AM
03/14/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | filter clog cleared | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
06/03/2023 | Alternative | RoutineScheduled | SD06-151 | Rappahannock | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | septic | Microfast | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | YES | None | Clear |  | 7.500000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 09:10 AM
12/21/2023 | Alternative |  | 18-100-0472 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
01/26/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Lord Fairfax | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Installed new Goulds 1/2 hp pump. Enhanced air filtration (canister filter) added to the Gast blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
05/05/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Multiflo |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Septic tank minimal scum and 10" sludge, treatment tank has trace of scum and trace of sludge. Aeration and system is running good, Alarm tested good. No pumping needed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
03/30/2023 |  | RoutineScheduled |  | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock-Rapidan | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 0-3 0-5 | 0-0 | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] |  | None | Clear |  |  | 5.000000 | [11 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 01:00 PM
05/02/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
01/19/2023 | Alternative | Routine/Scheduled | 136-10-0183 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Routine Service. Pumped processing tank empty - cleaned and serviced. Trash Tank - pumped empty. Aeration tank - mixing present - pumped empty - compressor serviced. Pump tank - float sensors, pump and controls operating - pumped. Drip - headworks serviced. Refilled processing tank with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2023 | 07:30 AM
06/03/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 5.000000 |  | Clearstream | Clearstream | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump and floats were replaced. System appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/22/2023 | Alternative | RoutineScheduled Component Maintenance | 061-STS-23775 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
01/04/2023 |  | Routine/Scheduled | {FIPSCode}-STS-4936 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/05/2023 | Jan 1 1900 8:00AM
01/27/2023 | Alternative | RoutineScheduled | 154-05-1090 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Pungent | Discolored | [13 empty] | Will be sent separately | Inspected | As noted previously, the EZ Set riser lid on the pump tank is damaged and should be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
11/29/2023 | Alternative |  | {FIPSCode}-STS-15912 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/29/2023 |  |  |  |  | 2.100000 |  |  | Will be sent separately |  | BOD: BDL TSS: 2.10 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/29/2023 | 12:00 AM
06/19/2023 | Alternative | Routine/Scheduled | 133-STS-94075 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/22/2023 | 11:00 AM
11/06/2023 | Alternative | Reportable Incident | 151-08-0083 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Travis stated alarm kept going off for 2 weeks Opened pump tank and found in high level Pulled floats to test and the pump came on Determined floats to be intermittently failing Also noted root intrusion though riser and coming through tank around forcemain Plumbing for pump is outdated Pump is functioning properly. Made solutions and Travis asked for them to be emailed to Keith(owner) | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 09:57 AM
05/04/2023 | Alternative | RoutineScheduled | KHAN-AMXGVA | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 10" of accumulated solids in septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. Removed floating solids from recirculation pump area of treatment unit. Cleaned solids from the recirculation pump intake screen. 10" of solids in recirculation portion of treatment unit. 12" of solids in discharge portion of treatment unit. Tested floats, pump and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/29/2023 | Jan 1 1900 7:03PM
06/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
10/31/2023 | Alternative |  | 177-17-0045-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/13/2023 |  | Routine/Scheduled | 133 07 0095 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 05:30 PM
08/09/2023 | Alternative | Pump-Out Only |  | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Supervised pumpout of processing tank - 3 compartments - Supervised refill of aeration tank for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | Dec 30 1899 9:45AM
04/19/2023 |  | RoutineScheduled | 179-13-0379-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 2.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | YES | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Found intake on recirc pump partially clogged, cleaned. Pressure gauge inside EZ-treat unit broken from corrosion, replaced with swreiter valve. EZ-TREAT unit was ponding due to Roots growing in bottom of pod coming in through 1" grommet, removed roots and dug up, wire wheel and sealed outside also added Root Destroyer. Recommended installing a SIM-TEC filter on recirc pump to protect pump intake, customer wants it installed next visit. treatment look very good crystal clear. DISCHARGE: HL 7, LL 24, OVERRIDE 17. 29 PSI. "R" counts back to zero. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
03/28/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | Nayadic ATU | none | Gravity | Gravity |  | Chlorination |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | fixed air leak on blower | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
09/01/2023 | Alternative | Routine/Scheduled | C 800-03-0025 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | Dec 30 1899 8:36AM
11/09/2023 | Alternative |  | 18-197-A3 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/09/2023 |  | 14.700000 |  |  | 24.400000 |  |  | Will be sent separately |  | BOD: 14.7 TSS: 24.4 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/09/2023 | 12:00 AM
04/17/2023 |  |  | 06-192-080 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 04/17/2023 |  | 15.500000 |  |  | 10.300000 |  |  | Will be sent separately |  | BOD: 15.5 TSS: 10.3 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 12:00 AM
04/18/2023 |  | RoutineScheduled | 099-06-0127-SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment was very clear. 26 psi. No meter to check gpm accurate. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
11/02/2023 | Alternative | RoutineScheduled | 175-13-0036 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic / Ecopod ATU Treatment Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 11/02/2023 | Sample Chamber | 26.000000 | [5 empty] | Attached to this report |  | Septic Tank-2"sludge 2"scum/ EcoPod-4"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ No pump out needed at this time/ Blower airfilter cleaned and blower is working correctly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-On-6m 15s Off-1h 53m/ Counts-16150 ETM-1466h/ High level-999994/ Watermeter-0,507,275/ No breakout or spongy areas on the dripfield and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/24/2023 | Alternative | Follow-Up | 800-08-0150 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Repair - pumped septic tank, processing tank and pump tank empty to effect repairs. Installed new wiring and air compressor for Aeration tank. Installed new wiring and control panel for discharge tank. Replaced leaking access risers on septic tank, processing tank. Replaced plumbing, pump and float sensors in discharge tank. Re-parged appurtenances in all tanks. Refilled with fresh water in aeration tank for re-start. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/28/2023 | Dec 30 1899 8:00AM
02/13/2023 |  | Initial Visit | 182-05-0184 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Blue Ox | [6 empty] | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/13/2023 | 12:00 AM
09/05/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20280 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
10/18/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/19/2023 | 10:25 AM
02/23/2023 |  | Routine/Scheduled | 234-14-295 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/23/2023 | Jan 1 1900 2:30PM
10/17/2023 | Alternative |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | [9 empty] | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/03/2023 | 12:00 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/22/2023 |  | Reportable Incident | 036-STS-33869 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | ["Dispersal System Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Alarm Event - system flooded over weekend - pumped discharge tank - found drip screen 100% clogged - serviced / replaced screen. Trash tank - returned to normal level Aeration Tank - returned to normal level - mixing present - compressor serviced. Pump Tank - pumped empty - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | Jan 1 1900 7:00AM
05/16/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Fast | Pump | Pressure | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | 12-15" of sludge thick 3' scum layer. Recommend pumping within the year. 12" loose in outlet side. Pump tank clean. Cleaned spin filter and blower filter. Pumps, alarms and floats are operational. Field is dry. 1380.35 Hr s of run time 7556 cycles | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:15 PM
10/11/2023 | Alternative | RoutineScheduled | 182-99-0024 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | SAND |  |  | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | UNABLE TO DETERMINE SLUDGE LEVEL DUE TO NO ACCESS TO SEPTIC TANK. PLANTS/TREES/SHRUBS SEEM TO HAVE BEEN PLANTED ON OR NEXT TO DRAINFIELD LINES 7 & 8 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | 12:00 AM
04/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower breaker had tripped. It was reset and the blower is working as designed now. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 2000 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/03/2023 | Alternative |  | SP-05-37 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
05/04/2023 |  | RoutineScheduled |  | Frederick | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | [17 empty] | This system has a fuji tank with a siphon tank after it | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/15/2023 | 11:40 AM
10/18/2023 | Alternative | RoutineScheduled | 109-02-0719 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Effluent filter installed or maintained | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | [16 empty] | Inspected | Routine Inspection - The system was pumped in 2022 - timer dosed pump is operational and the alarm float operational. Peat is worn but had no ponding. it was turned and looks in good condition for its age. Cleaned effluent filter in the septic tank. pump has 427.37 hours versus 402.42 hours last year. counter does not work. total years pumping of about 25 hours since last years reading | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/21/2023 | 09:30 AM
10/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | NO | [17 empty] | Septic Tank-0"sludge 0"scum/ Pump Tank-0"sludge/ No pump out needed at this time/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump- 12715 ETM-2125h 29m/ Peak-84 ETM-7797h 8m/ High-50/ Zone1-5894/ Zone2-6190/ Watermeter-0,685,857.46/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/04/2023 |  | Routine/Scheduled | 228-16-0357 A | Virginia Beach | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/04/2023 | Jan 1 1900 1:15PM
02/10/2023 |  | RoutineScheduled | 177-12-0071-SR | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Septic Tank Baffles" ,"Effluent Screens" ,"Attached Growth Medium" ,"Control Operation"] | ["Septic Tank Baffles" ,"Effluent Screens" ,"Attached Growth Medium" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Water level was high on septic tank due to clogged filter, cleaned filter. Both sand filter were ponding water level was 18" above manifold. Pumped water from Both filters into septic tank and augered and raked them. Water was slowly draining. Dug a couple holes to check sand in the bottom of Both sand filters and found a lot of sludge in there, recommend to replace sand. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
01/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | Best 1 | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
05/23/2023 | Alternative | Reportable Incident Component Maintenance | 175-04-0803 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Distribution Pump Operation" ,"SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation" ,"SludgeScum Accumulation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Met local pumper (Septic Clean) on site. Tank pumped clean of all sludge and debris. Trash in the tank was ridiculous. Ballast blocks removed and replaced with PVC stands to support the diffusers and allow for unobstructed aeration. New Gast blower installed and enhanced air filtration added. Goulds pump model 1DW51E1EA was replaced with a new pump, same model. Junction box at tank was cleaned up, corroded terminal strip and grounds replaced. Cleaned carbon dust from inside the control panel (usually created by frequent or sustained alarms). Refilled tank for 1.5 hours with fresh water. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 06:43 AM
08/10/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | [7 empty] | 08/10/2023 | Sample Chamber |  |  | 1600.000000 |  |  |  | Attached to this report |  | Septic Tank-12"sludge 6"scum/ Microfast-14"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ Highly recommend pump out of the Septic-Microfast Tank/ Blower air filter cleaned and blower functioning correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-1852 ETM-291h 55m/ Peak-20 ETM-65h 30m/ High level-18/ Watermeter-0,114,319.27/ UV-Light sleeve cleaned but the light is not working- requires service/ No breakout or spongy areas on the drip field. Returned on 8/16/2023 and replaced the UV-Light Bulb- Now functioning properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/27/2023 |  | RoutineScheduled | 154-13-0059 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco | Sand Tank | Gravity | Gravity | Discharge | UV | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 12:00 AM
10/05/2023 | Alternative | RoutineScheduled | SD-15-180 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | sludge checked, system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/31/2023 | Alternative | Routine/Scheduled | 136-08-0456 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/01/2023 | 12:30 PM
01/09/2023 |  | Routine/Scheduled | 04-142-0021 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1250 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","SludgeScum Accumulation"] | ["Effluent Screens","SludgeScum Accumulation"] | NO | [17 empty] | Effluent filter checked. System appears to be operating normally. Need some room in front of the control panel to be able to access it. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | Jan 1 1900 7:54AM
04/25/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 11:24 AM
03/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Microfast blower filter was missing. It was replaced. Bell cap for the hydraulic unit filter had broken. It was replaced. System appears to be functioning as designed now. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/17/2023 | Alternative | Routine/Scheduled | 151-13-0120 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 40.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/17/2023 | 06:40 PM
02/27/2023 |  |  | 099-13-0093-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
03/13/2023 |  |  | 165-STS-335594 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | 12:00 AM
04/18/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | 12:00 AM
09/29/2023 | Alternative | RoutineScheduled Component Maintenance | 177-15-0248-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"SludgeScum Accumulation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Effluent Screens" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend pumping the Advantex recirculation tank due to sludge accumulation in the tank. It may be advisable to clean the pump tank also as it may need pumping at next year's inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Parking on distribution box is falling off. There is root infiltration and the level is low. Recommend adding a 90 or a Tee to the inlet pipe. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
01/23/2023 |  | RoutineScheduled | 132-17-0048 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | AquaSafe |  | Gravity | Pressure | Drip | Not Applicable | 500.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 12:00 AM
04/18/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
07/25/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | 12:00 AM
09/19/2023 | Alternative | Reportable Incident Component Maintenance | 175-18-0401 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | UV |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | High level alarm for EZ Treat recirc tank. Observed panel/ pump running an automatic cycle, but no effluent draining over to the discharge pump tank. Tried flushing UV housing and then flushing through the discharge tank inlet pipe. Suspected the P-trap-shaped 2" drainpipe coming off of the UV assembly was where the clog was. Called EZ Treat technician who verified that the UV assembly was not removable (hard-piped). Finally cleared the clog by attaching a big wet/ dry vac to the discharge tank inlet pipe. Treatment looked good and system has had regular maintenance. Cleaned effluent filter and cleaned the Simtech pump screen for the recirc pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
08/24/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | pure flow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/11/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.830000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 03:45 PM
05/31/2023 |  | RoutineScheduled | SWP-04-269 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. D-box out of shape and has 1 corner broken due to tree root pushing on it, tree about 6 feet from box, Recommend to replace box and snake camera headers. Will send proposal. Peat showing its age we will evaluate next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
05/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 3.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air release valve on Zone 2 had come off. It was replaced and appears to be functioning as designed now. Valve box and air release valve will be replaced and area will be limed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Dispersal System Operation"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Discharge Pump replaced, Power was off to system Leak in Drainfield not repaired Fence installed in drainfield | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 09/20/2023 | 01:07 PM
08/25/2023 | Alternative | Routine/Scheduled | 02-177-1381 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 17.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/25/2023 | 03:30 PM
09/05/2023 | Alternative | RoutineScheduled | 128-15-061 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/06/2023 |  | RoutineScheduled | 179-STS-90112 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Spinners were barely spraying due to clogged pump intake (Recirculation), cleaned intake and spinners and got better 2.9 psi with gate valve all the way. will keep an eye on it. Area around observation port in mount kind of wet but no water above ground. 59 psi on return. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
01/18/2023 | Alternative | Routine/Scheduled | 166-12-192 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Alarm Event Discharge tank flooded - clogged drip screen, clogged discharge pump, Timer enable float sensor failed (stuck ON) Pumped system empty for service and maintenance. Serviced discharge pump, serviced drip headworks. Refilled system for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/19/2023 | 07:30 AM
07/18/2023 | Alternative | Routine/Scheduled | 550-STS-6707 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/18/2023 | Dec 30 1899 8:35AM
10/25/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-19857 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.500000 | 8.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
03/09/2023 |  |  | 15-142-0268 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex | [6 empty] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 12:00 AM
01/16/2023 | Alternative | Routine/Scheduled | 166-05-408 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/17/2023 | 08:00 AM
06/28/2023 | Alternative | Routine/Scheduled | 085-STS-34235 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 650 |  |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | Dec 30 1899 11:30AM
11/16/2023 | Alternative | Reportable Incident Component Maintenance | 177-17-0403-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Septic | Cloudy | [13 empty] | Will be sent separately | Inspected | Complaint inspection. Blower was not working due to bad diaphragm, replaced chamber block and system went back to normal. Treatment should get back to normal 8n few days. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
05/23/2023 | Alternative | RoutineScheduled | SD-04-607 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation","SludgeScum Accumulation","Distribution Pump Operation","Dispersal System Operation"] | [] | YES | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/23/2023 | 09:00 AM
10/23/2023 | Alternative | RoutineScheduled | 16-100-0288 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 500 | AQUASAFE |  | Pump | Gravity | Mound | UV | 480.000000 | [] | [] | [17 empty] | Pumped Out | PUMPED SYSTEM REPLACED UV LIGHT UNIT EVERYTHING WORKING AS IT SHOULD | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/15/2023 | 02:40 PM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance | SD-10-152 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | Chlorination |  | ["Disinfection"] | ["Disinfection"] | NA | Septic | Clear | 7.700000 | 5.100000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 10/16/2023 | 12:58 PM
10/09/2023 | Alternative | RoutineScheduled Component Maintenance | 107-13-0030 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced blower and repaired pump supply | This AOSS should now return to normal function after having provided the above state routine maintenance | 11/22/2023 | 09:18 AM
02/16/2023 |  |  | 11-142-0308 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [18 empty] | Replaced float 2/20/23 | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/24/2023 | 12:00 AM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/28/2023 | Alternative | RoutineScheduled Component Maintenance | 177-09-0322-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | - We recommend removing the brush, vines, and small trees next to the distribution box and on the header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2024 | 07:56 AM
05/02/2023 |  | Routine/Scheduled | 2018-143-0025 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Meet with the pumping company and pumped out the septic tank and pumped the trash out of the Clearstream tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | 09:30 AM
10/06/2023 | Alternative | RoutineScheduled | 065-STS-35020 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco | Norweco | Gravity | Pressure | Mound | UV | 450.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 12:00 AM
01/26/2023 |  | RoutineScheduled | 2133-10-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Whitewater ATU | none | Pump | Gravity |  | UV |  | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 02/13/2023 | 08:47 AM
06/07/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Panel was rewired and aerator was reaplaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/06/2023 | Alternative | Reportable Incident Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced filter flush valves. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/16/2023 | Dec 30 1899 12:58PM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-90352 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Disinfection" ,"Dispersal System Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump" ,"Disinfection" ,"Dispersal System Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The drain field & reserve area are across the creek and not accessible. This area should be mowed and maintained in a mowed condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
12/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1200 |  |  | Gravity | Gravity | Pad | Not Applicable | 600.000000 | ["None"] | ["None"] | NA | [17 empty] | overgrowth around pods removed for access | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/27/2023 | Dec 30 1899 12:55PM
07/31/2023 | Alternative | Routine/Scheduled |  | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [29 empty] | Maintenance and Inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/29/2023 | 04:06 PM
02/09/2023 |  | RoutineScheduled | 177-STS-86724 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"Attached Growth Medium"] | ["Auxiliary Filter" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
12/15/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 8.100000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 09:45 AM
03/27/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 3.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Pad | UV |  | ["SludgeScum Accumulation" ,"Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"SludgeScum Accumulation"] | NA | [7 empty] | 03/27/2023 |  | 9.000000 |  |  | 13.700000 |  |  | Will be sent separately | Inspected | changed uv bulb Recommended pump multiple tanks Septic tank 1 ans microfast tank Lab normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
06/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was replaced. Aquaworx bugs were replaced. Bristle filter was added. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/14/2023 | Alternative | RoutineScheduled | 147-07-0123 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Hutchens Septic Services LLC | 1942001509 | Robert | Hutchens, Jr. | 1.000000 | 1500 | Advantex AX-20 |  | Pump | Pressure | Drip | UV |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | None | Clear | [15 empty] | Replaced UV unit and controller | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | 12:00 AM
05/02/2023 | Alternative | RoutineScheduled | SD-09-190 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation","Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/03/2023 | 12:00 AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | System appears to be functioning as designed. Tanks appeared the same as in past years. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/23/2023 | Alternative |  | 154-07-0402 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Chuck | WOYCIK | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/07/2023 | Alternative | RoutineScheduled Component Maintenance | 179-09-0145-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation"] | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Maple tree close to D-box recommend to remove before it causes root problems. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
10/23/2023 | Alternative | Follow-Up Component Maintenance | 177-17-0017-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Sealed supply and return pipe penetrations on pump tank riser. Bleached flushed drip tubing in attempt to improve drip rate. Assisted pumper with proper pump out of Recirc tank. Installed filter screen on recirc pump and drip pump to help reduce clogging of intake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
06/15/2023 |  |  | 033-18-0009-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Multi-Flo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
01/23/2023 |  | RoutineScheduled |  | Buckingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 3.000000 | 6000 | EZ Treat Sandfilter |  | Pump | Gravity | Trenches | Not Applicable | 1400.000000 | ["Effluent Screens","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["Control Operation","BlowerCompressorAerator Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | YES | Musty | Cloudy | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2023 | Jan 1 1900 1:30PM
01/09/2023 |  | RoutineScheduled | {FIPSCode}-STS-14725 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/09/2023 | 12:00 AM
03/17/2023 |  | RoutineScheduled | 132-06-0055 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/19/2023 | 12:00 AM
06/02/2023 |  | Follow-Up | 113-STS-25896 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 1.000000 |  | MicroFast .625 |  | Gravity | Gravity | Trenches |  |  | ["SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 05/25/2023 | Sample Chamber | 11.000000 | [5 empty] | Attached to this report | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/02/2023 | 05:00 PM
11/29/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.950000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 02:45 PM
10/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/20/2024 | 08:56 AM
10/17/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | Dec 30 1899 2:02PM
08/15/2023 | Alternative | Reportable Incident Component Maintenance | 179-16-0344-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 2.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to control panel not being set properly and a failed overide float in the recirc tank. On time for recirc pump was set for 8.0 on proper setting is 0.8. The over recirculation caused alot of growth on the sheets. Wanded sheets and set timer set ro proper setting. Replaced overide float. Drainfield has been cut back by home owner. Proposal to be sent to level D-box as top 2 lines are the only lines getting water. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | EcoPod | Pump | Gravity |  | UV |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | 6.900000 | 9.800000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 08/29/2023 | Dec 30 1899 3:58AM
11/15/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-79879 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Normal level 4in of sludge 4in of solids Pulled and cleaned rsv No signs of infiltration -Recirculation Tank: Normal level Tested floats and pump all working as should Pulled flushed and brushed bio tube filter All plumbing intact and pump moving water properly Floats are aged No signs of infiltration -RSV (Recirculating Splitter Valve): Taken apart cleaned check ball and flushed out Male slide intact and properly working -Discharge/Pump Tank: Arrived on site found tank was in high level due to timer enable float intermittently failing however as of now it is operational plumbing all intact and pump moving water properly Plumbing is aged, pump is free hanging Croc riser Pumped down to normal level -Media Sheets: Flushed and brushed laterals Sheets are bridging and stained locking struts are broken off. Lid is started to deteriorate Ran in test mode until water ran clear -Control Panel: 120 volts coming in All visual and audible alarms functional Discharge pump pulled 8.09 amps Recirc pump pulled 9.90 amps All components working properly Panel is aged -Distribution Box: Normal level 4 lines all intact and taking water properly Speed balancers intact and functional -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/17/2023 | 01:28 PM
11/06/2023 | Alternative | RoutineScheduled | 101-18-0329 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Aquasafe |  | Gravity | Gravity | Trenches | Not Applicable | 150.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/15/2023 | 11:05 AM
05/30/2023 | Alternative | RoutineScheduled Component Maintenance | 061-16-250 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Biweekly inspection. Dripfield grass needs cut. Hopefully no effluent has been surfacing as it would be impossible to pinpoint the leak. In the past 13 days, system pumped an average of 1,075 gals/day at 236.8 gals/dose (avg.) for a total of 13,975 gallons. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
10/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 | 2500 | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"Control Operation" ,"SludgeScum Accumulation"] | NA | [7 empty] | 10/16/2023 |  | 44.000000 | [5 empty] | Will be sent separately | Inspected | Repaired 2 floats Replaced 2 pressure gauges All tanks pumped | This AOSS should now return to normal function after having provided the above state routine maintenance | 11/22/2023 | 09:18 AM
05/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
02/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Sale inspection on an Alternative septic system. The state requires that all Alternative septic system must be inspected every year between January 1 and July 1. And filed with the state and county. The septic control panel is an exterior time dose panel. There are 2 clean outs from the house to the septic tank. The sewer line was camera snaked and was clear. The septic tank has a plastic riser on the outlet side of the tank for access. The effluent level was at the correct level. The tank was pumped out and inspected for any cracks or leak and none were seen. The Whitewater DF60 aeration tank was inspected and the air blower. The pump tank, pump, floats and force main were inspected. The drain field was probed and dry. The buyer did not want d-boxes dug up. So at time of inspection all components that were looked were in working condition | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
08/15/2023 | Alternative | RoutineScheduled | 09-113-182 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/25/2023 | Alternative | RoutineScheduled | 04-197-A17 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 5.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/04/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20452 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | 180 Inspection and sampling | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
07/06/2023 | Alternative | Routine/Scheduled | 550-STS-5875 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | Replaced pump relay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/06/2023 | Dec 30 1899 1:18PM
04/28/2023 | Alternative | RoutineScheduled | 115-10-0133 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 300 | Best 1 |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | Sludge level-4-5" Scum layer on top- 12-16" Sludge layer on bottom- Treatment 6" sludge and not super clear, lot of flock- has good aeration when timer engages, Observed timer engage automatic one cycle- Blower operational- Cleaned blower airfilter. It was moderatly dirty/dusty. Effluent discharge filter was dirty/clogged with a 4 in back up in the entire tank system. Clear effluent observed, trace of sludge- Cleaned effluent screen - levels returned to normal- Alarm tested operational. Owner to arrange pump out with Foutz Septic Service before next year. Risers maybe need replaced as few they plastic screw sleeves are almost all broken. pl-24rc 6" extension | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
08/03/2023 | Alternative | RoutineScheduled | 01-192-354 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | CLEARSTREAM |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 - Blue Crystal tablets added 6 - Bio Max tablets added | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/03/2023 | 12:00 AM
03/06/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Puraflo |  | Pump | Gravity | Trenches |  |  | ["Level Sensor Operation","Septic Tank Baffles"] | ["Level Sensor Operation","Septic Tank Baffles"] | [18 empty] | Baffle filter cleaned. Float adjusted in pump tank. Recommend fencing around Puraflo pods with cattle present | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/06/2023 | 12:00 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/27/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/20/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | ["None"] | ["BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
04/05/2023 |  | Initial Visit | 179-STS-92013 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Pad | UV |  | ["Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | This RT unit requires different float settings and different rest time for the recirc pump. Adjusted per instructions from Orenco. Made minor adjustments to a few of the dial-a-flows in the d-box. Reset all "R" counts back to zero. Recirc contactor released 3 or 4 times with HOA switch in the hand position. No loose connections found. Tested recirc pump operation numerous times afterwards, no further problems. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
05/23/2023 | Alternative | Reportable Incident | 073-STS-93299 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called and stated they had an alarm on Saturday. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. The septic tank needs to be pumped out and also pump the sludge from the bottom of the Clearstream tank when doing so. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/23/2023 | 02:45 PM
12/12/2023 | Alternative | Routine/Scheduled | 166-07-205 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Puraflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 35.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 05:08 PM
04/12/2023 |  | RoutineScheduled | 193-STS-95970 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/30/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | Dec 30 1899 10:05AM
12/14/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | Dec 30 1899 9:10AM
07/15/2023 | Alternative |  |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 | 1000 | 1000 | Pump | Pressure | Drip | Not Applicable |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/30/2023 | 12:00 AM
04/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/17/2023 | Alternative | Routine/Scheduled | 093-11-0065 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | Dec 30 1899 12:35PM
01/26/2023 |  | Routine/Scheduled | {FIPSCode}-STS-4805 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | Jan 1 1900 10:05AM
03/31/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/29/2023 |  |  | 06-142-0437 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Puraflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/12/2023 | 12:00 AM
10/24/2023 | Alternative | Reportable Incident Component Maintenance | 179-STS-89779 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Partial inspection. Homeowner stated he had standing water around tank. Outlet filter is clogged. Grease in septic tank. Spinners in RT unit clogged; barley spinning. RT unit is not level. Drainfield was probed, not wet. No standing water seen. Improper drainage around RT unit. 6" valve box used as inspection port requires replacement. Drainfield mostly overgrown; must mow and establish grass. System requires maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
01/18/2023 | Alternative | RoutineScheduled | SD-02-471 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | trash | Microfast | Gravity | Pressure | Discharge | Chlorination |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 08:10 AM
07/20/2023 | Alternative | Reportable Incident | {FIPSCode}-STS-2751 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [16 empty] | Pumped Out | Replaced UV control panel and gauges | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | Dec 30 1899 12:05PM
04/19/2023 | Alternative | RoutineScheduled | 12-100-0261 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 500 | AQUASAFE |  | Pump | Pressure | Mound | UV | 450.000000 | [] | [] | [18 empty] | REPLACED UV LIGHT BULB. EVERTYTHING WORKING AS IT SHOULD. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/18/2023 | 12:55 PM
10/30/2023 | Alternative | Routine/Scheduled | 2018-143-0086 | Henrico | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1060 | Purasys |  | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | [17 empty] | Performed purasys maintenance procedure. Aerator is running but not blowing air. Propeller is broken. Aerator 5010hrs 46 min, sludge 189 hrs 57 min, clear 121 hrs 36 min | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/30/2023 | 08:38 AM
03/21/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation"] | NA | [7 empty] | 03/21/2023 |  | 47.000000 | [5 empty] | Will be sent separately | Inspected | Lab Pumped all Septic Solution to media and washed media | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
10/03/2023 | Alternative | Pump-Out Only | 17-118-0020 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/10/2023 |  | RoutineScheduled | 177-STS-91940 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [5 empty] | 04/10/2023 |  | 6.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Enabler float in discharge pump tanks was stock close, replaced. RECIRC: HL 1, LL 19, OVERRIDE 0. DISCHARGE: HL 16, PEAK 16, PEAK ETM 23H10M | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
04/26/2023 |  |  | 14-197-A3 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 04/26/2023 |  | 7.020000 | [5 empty] | Will be sent separately |  | BOD: 7.02 TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | 12:00 AM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Tree that was next to the distribution boxes in the past has been cut down. System appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
08/16/2023 | Alternative | RoutineScheduled | 147-16-0079 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  |  |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Dispersal System Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/16/2023 | 12:00 AM
10/06/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Loudoun Environmental Treatment | 1942001460 | Raymond | Kirkpatrick | 2.000000 | 1500 |  |  | Pump |  | Trenches | Not Applicable |  | [] | [] | YES | Musty | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/27/2023 | Alternative | RoutineScheduled |  | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/27/2023 | 12:00 AM
05/15/2023 |  | RoutineScheduled | 175-17-0583 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | 1. All riser on inlet and outlet side of the pump tank are leaking exterior water need to be resealed 2. Some roots growing in the pump tank 3. Two areas on Drainfield water coming to surface need to be dug up and look for broken tube. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | 12:05 PM
09/25/2023 | Alternative | RoutineScheduled | 061-STS-25954 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Fuji Cen5 | Pump | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | [8 empty] | 09/25/2023 | Sample Chamber | 3.690000 | [7 empty] | Thick scum layer in trash tank, hard to measure sludge, outlet side some sludge .fuji setting tank 2" of sludge. If pump only pump the septic tank. Blower, floats, alarms, pump all working. Field dry flushed fuji. 143 Cycles,3.57 hrs. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 10:50 AM
10/19/2023 | Alternative | RoutineScheduled | SD-04-469 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | micrfast |  | Gravity | Pressure | Drip | Not Applicable |  | [] | [] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/19/2023 | 09:15 AM
02/22/2023 |  | Routine/Scheduled | 234-15-153 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | Jan 1 1900 1:42PM
07/14/2023 | Alternative | Routine/Scheduled | NYII-ATHKUK | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | Dec 30 1899 11:50AM
12/20/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation"] | [18 empty] | FAST cleaned | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/05/2024 | 12:00 AM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance | 177-06-0671-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The system is functioning, however, we did remove roots that were blocking the RSV and causing low level alarms. We recommend mowing the drainfield area and maintaining it in a mowed condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
11/15/2023 | Alternative | RoutineScheduled | 2004-143-0290 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Advantex AX20 |  | Pump |  |  |  |  | [] | ["Attached Growth Medium","Control Operation","Recirculation Pump","Level Sensor Operation","Distribution Pump Operation"] |  | Septic | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/15/2023 | 12:00 AM
03/20/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Installed new air blower Septic system is working as it should | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Mound | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The end of the lowest mound (closest to Hillsboro Rd) is soft and spongey. Homeowner is contacting someone to look at. Recommend addressing issue before if becomes a bigger problem. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
01/06/2023 |  | RoutineScheduled | 169-STS-26545 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Eco Flo |  | Gravity | Gravity | Discharge | UV | 200.000000 | ["Attached Growth Medium","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/06/2023 | 12:00 AM
04/24/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [9 empty] | [] | [] |  |  |  | 7.440000 | 5.480000 |  |  |  | 04/24/2023 |  | 22.000000 |  |  | 20.400000 |  |  |  |  | Flow meter not working | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | 03:15 PM
12/22/2023 | Alternative | RoutineScheduled | 17-184-102 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | Musty | Cloudy | 4.500000 | 3.000000 | [14 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
08/16/2023 | Alternative | RoutineScheduled Component Maintenance | 101-02-0288 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend replacing the heater for the hydraulic unit before winter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
01/11/2023 |  | RoutineScheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | Norweco Singulair ATU | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 01/11/2023 |  | 34.000000 | [5 empty] | Will be sent separately | Inspected | Power was off to system was corrected | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
04/11/2023 |  | RoutineScheduled | 177-STS-89445 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/18/2023 | Alternative | Routine/Scheduled |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. PUmp tank - float sensors, pump and controls operating. DBox - at grade - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | 10:30 AM
09/11/2023 | Alternative | Reportable Incident | 09-120-0253A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Went for Alarm call and performed Annual maintenance - Trash Tank: Water level normal. Outlet tee appears to be intact. Due for pump out. - Discharge Tank: Water high due to clogged discharge pump. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge water sensors are functioning properly. Water level normal upon departure. - Aeration: Water level normal. Not due for pump out - Air Pump/Blower: Checked and confirmed aerator is functioning properly. Flushed and cleaned aerator air intake filter. - Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. - Drip Field: Found no signs of surfacing on dispersal field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/11/2023 | Dec 30 1899 11:00AM
12/14/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0141-SWP | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Replaced broken checkvalve in pump tank. Pumpline is broken approximately five feet from the tank. Repairs to be completed as soon as weather allows | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 01/02/2024 | 11:12 AM
08/22/2023 | Alternative | RoutineScheduled | SD-13-056 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | MicroFAST 0.75 |  | Gravity | Pressure | Drip | Not Applicable | 54.000000 | ["SludgeScum Accumulation","Attached Growth Medium"] | ["SludgeScum Accumulation","Attached Growth Medium","Other"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/11/2023 | 04:05 AM
11/28/2023 | Alternative | RoutineScheduled | 107-06-0100 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 2.000000 |  | Advantex AX20 |  | Gravity | Pressure | Trenches | Not Applicable |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles"] | YES | None | Clear | 6.500000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | 08:00 AM
09/28/2023 | Alternative | RoutineScheduled | 061-17-210 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | MicroFast | Pump | Pressure | Drip |  |  | [] | ["BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [17 empty] | 0 scum, 12" of loose sludge, pump tank is clean. Alarm, blower, floats, and pump all working. field dry. Header line is leaking. Drip line came out of header. Fixed on 9/29/2023. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/02/2023 | 12:00 PM
10/20/2023 | Alternative | RoutineScheduled | 182-14-0226 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:00 AM
05/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | [] | YES | [17 empty] | Septic Tank-6"sludge 3"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-016802 ETM-0025735/ Pump2-016975 ETM-0025603/ Puraflo Peat is not ponding or blowing out of the pods but it is no longer fibrous and requires replacement/ No breakout or spongy areas on the drainfield. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12:00 AM
06/10/2023 | Alternative | RoutineScheduled | SD-08-009 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1750 | septic | Aquasafe | Gravity | Pressure | Mound | Not Applicable |  | [] | [] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 08:15 AM
04/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/12/2023 | Alternative | RoutineScheduled | 149-15-0083 | King & Queen | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 2.000000 | 1000 | 750 |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/24/2023 | Alternative | RoutineScheduled | 121-STS-12905 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Southwest Soils, Inc. | 1942001494 | Stephen D. | Dalton | 1.000000 | 1000 | AS 500 |  | Gravity | Pressure | Trenches | Not Applicable | 450.000000 | ["None"] | ["SludgeScum Accumulation","Other"] | NA | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | 01:55 PM
08/26/2023 | Alternative | RoutineScheduled | SD-10-301 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1000 | septic | EZ Treat | Gravity | Pressure | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | 12:30 PM
08/02/2023 | Alternative | RoutineScheduled Component Maintenance | 107-04-0384 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Recommend upgrading timer | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
09/29/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-91798 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation"] | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Blower 3.04 amps. Customer said that installer came back a couple times to work on system, last time installer replaced floats because system was giving alarms. Leak on riser was sealed and inlet side lid on pump tank still buried but no water came in when hose tested and also inspection was done after rain. HL-64. LL-26. OVERRIDE-0. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
10/10/2023 | Alternative | Routine/Scheduled | 14-142-0330 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","None"] | YES | [17 empty] | Effluent filter cleaned. Manifold flushed. Spinners have a greasy build up causing them not to work correctly. Pump screen also showed greasy build up. Cleaned both. Recommend pumpout and refill of advantex tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/10/2023 | Dec 30 1899 10:19AM
06/08/2023 | Alternative | Routine/Scheduled | 06-120-0343A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | Dec 30 1899 1:00PM
06/12/2023 | Alternative |  | 05-142-0125 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1750 | 1000 | 750 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","SludgeScum Accumulation","Recirculation Pump","Level Sensor Operation","Effluent Screens","Distribution Pump Operation"] | YES | Pungent | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 12:00 AM
04/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/11/2023 | 01:03 PM
08/09/2023 | Alternative | Follow-Up |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | replaced old blower control panel with new one. replaced old blower with new blower | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/06/2023 | Alternative | Routine/Scheduled | 800-08-0396 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. BioFilter - peatmoss has some ponding, but overall in good condition. Pump Chamber - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | Dec 30 1899 10:00AM
03/22/2023 |  | Follow-Up | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Disinfection"] | ["Disinfection"] | [8 empty] | 03/22/2023 | Sample Chamber | 19.000000 | [5 empty] | Attached to this report |  | Sample results only: Several week after replacement of the UV-Light sample results. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/13/2023 | Alternative | Pump-Out Only | 03-160-0566 | Montgomery | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner |  |  | Whitewater | [6 empty] | [] | [] | [17 empty] | Pumped Out | - pumped/cleaned septic and pretreatment tank - customer not on maintenance with MSS INC - need to refer to regular provider for more information or customer needs to schedule initial inspection with new provider | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/17/2023 | 12:00 AM
03/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | Dec 30 1899 12:26PM
07/20/2023 | Alternative | Reportable Incident | {FIPSCode}-STS-5576 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Control Operation","Distribution Pump Operation"] | ["Control Operation","Distribution Pump Operation"] | N/A | [17 empty] | Replaced pump relay | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/20/2023 | Dec 30 1899 10:00AM
03/27/2023 |  | RoutineScheduled | 08-184-5003 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/27/2023 | 12:00 AM
10/03/2023 | Alternative | RoutineScheduled | 18-100-0135 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 500 | Aqua Safe |  | Pump | Gravity | Mound | UV | 450.000000 | [] | [] | NA | [17 empty] | Sludge judge test revealed 4-5 inches of accumulation at the bottom of the septic tank. No pumping is needed. System and component are working as designed. UV Light is working. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 02:35 PM
03/30/2023 |  | RoutineScheduled | 14-142-0128 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1000 | Clearstream | [6 empty] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 12:00 AM
12/07/2023 | Alternative | RoutineScheduled | 16-100-0069 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | JEFulbright Septic, LLC | 1942001131 | Jason | Fulbright | 1.000000 | 1500 | Aqua Safe ATU | EcoPod | Pump | Gravity | Mound | UV | 1500.000000 | [] | [] | NA | Musty | Clear | 7.200000 | 3.800000 |  |  |  | 12/07/2023 | Pump Chamber | 1.000000 |  | 220.000000 | 7.000000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 12:15 PM
08/22/2023 | Alternative | Pump-Out Only | 04-160-0598 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000 | LPD | [6 empty] | [] | [] | [18 empty] | System is function but not as designed per alternative codes. - pump chamber riser needs repaired/replaced - inlet line dives into septic tank causing inlet and outlet line to be approx same level in tank - customer would like to proceed with getting an estimate | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/20/2023 | 12:00 AM
06/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
04/10/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [7 empty] | 04/10/2023 |  | 7.000000 | [5 empty] | Will be sent separately | Inspected | Limit soaps oils and grease going into system | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
01/06/2023 |  | Routine/Scheduled | C 800-16-0171 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/06/2023 | Jan 1 1900 1:32PM
03/13/2023 |  | RoutineScheduled | 177-10-0229-ST | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | As a follow-up to last year's inspection, we wanted to check to see if roots had grown back into the Monster Box. We removed roots that had grown back into the box around the seals. We recommend excavating by machine and installing new seals on the Monster Box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
12/06/2023 | Alternative | Routine/Scheduled | 041-STS-257703 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/06/2023 | Dec 30 1899 12:48PM
07/19/2023 | Alternative | Reportable Incident | {FIPSCode}-STS-2572 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | ["Level Sensor Operation","Recirculation Pump"] | ["Attached Growth Medium","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | [17 empty] | System alarming and reported back-up to residence. Found recirc pump failed, pulling extreme high amperage and tripping circuit breakers. Replaced failed recirc pump, serviced effluent screen while on property and pumped system out of high level. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/20/2023 | Dec 30 1899 7:00AM
10/02/2023 | Alternative | RoutineScheduled | 03-197-136 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 5.000000 |  | 0.000000 | [11 empty] | Aerator working, tablets stocked, no odor | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/03/2023 | 12:00 AM
01/29/2023 |  | Routine/Scheduled | 149-STS-10547 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 2.000000 | 1000 |  |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/29/2023 | Jan 1 1900 9:30AM
08/01/2023 | Alternative | RoutineScheduled | 15-100-0415 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | ELJEN |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | [] | [] | YES | [16 empty] | Pumped Out | PUMPED SEPTIC | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/11/2023 | 02:25 PM
01/03/2023 |  |  | 13-197-103 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/03/2023 |  | 3.960000 |  |  | 3.100000 |  |  | Will be sent separately |  | BOD: 3.96 TSS: 3.10 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2023 | 12:00 AM
04/25/2023 |  | RoutineScheduled | 181-06-0250 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 2.000000 | 1500 | Septic Tank Only | MicroFast | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | NO | [17 empty] | The system did not need to be pumped. The blower and spin filters were both cleaned. The controls were operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/24/2023 | 09:15 PM
11/17/2023 | Alternative | RoutineScheduled | 163-STS-333409 | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 RT |  |  |  | Trenches | Not Applicable |  | ["Attached Growth Medium","Septic Tank Baffles","Control Operation"] | ["Attached Growth Medium","Septic Tank Baffles","Control Operation"] | [18 empty] | Breakers were found in off position causing backup. 5 fabric sheets dislodged from "perch". Crack in pump line to be addressed | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/17/2023 | 12:00 AM
07/05/2023 | Alternative | RoutineScheduled | 133 08 0035 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Western Virginia Water Authority | 1942001145 | Michael | Doss |  |  |  |  | Gravity | Pressure | Drip | UV |  | ["None"] | ["None"] | YES | None | Clear | [5 empty] | 07/05/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 06:25 AM
03/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic/atu tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
11/21/2023 | Alternative |  | {FIPSCode}-STS-21755 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/21/2023 |  | 3.690000 |  |  | 9.400000 |  |  | Will be sent separately |  | BOD: 3.69 TSS: 9.40 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/21/2023 | 12:00 AM
06/14/2023 | Alternative |  | 13-163-0037 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Norweco Singulair |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | 12:00 AM
11/14/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - West Piedmont | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | BioMicrobics Fast 3.0 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | Replaced Control panel with upgraded alarm. System alarm is now operational. System has good aeration and does not need pumping at this time. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/15/2023 | 09:30 AM
05/18/2023 | Alternative | RoutineScheduled Component Maintenance | 182-19-0003 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
12/05/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1200 |  |  | Pump | Gravity |  | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | [18 empty] | Peat Moss in 5 Pods needs to be replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/07/2023 | Dec 30 1899 3:40PM
02/20/2023 |  | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | [28 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/01/2023 | 10:34 AM
12/13/2023 | Alternative | Routine/Scheduled | 228-14-0031 | Virginia Beach | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | UV is not working | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/13/2023 | Dec 30 1899 3:00PM
11/20/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | Dec 30 1899 9:34AM
02/21/2023 |  | RoutineScheduled | SWP-04-346 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | The amperage on the pump is very low and water is moving slowly to the Puraflo modules. The pump is reaching the end of its useful life, and replacement is recommended. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
11/07/2023 | Alternative | RoutineScheduled | SD-10-014 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Biomicrobics |  | Pump | Pressure | Drip |  | 150.000000 | [] | [] | [17 empty] | Pumped Out | System was pumped out on 12-5-23 and blower line repaired on 12-14-23 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | 10:55 AM
03/27/2023 | Alternative | RoutineScheduled | 154-06-0891 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 12:00 AM
02/09/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/17/2023 | Dec 30 1899 10:44AM
02/15/2023 |  | RoutineScheduled | {FIPSCode}-STS-58302 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
02/21/2023 |  | RoutineScheduled | 175-05-0304 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic/ Microfast | Pump Tank to Sand Filter | Pump | Pressure | Discharge | Chlorination |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation"] | NA | [7 empty] | 03/15/2023 | Sample Chamber | 27.000000 | [5 empty] | Attached to this report |  | Septic Tank-4"sludge 1"scum/ Delta DF ATU-14"sludge 6"scum/ Pump Tank to Sand Filter-4"sludge 0"scum/ Pump Tank to Spray Discharge-2" Sludge 0"Scum/ Found broken air line for the ATU Blower, repaired and now functioning properly/ Sand filter ponding water, turned the sand but no improvement in drainage, the sand requires replacement / Recommend the Delta DF Unit be pumped out/ Disinfection working properly/ Spray functioning properly/ Counts: Pump1 sand filter-007106/ Pump2 Spray-007722 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12:00 AM
04/19/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Effluent Screens" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | Jan 1 1900 12:48PM
05/01/2023 | Alternative | Reportable Incident | 157-15-0035 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm last night - muted it. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream. Changed the filter in the aerator. Installed an aerator rebuild kit. Replaced the mute button. The timer is set to 2 minutes every 1 hour. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/01/2023 | 09:45 AM
07/14/2023 | Alternative | RoutineScheduled | 196.02.143 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Advantex |  | Pump | Pressure |  |  |  | [] | ["Attached Growth Medium","Recirculation Pump","Level Sensor Operation","Control Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
02/20/2023 | Alternative | Reportable Incident | 171-11-0041 | Pittsylvania | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20-RT |  | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | RTU122504 - System was in an alarm on this retrun trip, found the pumps to be fully functional but the discharge pump was not moving water to the drainfield. We dug and searched to located the air relief valves, found both of them, one was airlocked not allowing water to retrun to the top section of the drainfield. Replaced one air refleif valve and flushed the lines. We dug up and located the upper loop of drip piping. located 3 loops, Opened the end of each loop and flushed the lines to allow more water to flow freely. We attempted to locate some of the lower drip zone, we could not find then and they may also need to be flushed. the lower section of drip tubing appear to have excessive water outside the tubing causeing a water lock situation due to the upper zone not accepting water. With upper zone repairs the system should return to normal operation. It maybe required to have an engineer check the layout of activate the drainfield reserve if the water issue continues. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/01/2023 | 09:30 AM
02/23/2023 |  | RoutineScheduled | 153-STS-20365 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank | Pump Tank | Pump | Pressure | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | YES | [17 empty] | Septic Tank-6"sludge 2"scum/ EZ-Treat Recirc Side-3"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ No pump out needed at this time/ Controls, pumps, floats and alarms functioning properly/ UV-Light bulb and cord replaced during inspection/ Drip Panel Counts: Pump-1452 ETM-322h 36m/ Peak-4/ High-26/ Watermeter-0,126,262.1 On- 15m Off-4h/ Drip rates: Zone1-5.5/ Zone2-5.4/ Zone3-5.3/ Recirc. Pump: On-2.5m Off-12.5m Counts-0094911 ETM-0442807/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
11/29/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 02:10 PM
11/17/2023 | Alternative |  | SWP-05-323 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Whitewater ATU | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | The sludge in the Aerobic Treatment Unit is at a level where pumping is recommended. We recommend pumping the septic tank at the same time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | 12:28 PM
04/03/2023 |  | Routine/Scheduled |  | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration tank - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | 09:30 AM
07/12/2023 | Alternative | Routine/Scheduled | 15-172-0133A | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | The treatment tank needs pumping | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/12/2023 | Dec 30 1899 8:58AM
02/21/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/28/2023 | Alternative | RoutineScheduled | 107-95-0527 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | Sand Filter | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The controls were operating as designed. The sand filter was inspected and was operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | 04:05 PM
05/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
02/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | Dec 30 1899 2:21PM
02/23/2023 |  | Routine/Scheduled | {FIPSCode}-STS-31825 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 500 | Fuji |  | Pump | Gravity | Pad | UV |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [17 empty] | Normal fuji maintenance done. Air filter cleaned. Uv checked. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/23/2023 | Jan 1 1900 11:55AM
03/28/2023 |  | Routine/Scheduled | 234-16-331 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/28/2023 | Jan 1 1900 10:05AM
05/15/2023 |  | RoutineScheduled | 2011-08-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | UV | 250.000000 | ["Disinfection","Distribution Pump Operation","Level Sensor Operation","Effluent Screens"] | ["Disinfection","Distribution Pump Operation","Level Sensor Operation","Effluent Screens"] | YES | Musty | Clear | 7.300000 | [15 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/18/2023 | 12:00 AM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Mound | UV |  | ["Level Sensor Operation","SludgeScum Accumulation","Disinfection"] | ["Level Sensor Operation","Disinfection"] | NA | [17 empty] | Septic Tank-12"sludge 4"scum/ Microfast ATU-12"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ Recommend pump out of the Septic-Microfast Tank/ Blower air filter cleaned and blower working correctly/ UV-Light sleeve cleaned, light functioning properly/ Found the off float was faulty and it was replaced during inspection/ Controls, pumps, floats and alarms are now functioning properly/ Counts: Pump1-660 ETM-48h 35m/ Pump2-659 ETM-48h 26m/ Peak-9/ High-10/ No breakout or spongy areas on the mound area. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/24/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip |  |  | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation","Distribution Pump Operation"] | ["Auxiliary Filter","Septic Tank Baffles","Distribution Pump Operation","Dispersal System Operation"] | [18 empty] | filters cleaned and pressure gauge replaced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/24/2023 | 12:00 AM
11/13/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | Dec 30 1899 10:25AM
03/21/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | septic | fast | Pump | Pressure | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | 8" of sludge 2' of scum in septic tank. 3" of sludge on the fast side. pump tank clean. Floats, blower, alarms, pump all are operational, Field is dry. 20769 events 291.77 hrs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/23/2023 | 08:00 AM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/11/2023 | Alternative | Routine/Scheduled |  | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [10 empty] | Control Operation | YES | [16 empty] | Pumped Out | Pulled and cleaned Orenco filter. System at normal level. Tested alarm for discharge tank. Regular pump out no issues at this time | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/12/2024 | 11:08 AM
11/17/2023 | Alternative | RoutineScheduled | 132-06-0274 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | 12:00 AM
10/12/2023 | Alternative | RoutineScheduled | 2004-143-0006 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Ecoflo |  | Pump |  |  |  |  | [] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation"] |  | None | Clear | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/12/2023 | 12:00 AM
02/20/2023 |  | Routine/Scheduled | 234-18-025 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [12 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/09/2023 | Jan 1 1900 10:00AM
10/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Primary tank pumped | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
05/19/2023 | Alternative | Reportable Incident | 151-14-0076 | Lancaster | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | AOSS - Initial Visit - Claimed traditional septic with pump - found Clearstream ATU - System does not appear to have had any service in years. Pumped trash tank side only - almost 100% sludge - compressor not operational, control panel heavily corroded - requires full maintenance inspection service and probably pumpout of aeration tank as it appears that has been used as a "septic" tank. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/30/2023 | 01:30 PM
07/17/2023 | Alternative | Routine/Scheduled | 041-STS-257856 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches | UV |  | ["Attached Growth Medium","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/17/2023 | Dec 30 1899 2:53PM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance | 061-16-250 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Biweekly inspection. Drip tank was barely in low level alarm on arrival. Low level count is now up to 481. About a month ago, system started a drip cycle when the timer float was open. This may have been due to a glitch in the processor, or to the timer float momentarily closing long enough to initiate a pump cycle. ETM has stopped working in the recirc panel, needs replaced. Dripfield grass needs cut. As is, it's impossible to spot any leaks. In the past 12 days, system has pumped an average of 2,086.4 gals/day at 431.6 gals/ dose (avg.) for a total of 25,037 gallons. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
10/25/2023 | Alternative | Routine/Scheduled | 228-02-1135 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Ecoflo |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Replaced peat moss | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/25/2023 | Dec 30 1899 8:00AM
12/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 12/29/2023 |  | 13.000000 | [5 empty] | Will be sent separately | Inspected | Set control panel and transducer | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/06/2024 | 10:42 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance | 061-16-250 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Biweekly inspection. Grass needs cut in dripfield. In the past 30 days, system pumped an average of 1,720.1 gals/day at 344.02 gals/dose (avg.) for a total of 51,604 gallons. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
03/28/2023 | Alternative | Routine/Scheduled | SHUN-B8AMTZ | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | Dec 30 1899 2:38PM
10/12/2023 | Alternative | RoutineScheduled | 103-STS-92685 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/10/2023 |  | Reportable Incident | 179-STS-89434 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to failed discharge pump. Replaced discharge pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
12/15/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | LP |  |  | Pressure | Trenches | Not Applicable |  | ["Septic Tank Baffles","Dispersal System Operation"] | ["Septic Tank Baffles"] | [18 empty] | pump line repair scheduled for 1/4/24 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2024 | 12:00 AM
09/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 3.000000 | 1250 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 4:00PM
07/07/2023 | Alternative |  | 033-16-0067-SR | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance | SD-06-51 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter"] | NA | [7 empty] | 05/17/2023 |  | 187.000000 | [5 empty] | Will be sent separately | Inspected | Microfast Blower is bad and needs replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/07/2023 | 07:43 AM
11/15/2023 | Alternative | Routine/Scheduled | 03-142-0349 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/15/2023 | Dec 30 1899 3:04PM
04/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/09/2023 | Alternative | RoutineScheduled | 166-12-104 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | sludge checked, system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/19/2023 | Alternative | Reportable Incident Component Maintenance | 179-15-0011-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system over flowing due to a tripped control breaker in the house. Breaker was tripping due to a failed timer float. Replaced float. Will flow up in august to fully inspect the system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
09/26/2023 | Alternative | RoutineScheduled | 085-STS-33918 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 |  | PuraSys SBR |  | Pump | Pressure |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 12:00 AM
04/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
01/13/2023 |  | Reportable Incident | 234-17-441 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the light coming on, breaker keeps tripping, and the pump might not be working. Serviced system. Cleaned the filter in the Clearstream, cleaned the disc filter, and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the aerator motor (new motor serial # 21030578), replaced the P-20 pump (new pump serial # 2112-132762), and replaced the wire nuts in the splice box. Meet with the pumping company and pumped out the pump tank and sludge/trash out of the Clearstream tank. The septic tank needs additional risers on it to be properly inspected in the future. The timer is set to 9 minutes every 2 hours. Could not locate the vacuum breakers - no valve boxes. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/13/2023 | Jan 1 1900 12:00PM
08/20/2023 | Alternative | Routine/Scheduled |  | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 750 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/20/2023 | Dec 30 1899 10:00AM
02/07/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
10/03/2023 | Alternative | RoutineScheduled | 061-STS-22612 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | replaced recirc pump, cleaned filters | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/23/2023 | Alternative | RoutineScheduled | 136-14-0373 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Virginia Septic Solutions LLC | 1942001500 | Justin | Barker | 1.000000 | 1000 | Clearstream 600N |  | Pump | Pressure | Drip | UV |  | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | NA | Musty | Clear | [14 empty] | Pumped Out | Perform pump out of septic tank and pump approximated 1/2 volume of clarifier zone. Customer instructed to refill clarifier zone with water hose until full. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/23/2023 | 12:00 AM
07/06/2023 | Alternative | RoutineScheduled Component Maintenance | 179-17-0086-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
01/23/2023 |  |  | SP-05-265 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
12/13/2023 | Alternative | RoutineScheduled | 103-STS-94360 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Laneview Environmental, LLC | 1942001775 | James | Boone | 3.000000 | 1000 |  |  | Gravity | Pressure | Trenches | UV |  | ["None"] | ["None"] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/11/2023 | Alternative | Follow-Up Component Maintenance | 177-06-0555-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to assist pumper with a pump out on the 2 compartment Ecopod and hose off media. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
05/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/14/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Discharge Middle float repaired Recommend take softner off of system | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
07/10/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-89337 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Auxiliary Filter"] | YES | Musty | [14 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
08/07/2023 | Alternative | RoutineScheduled Component Maintenance | 177-19-0029-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Auxiliary Filter" ,"Effluent Screens" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | As noted previously, the logo screen is dark, but the control panel appears to be functioning properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
01/23/2023 |  | Routine/Scheduled | 041-STS-260035 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/23/2023 | Jan 1 1900 10:52AM
03/31/2023 |  | RoutineScheduled | S-03-111-0143 | Botetourt | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Attached Growth Medium","Auxiliary Filter"] | ["Effluent Screens","Attached Growth Medium","Auxiliary Filter"] | NA | [16 empty] | Inspected | Initial visit to an exhisting system-(20 years approx) Sludge levels-- 1" Scum- 16" sludge in Septic/recirc zone of tank. Discharge zone 13" sludge- Pump tank had about 5 " sludge- No pumping needed Needed- Removed and cleaned RSV - Saw an 8" crack developing in the lid of treatment unit and it has no prop bar to support the lid but it is secure when closed. Removed and Cleaned Biofilter - It was very clogged- Pulled Recirc pump and cleaned the inlet screen very dirty, Flushed and brushed sprayer manifold and sprayed of media. Flushed and Brushed header bars and ran until RSV flow was clear. Floats switches tested ok, alarm ok. - MVP - Counters Recirc pump 587,419 Cycles and ETM(elapsed time in minute) 294370min almost 5,000 hours on recirc pump - Discharge. Ct 19,281 cycles, ETM 25,761mins or 430 hours. Recirc overide Ct 1528 and Discharge ovr county 2234. Drainfield looks good with about 7 lines and d box visable in different color grass. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/03/2023 | Jan 1 1900 9:30AM
07/07/2023 | Alternative | RoutineScheduled Component Maintenance | 179-08-0118-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Dispersal System Operation" ,"Attached Growth Medium" ,"SludgeScum Accumulation" ,"Septic Tank Baffles" ,"Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for routine inspection. System is not processing paper products due to dairy products going down the drain. Told homeowner this needs to stop as it can effect the treatment and cause premature pump outs. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
03/30/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | An inspection on a conventional pump septic system. The septic control panel is an interior demand dose. There is 1 pvc clean out near the house. We camera snaked the sewer line and it was clear. The pump tank, risers, force main, floats and pump were inspected. The 10 port concrete d-box is at ground level. There is a tree 9 feet away from it. The d-box water level is below pipes. There are roots growing in from around the pipes There are 9 header lines. Lines 1,2 and 3 are good and clear. Lines 4-9 are crushed and are unable to get thru. Drain field was probed. Issues that need fixed. Need new d-box and header lines as needed. At this time the septic system is not in working condition. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
07/28/2023 | Alternative | RoutineScheduled Component Maintenance | 177-14-0050-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Inlet T was clogged, unclogged it. Blower 2.74 amps. Treatment is crystal clear. Septic tank needs pumping due to solids in treatment side. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:19 PM
06/09/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-48 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | The Advantex vent kit should be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/27/2023 |  | RoutineScheduled | 179-STS-88336 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Level Sensor Operation" ,"Control Operation" ,"Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Alarm horn for recirc control panel was burnt out again. Horn was just beyond warranty, replaced with a used one in good shape for N/C. Slightly increased the number of daily recirc cycles by reducing off time from 16 min to 14 min. This will help with treatment and move water a little quicker through the system. Cleaned pump intake on recirc pump. After testing float switches, the discharge panel was showing a total of 6 high level alarms and 37 low level alarms. Reset all "R" counts back to zero. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
02/13/2023 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Orenco Advantex |  | Pump | Pressure | Drip |  |  | Auxiliary Filter | Auxiliary Filter | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2023 | 09:41 AM
01/25/2023 |  | RoutineScheduled | {FIPSCode}-STS-69219 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles"] | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Found 2 bad emitters on dripfield causing water to surfacing, replaced them and that fixed the problem. 3.0 gpm after repair. Microfast tank needs pumpout due to 20" of sludge in treatment side. Customer already contacted pumper to get it pumped. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
07/11/2023 | Alternative | RoutineScheduled | 165-STS-333590 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Auxiliary Filter"] | ["Effluent Screens","Auxiliary Filter"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | 12:00 AM
06/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Lines were not receiving equal dose. Distribution box was uncovered and dial flows adjusted | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/24/2023 | Alternative | RoutineScheduled | 150-07-0231 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 3.000000 | 2900 | Septic Tank | Delta Whitewater | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear |  |  | 20.000000 | [11 empty] | Pumped Out | Maintenance/Inspection/Pumping for real estate sale. Septic tank pumped, Delta Whitewater pumped, refilled with fresh water, pump tank- pump, floats, alarm, controls operating properly. Distribution box and surge box concrete, no roots, cracks, leaks, pump dosed, equal distribution to all lines, field probed, 5 lines, no saturation above or between lines, no signs of effluent surfacing. Aerator functioning properly, filter cleaned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/26/2023 | 02:50 PM
04/25/2023 |  | RoutineScheduled | 2001-143-0061 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 2.000000 |  | Clearstream |  | Gravity | Gravity | Discharge | Chlorination |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation"] |  | Musty | Clear |  | 3.700000 |  | 3.100000 | Dechlor 0.00 | [11 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | 12:00 AM
06/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001527 | Jacob | Hott | 1.000000 | 1875 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance | 137-STS-25061 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | 90-Day Inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
07/20/2023 | Alternative | Routine/Scheduled | 085-STS-31961 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Processing Tank - recirc - recirc pump, spray grid & media drapes serviced. Processing Tnak - discharge - float sensors, pump and controls operating. Pumps to community drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | Dec 30 1899 8:00AM
01/04/2023 |  | RoutineScheduled | 177-14-0288-SR | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
11/29/2023 | Alternative | Follow-Up | 041-STS-258000 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Meet with the pumping company and pumped out the septic tank and Clearstream tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/29/2023 | Dec 30 1899 9:00AM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance | 113-STS-25897 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
05/20/2023 | Alternative | RoutineScheduled | 109-04-0947 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | MultiFlo ATU |  | Gravity | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | Annual inspection. 14" of accumulated solids in septic tank. Adequate aeration. Cleaned solids from several treatment unit "socks". Due to solids buildup in treatment unit, the treatment unit and septic tank should be pumped out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/24/2023 | 07:03 PM
03/23/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Upon arrival the airblower was not on nor was the alarm light or buzzer. The septic/atu tank needs pumped | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
10/17/2023 | Alternative | Routine/Scheduled | S 093-19-0086 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | Dec 30 1899 12:55PM
10/04/2023 | Alternative | Follow-Up Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank and pump tank pumped out by others prior. Peat replacement completed. Removed degraded peat by hand and installed new peat. Peat was purchased from Driller Services and degraded peat was disposed at Spotsylvania Refuse. Dug up splitter box and 2 distribution boxes, few roots, added root kill. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
03/23/2023 |  |  | 087-STS-6275 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | EZ Treat | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
12/07/2023 | Alternative | RoutineScheduled | SD-90-068 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.900000 |  |  | 0.650000 |  | 12/07/2023 |  | 33.000000 |  |  | 21.900000 |  |  |  |  | Recommended pumping and cleaning. Will resample after | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/14/2023 | 02:00 PM
09/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank to Puraflo Pump Tank | Pump Tank to the Drainfield | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Distribution Pump Operation"] | ["Attached Growth Medium","Distribution Pump Operation"] | YES | [17 empty] | Septic Tank-6"sludge 0"scum/ Pump Tank to Puraflo Modules-2"sludge/ Pump Tank to the Drainfield-2"sludge/ No pump out needed at this time/ Replaced 1-Zoeller N-140 Pump/ Controls, pumps, floats and alarms are now functioning properly/ Found 1 module was ponding water/ Turned the Puraflo Peat in all 4 modules and improved the drainage/ Counts: Pump1-31125 ETM-45837/ Pump2-31077 ETM-45592/ No breakout or spongy areas on the drainfield area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/02/2023 |  |  | 18-197-A2 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 05/02/2023 |  | 2.490000 | [5 empty] | Will be sent separately |  | BOD: 2.49 TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | 12:00 AM
12/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | Dec 30 1899 9:15AM
08/09/2023 | Alternative | RoutineScheduled | 09-120-0380A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 2750 | 1000 | 1000 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Pungent | Dark Brown | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | 12:00 AM
05/05/2023 |  | Reportable Incident | 234-15-47 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["Control Operation","Disinfection"] | ["Control Operation","Disinfection"] | N/A | [17 empty] | Replaced Salcor UV control pane | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/05/2023 | Jan 1 1900 9:30AM
03/30/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [8 empty] | 517.000000 | [] | [] | [8 empty] | 03/07/2023 | Sample Tap | 0.000000 |  |  | 1.300000 | 66.570000 |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | 12:00 AM
07/13/2023 | Alternative | Routine/Scheduled | 196-09-162 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - lid fractured - box intact - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 07:10 AM
10/10/2023 | Alternative | Routine/Scheduled | 145-STS-259770 | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Pressure | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/10/2023 | Dec 30 1899 11:20AM
01/09/2023 |  | Reportable Incident | 177-06-0074-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to a failed discharge pump drawing 18.1 amps. Replaced pump. Homeowner will contact us in a few weeks to complete a routine inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 09:31 AM
08/08/2023 | Alternative | RoutineScheduled | 09-100-0116 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1000 | Septic Tank | Bio-Coir 400 | Gravity | Pressure | Trenches | Not Applicable | 300.000000 | ["None"] | ["None"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 04:00 AM
12/11/2023 | Alternative | RoutineScheduled | 09-100-0197 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | BIOCOIR ATS-6 |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 | [] | [] | YES | [17 empty] | SLUDGE JUDGE OF SEPTIC TANK REVEALED 4-6" FROM THE BOTTOM EVERYTHING WORKING AS IT SHOULD FIBER IN GOOD CONDITION | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | 11:25 AM
07/12/2023 | Alternative | Routine/Scheduled | 159-12-038 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Advanced Septic |  | Pump | Gravity | Trenches | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service - AquaSafe ATU Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. U.V. - bulb and housing serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/13/2023 | 07:00 AM
03/13/2023 |  | Routine/Scheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 750 | Sandfilter, Recirculating |  | Pump | Gravity | Trenches |  | 360.000000 | ["Attached Growth Medium","Dispersal System Operation"] |  | N/A | [16 empty] | Pumped Out |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/28/2023 | 11:29 AM
01/04/2023 |  | RoutineScheduled | 179-11-0050-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
09/14/2023 | Alternative | RoutineScheduled | 08-197-A3 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | MULTIFLO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 15 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/14/2023 | 12:00 AM
12/07/2023 | Alternative | RoutineScheduled | 87-123 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 12:00 AM
03/17/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Installed new UV Bulb. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/31/2023 | Dec 30 1899 12:26PM
01/27/2023 |  |  | 1998-143-0196 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Puraflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Inspected | Peat moss will likely need to be replaced next year | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | 12:00 AM
10/11/2023 | Alternative | RoutineScheduled Component Maintenance | VAG408152 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Gravity | Gravity | Pad | Chlorination |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Added chlorine and dechlor tablets Heavy amount of cleaners in system Filter was clogged and cleaned | This AOSS should now return to normal function after having provided the above state routine maintenance | 11/22/2023 | 09:18 AM
08/15/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Auxiliary Filter","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Auxiliary Filter","Dispersal System Operation"] | [18 empty] | repairs needed addressed by homeowner | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/15/2023 | 12:00 AM
02/10/2023 |  | RoutineScheduled | 91-197-5001 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/10/2023 | 12:00 AM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/01/2023 |  | Routine/Scheduled | 228-04-1187 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | Jan 1 1900 8:00AM
11/25/2023 | Alternative | Routine/Scheduled | 11-160-0050 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | EcoPod |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/25/2023 | 09:30 AM
08/16/2023 | Alternative | Routine/Scheduled |  | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration tank - normal level - mixing present - compressor serviced. U.V. - bulb and housing serviced. PUmp Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | 08:00 AM
03/23/2023 | Alternative | Reportable Incident | 119-STS-106012 | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | [18 empty] | COSS - Maintenance - GMP2018-02 Replaced failing distribution box with new 8 port concrete DBox. Spliced to existing conveyance line Spliced to existing header lines. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/28/2023 | 06:30 AM
10/11/2023 | Alternative | Pump-Out Only | 01-120-0617A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [16 empty] | Pumped Out | Supervised pump out of 1250 gallon primary septic tank performed by CWS | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | Dec 30 1899 3:50PM
07/19/2023 | Alternative | RoutineScheduled | 09-100-0346 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1250 | DF 50 ATU | PURAFLO | Pump | Gravity | Pad | Not Applicable | 300.000000 | [] | [] | [17 empty] | Pumped Out | PUMP RECENTLY REPLACED AND PUMP STATION PUMPED OUT. NO SLUDGE. PEAT LOOKS GREAT. EVERYTHING WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/03/2023 | 12:45 PM
05/24/2023 |  | Routine/Scheduled | {FIPSCode}-STS-1092 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  |  |  | Pump |  |  |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/24/2023 | Jan 1 1900 1:00PM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-89615 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Disinfection" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend replacing the Fralo Monster Box lid. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
03/28/2023 | Alternative | Routine/Scheduled | 175-05-0207 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | Dec 30 1899 11:07AM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance | 179-14-0162-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump" ,"SludgeScum Accumulation"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend pumping the Septic Tank & the Advantex RT Tank with our staff present to assist the pumper. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
12/15/2023 | Alternative | RoutineScheduled | 145-STS-258138 | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 2.000000 | 1000 | EZ Treat |  | Gravity | Gravity | Pad |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/29/2023 | 12:00 AM
11/30/2023 | Alternative |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | 12:00 AM
03/06/2023 |  |  | VAG408430 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Gravity | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | no discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/06/2023 | 12:00 AM
09/08/2023 | Alternative | RoutineScheduled | 09-125-142 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 3 - Blue Crystal tablets installed 9 - Bio Max tablets installed 1 - Discharge sign installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/08/2023 | 12:00 AM
01/09/2023 |  | RoutineScheduled | 03-197-272 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 12:00 AM
10/27/2023 | Alternative | RoutineScheduled |  | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1750 | 1000 | 750 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | None | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/27/2023 | Dec 30 1899 12:00PM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/19/2023 | Alternative | RoutineScheduled | RRAR-8YBPCG | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 300 | BioMicrobics MicroFast |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. New homeowners. 16" of accumulated solids in bottom of septic tank. 2" of solids crust in septic tank. 14" of accumulated solids in treatment unit. Cleaned blower air filter. Adequate aeration. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/24/2023 | 12:00 AM
10/31/2023 | Alternative | RoutineScheduled | 181-02-0238 (LEGACY ALT. SYSTEM) | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
03/13/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected | Septic tank riser & lid has been damaged by lawn equipment. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/15/2023 | Jan 1 1900 7:20PM
08/22/2023 | Alternative | Follow-Up | 085-STS-34651 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/22/2023 | Dec 30 1899 10:00AM
01/13/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation"] | NA | [17 empty] | Septic-12"sludge 0"scum/ Microfast-20"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ Septic-Microfast Tank requires pump out and media sprayed. Controls, pumps, floats and alarms functioning properly/ Blower air filter cleaded and blower working properly/ Counts: Pump1-6063 ETM-133h 47m/ Pump2-5914 ETM-131h 34m/ Peak-802/ High-35/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/25/2023 | Alternative | Routine/Scheduled |  | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. \DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/29/2023 | Dec 30 1899 12:45AM
01/11/2023 |  | Initial Visit | 182-09-0173 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex | [6 empty] | ["Attached Growth Medium","Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/11/2023 | 12:00 AM
11/30/2023 | Alternative | Follow-Up | 07-197-A7 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | [33 empty] | The system is dead no tablets | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/19/2023 | 12:00 AM
11/01/2023 | Alternative |  | 151-13-0138 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Laneview Environmental, LLC | 1942001775 | James | Boone | 1.000000 | 1250 |  |  | Gravity | Pressure | Pad | Not Applicable |  | ["None"] | ["None"] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/05/2023 | Alternative | Routine/Scheduled | 115-STS-95470 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Trash Tank Condition of above Component Notes for above Component Normal level Less than 1in of sludge less than 1 in of solids No signs of infiltration Recirculation Tank Condition of above Component Notes for above Component Normal level 1 in of suspended solids Tested floats and pump all working as should Pulled and cleaned pump All plumbing intact and pump moving water properly Brushed and flushed bio tube filter No signs of infiltration RSV (Recirculating Splitter Valve) Condition of above Component Notes for above Component Sprayed outside clean Removed rubber grommet cleaned check ball and flushed housing out Male slide intact and functional Discharge/Pump Tank Pump tank/uv Condition of above Component Notes for above Component Normal level 1 in of suspended solids Tested floats and pump all working as should Pulled uv light and flushed housing Uv bulb is showing signs of burning out Pulled and cleaned filter Pulled and cleaned pump All plumbing intact and pump moving water properly No signs of infiltration Media Sheets Condition of above Component Notes for above Component Brushed and flushed laterals Sprayed sheets clean Cups all intact and in proper positions Flushed module until water ran clear Control Panel Condition of above Component Notes for above Component 120 volts coming in All visual and audible alarms functional Discharge pump pulled 5.4 amps Recirc pump pulled 10.6 amps All components working as should Drip Field Condition of above Component Notes for above Component No signs of surfacing Located vacuum, breakers Repair 12/07/23: -Installation of an Ultraviolet Disinfector Bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 09:49 AM
10/04/2023 | Alternative | RoutineScheduled | 2006-143-0145 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Distribution Pump Operation","BlowerCompressorAerator Operation","Control Operation"] | ["Distribution Pump Operation","BlowerCompressorAerator Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/20/2023 | Alternative | Routine/Scheduled | 18-120-0199AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Purasys |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service - Sequential Batch Reactor. Primary septic tank - normal level Processing Tank - sludge return operating. Aeration - submersible aerator serviced - mixing present. Discharge pump - float sensors, pump and controls operating. Surge Box - intact Water level high in distribution box | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | Dec 30 1899 7:45AM
01/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/20/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 03/20/2023 |  | 18.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
06/12/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-5730 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controlsoperating. U.V. - bulb and housing serviced. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | Dec 30 1899 3:30PM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
12/12/2023 | Alternative | Routine/Scheduled | 095-STS-6848 | Williamsburg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | Dec 30 1899 10:00AM
08/23/2023 | Alternative | RoutineScheduled | 18-197-A2 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 4 - Blue Crystal tablets installed 12 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/23/2023 | 12:00 AM
02/22/2023 |  | Reportable Incident | 228-18-0352 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm - installed an aerator rebuild kit. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The return hose is in the pump tank and not the septic tank - should put the return in the septic tank. The timer is set to 9 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | Jan 1 1900 3:00PM
12/01/2023 | Alternative | RoutineScheduled Component Maintenance | 107-11-0219 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 2.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | pumped pump tank filter clog | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | System appears to be functioning as designed. There was some nitrification down hill on the header lines. The box was uncovered and appeared to be functioning as designed. Recommended to contact the installer and monitor the area and advise of any changes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/02/2023 | Alternative |  | 12-113-033 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 08/02/2023 |  | 6.080000 |  |  | 29.200000 |  |  | Will be sent separately |  | BOD: 6.08 TSS: 29.2 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/02/2023 | 12:00 AM
07/17/2023 | Alternative | Routine/Scheduled | 228-04-0832 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | Septic | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | Dec 30 1899 8:30AM
09/05/2023 | Alternative | Routine/Scheduled | 13-120-0079AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | Aquaworx Remediator |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | N/A | [17 empty] | Air filter cleaned. System checked. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | Dec 30 1899 4:13PM
02/24/2023 |  | Reportable Incident | SP-01-593 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Complaint inspection. System was on high level due to a bad diaphragm on filter 2 silinoid valve, replaced diaphragm with a used due to old style valves being discontinued. Replaced silinoid base T for filter 1 with new brass style. Recommend to replaced hydraulic unit when possible. Customer asked for proposal. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
06/14/2023 | Alternative | Routine/Scheduled | 234-13-85 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | Dec 30 1899 12:25PM
12/29/2023 | Alternative | RoutineScheduled | 177-STS-89719 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 0-2 0-1 | 0-0 | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] |  | None | Clear |  |  | 3.000000 | [11 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/29/2023 | 12:00 PM
03/31/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-9358 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 3 Chlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/31/2023 | 12:00 AM
11/13/2023 | Alternative | RoutineScheduled | 182-08-0167 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | repair scheduled to fix air leak and determine raised level in FAST | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 12:00 AM
04/05/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | EcoVirginia LLC | 1942001235 | William | Poindexter | 2.000000 |  | MicroFAST ATU |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Auxiliary Filter"] | ["BlowerCompressorAerator Operation","Auxiliary Filter"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | 12:00 AM
01/05/2023 |  | RoutineScheduled | 18-100-0472 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/10/2023 | 12:00 AM
03/22/2023 |  | RoutineScheduled | 16-113-100 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Clearstream |  | Gravity | Pressure | Drip | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation","Effluent Screens","Dispersal System Operation","Control Operation","Auxiliary Filter","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/22/2023 | 12:00 AM
06/21/2023 | Alternative | RoutineScheduled Component Maintenance | 179-09-0007-SP | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Auxiliary Filter"] | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | Musty | Clear | [5 empty] | 06/21/2023 | Pump Chamber | 110.000000 |  |  | 11.000000 |  |  | Will be sent separately | Inspected | Routine inspection and scheduled effluent sampling. Measured a pH of 7.80 and just .4 mg/L dissolved oxygen in pump tank. Suspect some products containing quats are going down the drain and hurting treatment significantly. Recently installed LGMI appears to be doing its job. Rain was falling during the inspection, and yet water level was down to the bottom float in the pump tank. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/26/2023 | 07:01 AM
05/12/2023 |  | RoutineScheduled | 132-15-0120 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco | Norweco | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/12/2023 | 12:00 AM
11/06/2023 | Alternative | Routine/Scheduled | 17-120-0133A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/06/2023 | Dec 30 1899 9:16AM
05/03/2023 |  | RoutineScheduled | 175-19-0185 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Annual inspection. Effluent was semi-clear/ cloudy. Probably would not pass BOD test. Advised owners to review household cleaning and laundry products. More and more products contain quaternary amonia which adversely affects onsite treatment systems. Septic tank may require a pump-out by next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/10/2023 | 05:56 AM
01/13/2023 |  | Routine/Scheduled | 15-174-0086 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Clearstream needs pumping | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/13/2023 | Jan 1 1900 5:14PM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
11/30/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.990000 | [14 empty] | Recommend having the system pumped | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 02:20 PM
02/22/2023 | Alternative | Pump-Out Only | 159-13-0120 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 2000 | Clearstream | Clearstream | Pump | Gravity | Trenches | Not Applicable | 1000.000000 |  | ["Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Pumped primary septic tank empty and serviced, as recommended during previous service visit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/23/2022 | 08:45 AM
08/29/2023 | Alternative | RoutineScheduled | 12-125-036 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/29/2023 | 12:00 AM
12/29/2023 | Alternative | RoutineScheduled Component Maintenance | 033-07-0348-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2024 | 07:56 AM
03/28/2023 | Alternative | RoutineScheduled |  | Shenandoah | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Gravity | Discharge | UV |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation","Disinfection"] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation","Disinfection"] | [17 empty] | Pumped Out | Blower and UV replaced. Septic/FAST pumped | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 05/23/2023 | 12:00 AM
02/28/2023 | Alternative | RoutineScheduled | 151-11-0091 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | KC Forge Environmental Service | 1942001034 | Kent | Cuthbertson | 4.000000 | 45000 | 15000 | 15000 | Pump | Gravity | Trenches | UV | 21400.000000 | ["None"] | ["Other"] | YES | None | Clear |  | 2.000000 |  |  |  |  | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 06:00 PM
12/01/2023 | Alternative | RoutineScheduled Component Maintenance | 177-06-0591-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
12/05/2023 | Alternative | Reportable Incident Component Maintenance | {FIPSCode}-STS-60610 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 2.000000 |  | none | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due failed field flush solenoid. Replaced solenoid. Will follow up after a rain event to check for infiltration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
05/17/2023 |  |  | 11-142-0120 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Puraflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/02/2023 | 12:00 AM
04/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/26/2023 | Alternative | RoutineScheduled | 14-184-072 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.500000 | 5.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
03/27/2023 | Alternative | Routine/Scheduled | 136-19-0204 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump TAnk - Float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | 09:15 AM
07/28/2023 | Alternative | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Orenco Advantex | [6 empty] | ["Control Operation","Distribution Pump Operation"] | ["Control Operation","Distribution Pump Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/13/2023 | 12:42 PM
06/20/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-92604 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | As noted previously, we are unable to locate the air release valves, but the system appears to be functioning. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | 11:26 AM
02/15/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
09/22/2023 | Alternative | Routine/Scheduled | 155-STS-12094 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/22/2023 | 03:00 AM
05/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping prior to 2024 inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/07/2023 | Alternative | Routine/Scheduled | 09-174-0002 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/07/2023 | Dec 30 1899 9:37AM
03/27/2023 |  | Reportable Incident | 228-18-0004 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Control Operation","Disinfection"] | ["Control Operation","Disinfection"] | N/A | [17 empty] | Replaced UV Bulb | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/27/2023 | Jan 1 1900 11:15AM
05/22/2023 | Alternative | RoutineScheduled | 12-173-055 | Prince Edward | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1500 | Septic | Norweco | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/22/2023 | Dec 30 1899 10:15AM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance | 179-07-0101-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Recirc tank was pumped during inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
09/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-7"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Interior controls, pumps, floats and alarm are functioning properly/ Counts: Pump1-7442 ETM-87h 26m/ Pump2-7506 ETM-87h 22m On-44s Off-2h/ Peak-3577 High-71/ Puraflo peat turned in all 5 modules and in good condition/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/19/2023 | Alternative |  | 003-STS-31642 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | June | Bates | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/19/2023 | Alternative | Routine/Scheduled | 12-160-0147 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | EcoPod |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/19/2023 | 05:15 PM
02/15/2023 |  | RoutineScheduled | {FIPSCode}-STS-78214 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
07/24/2023 | Alternative | RoutineScheduled | 145-06-0002 | Highland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Dispersal System Operation"] | ["Auxiliary Filter","Dispersal System Operation"] | NO | [17 empty] | The system did not need to be pumped. The blower and spin clean filter were both pulled and cleaned. The controls were operating as designed. The treatment unit was operating as designed. The pressure gauge on the return line was not working so a new gauge was installed. The pressure was adjusted. There was return effluent returning to the pump tank so the drip field was operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/08/2023 | 03:55 PM
11/30/2023 | Alternative |  | 113-18-074 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 12:00 AM
03/13/2023 |  | RoutineScheduled | 179-19-0140-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles"] | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. HL 4, LL12, OVERRIDE 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
01/18/2023 |  | Routine/Scheduled | RRAR-9UHLHF | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | Jan 1 1900 11:00AM
08/03/2023 | Alternative | RoutineScheduled | 08-163-0006 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Advantex |  | Pump |  |  |  |  | [] | ["Attached Growth Medium","Control Operation","Level Sensor Operation","Distribution Pump Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/03/2023 | 12:00 AM
03/16/2023 | Alternative | Initial Visit | 151-09-0152 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - initial visit Primary septic tank - normal level - effluent screen serviced. PUmp tank - float sensors, pump and controls operating. BioFilter - Three modules - peatmoss in fair condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/20/2023 | 08:15 AM
02/24/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | None | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 10:15 AM
12/22/2023 | Alternative | Routine/Scheduled |  | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component Normal level 5 in of sludge 1 in of solids Pulled and cleaned filter No signs of infiltration Discharge/Pump Tank Condition of above Component Notes for above Component Normal level Less than 1 in of suspended solids Tested floats and pump all working as should All plumbing intact and pump moving water properly No signs of infiltration Aeration Condition of above Component Notes for above Component Normal level 7 in of suspended solids Air dispersing properly No signs of infiltration Air Pump/Blower Condition of above Component Notes for above Component 120 volts coming in Pulled and cleaned filter Air pump is a little louder than normal but working properly as of now Control Panel Condition of above Component Notes for above Component 120 volts coming in All visual and audible alarms functional Discharge pump pulled 9.75 amps Air pump pulled 4.4 amps All components working as should Distribution Box Dbox/surge box Condition of above Component Notes for above Component Normal level 5 lines all intact and taking water properly Speed balancers intact and functional Pulled minor grass roots Surge box line intact and taking water Pulled minor grass roots Both boxes intact and functional Drain Field Condition of above Component Notes for above Component No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | Dec 30 1899 8:59AM
03/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Effluent pump had failed. It was replaced and the system appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/04/2023 |  |  | {FIPSCode}-STS-4810 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 05/04/2023 |  | 3.250000 |  |  | 2.900000 |  |  | Will be sent separately |  | BOD: 3.25 TSS: 2.90 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/04/2023 | 12:00 AM
12/19/2023 | Alternative |  | 101-08-0092 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Brian | Bennett | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/18/2023 | Alternative | Follow-Up |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [8 empty] | N/A | [7 empty] | 10/18/2023 |  | 5.000000 | 1.000000 |  |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | Dec 30 1899 1:00PM
01/27/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
01/05/2023 |  | Pump-Out Only | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 1.000000 | 1500 |  |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | Jan 1 1900 3:30PM
10/30/2023 | Alternative |  | 033-08-0153-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 | 1250 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 3:40PM
03/24/2023 |  | RoutineScheduled |  | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Blue Ridge | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
10/27/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-154 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. peat was ponding on both sides, fluffed it and mixed it up very good. There was a lot of new looking peat on edges so mixed and fluffed it and drained good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
02/11/2023 |  | RoutineScheduled | 2115-06-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Attached Growth Medium","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles"] | ["Attached Growth Medium","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles"] | YES | Musty | Clear | 7.800000 |  |  | 1.900000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/14/2023 | 12:00 AM
01/31/2023 |  | RoutineScheduled |  | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
02/01/2023 | Alternative | Follow-Up Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Fairfax | Ace Contracting Services, Inc | 1942001120 | Lawrence | Fellenz Jr. |  | 3750 | none | none | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected | Pumped Out All The Tanks To Get All Sludge Out And In 30 to 45 Days We Can Take Another Feces Test | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | Dec 30 1899 3:09AM
05/11/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
09/26/2023 | Alternative | Routine/Scheduled | 09-174-0068 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/12/2023 | Dec 30 1899 9:49AM
07/31/2023 | Alternative | RoutineScheduled Component Maintenance | 2132-10-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity |  | UV |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | 6.800000 | 14.200000 |  |  |  | 07/31/2023 | [7 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 08/15/2023 | 01:44 PM
01/23/2023 |  | Reportable Incident |  | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Three Rivers | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | COSS- Maintenance - GMP2018-02 Replaced conveyance line Replaced Distribution Box with new 8 port concrete DBox Replaced header lines with new. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/24/2023 | 07:00 AM
03/15/2023 |  | Routine/Scheduled | 234-15-367 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | Jan 1 1900 12:50PM
04/04/2023 |  |  | SWP-05-514 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
09/12/2023 | Alternative | Routine/Scheduled | 085-STS-31789 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Outlet tee appears to be intact. Flushed and cleaned effluent screen. Not due for pump out. -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Recirculation at Rest Voltage: 122.6 Recirculation Amperage: 9.5 -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Discharge at Rest Voltage: 122.7 Discharge Amperage: 7.8 - Media Sheets: Cleaned media sheets. Checked and confirmed spray pattern is good. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Control Voltage: 122.3 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | Dec 30 1899 2:16PM
11/08/2023 | Alternative | RoutineScheduled | SD-09-308 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 62.500000 | ["Effluent Screens","Dispersal System Operation"] | ["Dispersal System Operation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/08/2023 | 03:45 PM
09/05/2023 | Alternative | RoutineScheduled | 14-172-0164A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1000 | EcoPod |  | Pump | Pressure | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/19/2023 | 12:00 AM
01/25/2023 |  | Routine/Scheduled | 2005-143-0322 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - rSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | 11:30 AM
06/30/2023 | Alternative | Routine/Scheduled | 550-STS-5885 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | Dec 30 1899 9:45AM
11/13/2023 | Alternative | RoutineScheduled | 154-18-0176 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 3.000000 | 3000 | Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Auxiliary Filter","Attached Growth Medium"] | NA | Musty | Clear | [14 empty] | Inspected | Sludge/Scum Accumulation - Septic 6", ATU 2", Pump Station 0" Spray Emitters Adjusted | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 11:00 AM
01/12/2023 | Alternative | RoutineScheduled | 151-04-159 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Ecoflo |  | Gravity | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | 12:00 AM
06/20/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was replaced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/09/2023 |  | Reportable Incident | 234-18-121 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/09/2023 | Jan 1 1900 7:00AM
07/03/2023 | Alternative |  | 027-STS-17670 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/03/2023 |  | 2.590000 | [5 empty] | Will be sent separately |  | BOD: 2.59 TSS: BDL | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/03/2023 | 12:00 AM
03/29/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, UC Series | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air line was repaired. System should resume functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/07/2023 |  | RoutineScheduled | 175-19-0096 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/17/2023 | 10:44 AM
05/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Aerator not functioning | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
03/13/2023 |  | RoutineScheduled | 177-17-0203-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The drainfield area was wet, but that may be due to recent rains. A follow-up visit this summer has been added to the schedule. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance | 179-17-0444-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
04/20/2023 |  | Routine/Scheduled | 2015-143-0075 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/20/2023 | 03:49 PM
12/21/2023 | Alternative | Routine/Scheduled | 04-160-0556 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable |  | SludgeScum Accumulation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | 02:00 PM
12/08/2023 | Alternative | RoutineScheduled | 154-08-0299 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2500 | MICROFAST |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | [14 empty] | Inspected | Sludge/Scum Accumulation - Septic 10", ATU 6" Blower Amperage - 3a Float Tree Mounted - bracket broken at the time of inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/08/2023 | 10:00 AM
05/30/2023 |  | Routine/Scheduled | 24-02-9997 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | Jan 1 1900 8:00AM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | ATU needs pumped out. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | Dec 30 1899 12:58PM
06/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/05/2023 | Alternative | RoutineScheduled | 2000-91-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | ATU | Polishing Sand Filter | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens"] | YES | Musty | Clear | 7.900000 |  |  | 2.200000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
12/08/2023 | Alternative | RoutineScheduled | 107-16-0062 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MICROFAST |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [7 empty] | 12/08/2023 | Pump Chamber | 2.600000 |  |  | 9.000000 |  |  | Attached to this report |  | THE SYSTEM DID NOT NEED TO BE PUMPED. THE BLOWER AND SPIN FILTERS WERE BOTH PULLED AND CLEANED. THE EFFLUENT SCREEN WAS CLEANED. THE CONTROLS WERE OPERATING AS DESIGNED. THERE WERE NO VISIBLE LEAKS IN THE DRIP FIELD. THERE WAS RETURN EFFLUENT RETURNING TO THE PUMP TANK. THE DRIP FIELD WAS OPERATING AS DESIGNED. THE BOD AND TSS WERE WELL WITHIN THE PERMITTED LIMITS. THE LIDS WERE SECURED. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | 12:45 PM
12/18/2023 | Alternative | RoutineScheduled | 18-160-0153 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner |  |  | Aquasafe | [6 empty] | [] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | Septic | [14 empty] | Will be sent separately |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 12:00 AM
10/06/2023 | Alternative | RoutineScheduled | 10-160-0118 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | King's Alternative Septic | 1942001112 | William | King, II | 1.000000 | 1000 | BioMicrobics Microfast 0.5 |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["None"] | ["None"] | NA | [17 empty] | System is working correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/10/2023 | 12:00 AM
09/25/2023 | Alternative | Follow-Up Component Maintenance | 175-02-0463 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Repaired break in force main at Puraflo modules. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
03/21/2023 | Alternative | Routine/Scheduled | 199-13-0034 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 2000 | Norweco Singulair ATU | Norweco Singulair ATU | Pump | Pressure | Trenches | Not Applicable | 900.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Service - System #2 only. Primary septic tnak - normal level Processing Tank - Trash Tank - normal level Aeration Tank - mixing present - Aspirators (2) serviced. Clarifier - effluent screens (2) serviced. left side housing fractured. Pump Tank - float sensors, pump and controls operating. No surfacing noted. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/22/2023 | Dec 30 1899 9:15AM
05/26/2023 | Alternative | Routine/Scheduled | 151-07-0068 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. BioFilter - Peatmoss in poor condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 11:30 AM
10/18/2023 | Alternative |  | 041-STS-261055 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 500 | 250 | 250 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Pungent | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | Dec 30 1899 11:30AM
01/11/2023 | Alternative | RoutineScheduled | SD-13-440 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | On site for annual inspection. Blower alarm ringing, blower not running. Control power off for septic panel (breaker off in the little cottage in front of the system). Event log in the Aquaworx control panel showed the panel being powered down 5/9/22 and not powered up again until today. Blower was locked up hard. System would have been in high level for months, which would have made the blower work harder. Returned on 1/20 and installed new blower that was supplied by the owner. Could not test as the blower power and septic control power were off again! Owner agreed to restore power. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
08/24/2023 | Alternative | RoutineScheduled Component Maintenance | 182-06-0052 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Media Cleaner added Repaired audible alarm | This AOSS should now return to normal function after having provided the above state routine maintenance | 09/20/2023 | 01:07 PM
01/26/2023 |  | RoutineScheduled | 12-100-0183 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 2.000000 | 2250 | ELJEN |  | Pump | Pressure | Mound | Not Applicable | 1050.000000 | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | FIRST TANK NEEDED TO BE PUMPED SO WE PUMPED-SECOND TANK WAS GOOD-ALL PUMPS AND ALARM WORKING. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/15/2023 | 11:25 AM
05/22/2023 | Alternative | Initial Visit | 157-08-0039 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | Distribution Pump Operation | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit - ALARM System in high level on arrival due to dosing pump failure. Septic tank - normal level - effluent screen serviced. Pump Basin - pump replaced - basin intact, float sensors, and controls operating. BioFilter - peatmoss rootbound - in poor condition - raked / turned best able. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 07:00 AM
05/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/10/2023 | Alternative | Reportable Incident Component Maintenance | 153-STS-20280 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired force main to LPD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
01/16/2023 |  | Reportable Incident | 179-12-0236-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for back up in the house caused by a grease clog in the inlet Tee. Dug up inlet wedge lid removed clog and installed inlet riser to provide future access. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
09/01/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  |  | Trenches | Not Applicable |  | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/01/2023 | 12:00 AM
04/25/2023 |  |  | 027-STS-15314 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 04/25/2023 |  | 7.060000 |  |  | 1.900000 |  |  | Will be sent separately |  | BOD: 7.06 TSS: 1.90 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | 12:00 AM
03/10/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | 1/2" of scum, 12" of loose sludge. Pump tank clean, Alarms and pump are operational. Peat moss is in good shape. Raked it out. Field looks good. 14767 Pump cycles. 444.35 Run time | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | 08:30 AM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was not functioning. When replacing, recommend lifting the housing. The control panel was having problems and did not appear to be cycling correctly. Parts have been ordered for replacement. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/01/2023 | Alternative | RoutineScheduled | 166-10-075 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
04/19/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/23/2023 | 09:32 AM
02/07/2023 |  | RoutineScheduled | 175-10-0330 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 4.000000 |  | Septic Tank #1 | Septic Tank #2 | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation","Recirculation Pump"] | ["Recirculation Pump"] | YES | [17 empty] | Septic Tank #1-18"sludge 6"scum (Requires Pump Out) Septic Tank #2-3"sludge 0"scum/ Advantex Recirc.Tank-2"sludge 0"scum/ Discharge pump tank-2"sludge 0"scum/ Media in good condition / Recirc. pump intake cleaned/ Controls, pumps, floats and alarms functioning properly/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Fixed Leaks in drainfield and pressure gauge | This AOSS should now return to normal function after having provided the above state routine maintenance | 07/06/2023 | 08:40 AM
05/23/2023 |  | Initial Visit | 165-STS-337844 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 2.000000 |  | FAST 0.5 |  | Gravity | Pressure | Drip |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles"] |  | Sulphitic | Dark Brown | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/02/2023 | 12:00 AM
12/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 12/27/2023 | Sample Chamber | 54.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/02/2023 | Alternative | RoutineScheduled | 13-177-1005 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Southwest Soils, Inc. | 1942001494 | Stephen D. | Dalton | 1.000000 | 1500 | Eco Pure |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 | ["SludgeScum Accumulation","Effluent Screens"] | ["Effluent Screens","SludgeScum Accumulation","Other"] | YES | Musty | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/02/2023 | 04:30 PM
01/23/2023 |  | RoutineScheduled |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith | 1.000000 |  | EZ Treat Sandfilter | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/27/2023 | 07:00 PM
02/16/2023 |  | Routine/Scheduled | 033-07-0210-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1250 | Puraflo |  | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Effluent filter cleaned. Peat checked. System appears to be operating normally. Ct 199806, etm 1107.89 hr | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/16/2023 | 11:43 AM
03/29/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
01/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
06/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Loudoun | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["Other"] | [] | YES | [17 empty] | Needs 1 Big Peat Pod Replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/20/2023 | 12:00 AM
02/02/2023 | Alternative | RoutineScheduled | 103-STS-95136 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/20/2023 | Dec 30 1899 12:57PM
07/12/2023 | Alternative | Pump-Out Only | 234-12-110 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | Dec 30 1899 9:00AM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
03/15/2023 | Alternative | RoutineScheduled | 159-17-0218 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Aquasafe |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | [] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
07/10/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-165 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | ["Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Broke down scum layer. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
08/02/2023 | Alternative | RoutineScheduled | 033-15-0107-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Elite Onsite | 1942001726 | Drew | Saunders | 2.000000 | 1750 | 1000 | 750 | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | 05:35 PM
08/01/2023 | Alternative |  | 13-113-181 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 08/01/2023 |  | 2.060000 |  |  | 1.400000 |  |  | Will be sent separately |  | BOD: 2.06 TSS: 1.40 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/01/2023 | 12:00 AM
08/09/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Puraflo in bad condition sample previously failed. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 09/15/2023 | Dec 30 1899 2:41PM
01/24/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [5 empty] | 01/24/2023 |  | 15.000000 |  | 1600.000000 |  |  |  | Will be sent separately | Inspected | Needs jet glass tube and bulb. Wet at bottom of mound. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/13/2023 | Dec 30 1899 8:47AM
05/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 | 1500 |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["Other"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation","Effluent Screens"] | [18 empty] | 3 of the 6 purflo lids are broken in pieces will need 3 new lids also the grids are broken and will need replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/14/2023 | Dec 30 1899 12:10PM
06/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1942001160 | Shane | Majewski | 1.000000 | 1500 |  |  | Pump | Gravity | Trenches | Not Applicable | 750.000000 | ["None"] | ["None"] | NO | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | Dec 30 1899 4:20PM
04/05/2023 | Alternative |  | 109-STS-30807 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Angela | Bischof | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/28/2023 |  | RoutineScheduled | 067-STS-38685 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | Modified Extended Aeration |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | YES | [17 empty] | Total flow to drain fields January 2023 - 90,980 gallons. Average 3,249 gallons per day. All aspects of the system are operational. Wasting of settled mixed liquor from the clarifier to the digester and decanting of supernatant from digester are occurring regularly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | 07:03 PM
11/15/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Clearstream | none | Pump | Gravity |  | UV |  |  |  | NA | Musty | Clear | 7.800000 | 18.500000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 12/01/2023 | Dec 30 1899 10:33AM
12/13/2023 | Alternative | RoutineScheduled | 182-04-0115 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.910000 |  |  |  |  | 12/13/2023 |  | 18.000000 |  |  | 8.800000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 10:00 AM
05/11/2023 |  | RoutineScheduled | 179-STS-87642 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"SludgeScum Accumulation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We also recommend the Advantex tank be pumped due to scum & sludge accumulation in the tank. We recommend the drainfield be mowed and maintained. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
09/15/2023 | Alternative | Routine/Scheduled | 07-160-0068 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Distribution Pump Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/15/2023 | 12:30 PM
08/09/2023 | Alternative | Reportable Incident | C 800-18-0149 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the UV light bulb. Changed the filter in the aerator and changed the mesh screen in the spinfilter. Installed an aerator rebuild kit. The septic tank needs to be pumped out - full of paper - inlet tee stopped up and need to pump the trash off of the top of the Clearstream tank. Could not locate the valve boxes. The timer is set to 4.5 minutes every 1.5 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/09/2023 | Dec 30 1899 3:15PM
04/07/2023 |  | RoutineScheduled | 101-18-0232 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | AquaSafe |  | Gravity | Gravity | Trenches | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/08/2023 | 12:00 AM
03/14/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Need to maintain area | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
12/19/2023 | Alternative | Reportable Incident Component Maintenance |  | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"Septic Tank Baffles" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to infiltration in pump tank and pump being out of time. Proposal to be sent to clean media, pump out all tanks and fix the infiltration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
05/22/2023 | Alternative | RoutineScheduled | SD-11-264 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | PuraFlo |  | Pump | Gravity | Trenches | Not Applicable | 47.500000 | ["Attached Growth Medium","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/22/2023 | 08:00 AM
09/20/2023 | Alternative | RoutineScheduled | SD-12-145 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Battlefield Soil And Septic LLC | 1942001084 | Josh | Johnston | 2.000000 | 2000 | AX-RT |  | Pump | Pressure | Drip |  | 400.000000 | ["Effluent Screens"] | ["Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation"] |  | Musty | Discolored | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/21/2023 | 05:05 PM
01/18/2023 |  | Follow-Up | 06-197-A2 | Wise | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | EHD - Lenowisco | [12 empty] | 450.000000 |  |  |  | Musty | Cloudy | 6.000000 | 5.000000 | [14 empty] | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 01/18/2023 | Jan 1 1900 3:30PM
05/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/06/2023 | Alternative | Routine/Scheduled | 160-03-0209 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 203.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/06/2023 | 12:45 PM
03/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 270505173 | Joshua | Hott | 1.000000 | 1500 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/02/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-89168 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
08/02/2023 | Alternative | RoutineScheduled Component Maintenance | 182-05-0510 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
02/09/2023 |  | Pump-Out Only | {FIPSCode}-STS-1174 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/09/2023 | Jan 1 1900 9:00AM
07/31/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["BlowerCompressorAerator Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | [20 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/17/2023 | 01:51 PM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
06/22/2023 | Alternative | Reportable Incident | 2002-143-0227 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Upgraded Advantex media to new drapes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/26/2023 | 07:15 AM
09/28/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
06/09/2023 | Alternative | Reportable Incident | 157-13-0068 | Mathews | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Delta Environmental Products, UC Series |  | Pump | Pressure | Drip | UV | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Dispatched under the impression this is a COSS with pump - pumped trash tank only for storage - Pump Tank not discharging to drip field. Root in media / aeration tank - blower overheating in alarm Panel appears to have an electrical issue. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/19/2023 | 08:00 AM
09/12/2023 | Alternative | Follow-Up Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/15/2023 | Dec 30 1899 2:41PM
11/01/2023 | Alternative | Follow-Up | 2007-143-0054 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | James Lee Miller III | 1942001468 | Kevin | Blasing | [29 empty] | Replacement of Ecoflo Biofilter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | 09:12 AM
06/26/2023 | Alternative | Pump-Out Only | 136-02-0290 | Gloucester | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 2000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 750.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial visit - ALARM EVENT - Primary septic tank - high level - due to clogged effluent screen in Secondary. Secondary Septic tank - high level - effluent screen clogged - handle broken, unable to remove and service fully - pumped secondary tank for storage. Pump Tank - appears to be normal level Has 6 puraflo peat chambers - sample port holding water - customer agreed to Service agreement. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/28/2023 | 09:30 AM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank filter was clogged and level was very high. Filter was cleaned and the level returned to normal levels. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/25/2023 | Alternative | RoutineScheduled | 136-17-0066 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/20/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation","Distribution Pump Operation"] | ["Distribution Pump Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2024 | 12:00 AM
02/13/2023 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Puraflo |  | Pump | Gravity | Trenches |  | 600.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2023 | 09:15 AM
06/24/2023 | Alternative | RoutineScheduled | SD-10-39 | Fauquier | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | ATU | Polishing Sand Filter | Pump | Gravity | Discharge | UV | 500.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | NA | Musty | Clear | 7.200000 |  |  |  |  | 07/05/2023 | Sample Chamber | 14.000000 |  | 1.000000 | 9.000000 | [5 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/18/2023 | 12:00 AM
09/14/2023 | Alternative |  | 107-06-0336 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","BlowerCompressorAerator Operation"] | ["Effluent Screens","BlowerCompressorAerator Operation"] | YES | Musty | Clear | [15 empty] | replaced squealing blower | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
02/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/03/2023 | Alternative | RoutineScheduled | SD-15-096 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
06/15/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Water was turned on. Serviced the Singulair Treatment unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/12/2023 |  | Routine/Scheduled | 175-STS-14169 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/21/2023 | Jan 1 1900 9:15AM
04/07/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
01/02/2023 | Alternative | RoutineScheduled | SD-13-46 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1200 | septic | Presby | Gravity | Pressure | Trenches |  |  | [] | [] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 03:35 PM
06/13/2023 | Alternative | RoutineScheduled | 104-09-0011 | Amherst | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1500 | Best One |  | Gravity | Gravity | Trenches | Not Applicable | 717.000000 | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/15/2023 | 01:30 PM
08/24/2023 | Alternative | RoutineScheduled Component Maintenance | 2032-96-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity |  | Chlorination |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | 8.200000 | 28.100000 | 0.000000 |  |  | 08/24/2023 | [7 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 09/15/2023 | 02:41 PM
09/13/2023 | Alternative | RoutineScheduled | 11-197-056 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Eljen |  | Gravity | Gravity | Mound | Not Applicable | 200.000000 | ["Dispersal System Operation","SludgeScum Accumulation"] | ["Dispersal System Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
02/02/2023 |  | RoutineScheduled | 179-14-0194-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | NA | Musty | Black | [13 empty] | Will be sent separately | Inspected | Routine inspection. Septic/Microfast tank needs pump out due to solids plus dead bacteria. Customer has been advised a few times to disconnect water softener treatment from sewer and still hasn't done it and is killing the treatment. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
12/07/2023 | Alternative | RoutineScheduled Component Maintenance | 177-16-0293-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Installed new AX 20 lid and pod vent cap for Advantex module. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
11/09/2023 | Alternative | Reportable Incident | 800-STS-14695 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Installed an extension to keep filter from floating out of tee. Changed the diffuser in the Clearstream and changed the filter in the aerator. The Clearstream tank needs to be pump (lots of solids in bottom) and the septic tank needs to be pumped out. There is visible wetness on the drainfield - once it dries need to keep an eye on it. The timer is set to 2 minutes every 3 hour. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/09/2023 | Dec 30 1899 9:00AM
07/05/2023 | Alternative | RoutineScheduled | 109-06-0305 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Multiflo |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Replaced the exhisting contactor and discovered the issue was with other wiring inside and below control. Fixed wiring issue and system returned to normal pumping operation. The wiring issue inside the control box was causing the contactor to not work in RK panel | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/30/2023 | 09:30 AM
04/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/12/2023 | Alternative | RoutineScheduled | 10-163-0058 | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Clearstream |  | Pump | Pressure | Drip |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","Auxiliary Filter","Dispersal System Operation","Effluent Screens"] |  | None | Clear | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/12/2023 | 12:00 AM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Distribution Pump Operation"] | NO | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/10/2023 | 11:17 AM
02/02/2023 |  | Routine/Scheduled | 12-142-0224 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 750.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Serivice Primary septic tank - normal level Processing Tank - RSV, recirc, pump and effluent screen serviced. Treatment Modules - (2) - media drapes & spray grids serviced. Pump Tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | Jan 1 1900 7:30AM
10/18/2023 | Alternative | Reportable Incident | 124-STS-2379 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Other"] | ["Other"] | [18 empty] | Replaced norweco agitator | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
11/08/2023 | Alternative | RoutineScheduled | 109-13-0174 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Aqua Klear |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | Musty | [15 empty] | Inspected | Sludge levels-Trace scum layer, 6" Sludge in Septic tank - Treatmeant tank 6" trace sludge at dischagre -- Pump Tank 0" Sludge, cleaned septic filter is was dirty and backed up -Cleaned air filter. Pump Run time 51698 min & 46,212 cycles, High level 129 Secondary count 6366, Power failure 87.effluent pump runs good- Runs when called. Clear Effluent on top. cleaned air filter. Drip Drain field appears fine no leaks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
12/11/2023 | Alternative | Follow-Up | 133-STS-101233 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/03/2023 |  | RoutineScheduled | 195-Discharge-15326 Greenway Rd. | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Septic Tank Baffles"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 Chlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/03/2023 | 12:00 AM
11/14/2023 | Alternative | RoutineScheduled Component Maintenance | 179-11-0172-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 2.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Blower 1.58 amps. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
05/25/2023 | Alternative | RoutineScheduled | 061-19-006 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"Control Operation" ,"Disinfection" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Disinfection" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Replaced uv lamp as maintenance. Effluent was flowing out top of uv housing. Cleared up after flushing out the sludge. Flush and drip rates both dropped a little from last year. Spin filter and pump intake were cleaned prior to test cycle. Drip rate is still a little above design, so no real worries there. The flush rate is well below design and will need investigation if it drops any further. Drip tubing may be pinched. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
04/27/2023 | Alternative | Follow-Up | 061-STS-24826 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Removed rebar and retrofitted a stainless-steel cable to support biotube. Epoxied holes and resealed riser on inside and out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
04/18/2023 |  |  | 18-142-0041 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Norweco | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | 12:00 AM
04/24/2023 | Alternative | Reportable Incident | 128-10-016 | Essex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Repaired broken air line connector. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
11/09/2023 | Alternative | RoutineScheduled Component Maintenance | 179-16-0111-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Ax20 unit out of level ponding on 1 corner. will send proposal for repair. Field flush improved to 13.6 after cleaning pump intake. PEAK-15, ETM-62H50M. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
01/26/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | [] | [] | [8 empty] | 01/26/2023 | Sample Chamber | 31.000000 |  | 1600.000000 |  |  |  | Attached to this report |  | Sample results only | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
09/29/2023 | Alternative | RoutineScheduled | 043-14-0067 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  | Norweco Trench |  | Pump | Pressure | Trenches | Not Applicable | 750.000000 | ["None"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 12:00 AM
04/26/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
10/25/2023 | Alternative | RoutineScheduled | 14-142-0221 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/29/2023 | Alternative | Routine/Scheduled | 18-120-0276AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. Biofilter - concrete - peatmoss in good condition - raked / turned. Pump Tank - float sensors, pump and controls operating DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | Dec 30 1899 7:15AM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance | 179-16-0367-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 2.000000 |  | EZ Treat Sandfilter | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken (most likely will fell because treatment do not look good). Ez-treat unit lid breaking apart needs to be replace. treatment didn't look to good due to most water going straight to d-box and not much recirculating, adjusted speed level to let more water back to recirc tank. Lowered enabler float 2" to keep it close to help recirculation. Recommend installing sim-tech filter to recirc pump. Grease accumulating in septic tank. Will send proposal for lid and for Sim-tech filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
02/13/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | End caps repaired. System appears to be functioning as designed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
01/26/2023 |  | RoutineScheduled | 04-177-1149 | Pulaski | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - New River | King's Alternative Septic | 1942001094 | David | King | 1.000000 | 1500 | BioMicrobics Microfast 0.5 |  | Gravity | Gravity | Discharge | UV | 120.000000 | ["Disinfection"] | ["Disinfection"] | NA | [17 empty] | Replaced UV light, system is working correctly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/31/2023 | 12:00 AM
10/04/2023 | Alternative | Routine/Scheduled | 14-174-0108 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/04/2023 | Dec 30 1899 9:37AM
01/18/2023 | Alternative |  | 132-06-0246 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Renica | McLaughlin | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/13/2023 | Alternative | RoutineScheduled Component Maintenance | 182-05-0024 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Chlorination |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Unable to check chlorine tablets due to van over feeder Recommend upsize air supply pipe to help with overheating | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
12/21/2023 | Alternative | RoutineScheduled | 08-197-176 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Multiflo |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | 12:00 AM
05/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | none | none | Gravity | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/03/2023 | Alternative | RoutineScheduled | VAG408271 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None |  | 7.400000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | 12:15 PM
06/13/2023 | Alternative | Reportable Incident | 179-13-0013 | Richmond | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Alarm due to clogged filter. Cleaned filter. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/07/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 03/07/2023 |  | 30.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
12/05/2023 | Alternative | Reportable Incident | C 800-16-0010 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 3.000000 | [7 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed a 3/4" brass check valve. The timer is set to 2 minutes every 2 hours. Took 5 year BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | Dec 30 1899 3:00PM
02/03/2023 |  | Initial Visit | 181-17-0048 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 2.000000 | 2500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip |  |  | ["Other"] | ["Other"] | [18 empty] | This was a start-up of the system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | 04:00 PM
01/09/2023 | Alternative | Routine/Scheduled | 073-STS-92734 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Gravity | Gravity | Pad | Not Applicable | 300.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | 10:45 AM
12/14/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | Dec 30 1899 10:35AM
07/28/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Puraflo |  |  | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/28/2023 | 12:00 AM
01/04/2023 |  | RoutineScheduled | 179-17-0186-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Distribution Pump Operation" ,"Dispersal System Operation"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
10/18/2023 | Alternative | RoutineScheduled Component Maintenance | 179-10-0086-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Treatment looks good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
05/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Just a note: Home owner needs to keep drain field mowed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
01/17/2023 |  |  | 033-06-0035-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
02/02/2023 | Alternative | RoutineScheduled | SD-01-700 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | On site to investigate high level alarm and perform annual inspection. Owner had turned off alarm/control breaker in main breaker panel because alarm would not stay silenced. Tank was in high level due to failed pump. Replaced with same model (Zoeller E140) and the brass check valve, which was rotten. The high level alarm float was stuck on internally and replaced. New pump did 38 gpm while drawing 5.40 amps. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
03/15/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Fast | Pump | Pressure | Drip |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | 2" of scum 12" of sludge in septic tank, Fast side has 8" of loose sludge. Pump tank is clean, Blower working, Blower alarm working. Audio alarm for the pump tank is not working. Floats are good. Pump is operational. one of the zones was leaking at the air valves. Owner had that repaired on 3/21/2023. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/23/2023 | 08:00 AM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | EZ treat unit might need servicing in the near future | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Two lateral ends are broken. Homeowner has scheduled repair | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/15/2023 | 06:51 AM
05/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/07/2023 | Alternative | Routine/Scheduled | 05-174-0018 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Ecoflo |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | The peat is starting to turn to mud; keep doing yearly maintenance and we should be able to get a few more years out of it. Tank did not need to be pumped at this time. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/07/2023 | Dec 30 1899 11:36AM
05/02/2023 | Alternative | Routine/Scheduled | 175-04-0278 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | Dec 30 1899 10:25AM
08/14/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-87861 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 4.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [5 empty] | 08/14/2023 |  | 577.000000 |  |  | 67.000000 |  |  | Will be sent separately | Inspected | Routine inspection. Sample taken. Found blower number 2 off, turned back on and is running good 3.79 amps. Influent HEM tested at 105 mg/L , BOD-4.29. EFFLUENT: BOD-577, TSS-67, HEM-8.30. Results fail due to 1 of the 2 blowers being turned off don't know for how long but also slightly improve from past sampling. System is running to its max capacity. Manager should continue to look for ways to reduce water usage. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
11/29/2023 | Alternative | RoutineScheduled Component Maintenance | 175-17-0042 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 09:34 AM
02/02/2023 | Alternative | Initial Visit | 157-07-0294 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | AOSS - Intitial Inspection - Real Estate Inspection. Primary septic tank - pumped empty - requires re-parging. Aeration Tank - dirt in bottom of tank - mixing was present - compressor serviced. Pump Tank - float sensors, pump and controls operating - requires re-parging. DBox - flooded - removed / pumped 700 gallons from DBox alone. Aeration tank refilled with fresh water for re-start. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | 08:00 AM
04/18/2023 |  | RoutineScheduled | SWP-03-475 / SWP-05-424 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
08/02/2023 | Alternative | RoutineScheduled Component Maintenance | 107-87-0055 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 | 1000 | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Septic Tank pumped and stingers installed on inlet | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
09/13/2023 | Alternative | RoutineScheduled | 003-STS-34071 | Albemarle | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Blue Ridge | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [9 empty] | [] | [] | [8 empty] | 09/13/2023 |  | 63.000000 |  |  | 55.400000 | 14.800000 |  |  |  | System is undergoing upgrades. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/15/2023 | 04:35 PM
03/17/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Fast | Pump | Pressure | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | 0 scum, 6" loose sludge in septic tank, 0 in other tank. 23.11 Hrs run time, 199 events. Blower, alarms , floats , and pump are operational. Field is dry with no leaks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/27/2023 | 11:40 AM
01/11/2023 |  | RoutineScheduled | 17-142-0223 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1500 | EZ Treat |  | Pump | Pressure | Drip |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/11/2023 | Jan 1 1900 3:00PM
05/31/2023 | Alternative | RoutineScheduled | 03-160-0552 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000 | LPD |  | Pump | Pressure | Trenches | Not Applicable |  | [] | ["Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | YES | [16 empty] | Inspected | - recommend outlet line filter be cleaned more often - septic tank needs to be pumped/cleaned | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/08/2023 | 12:00 AM
12/12/2023 | Alternative |  | 17-192-166 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/12/2023 |  | 7.030000 |  |  | 2.200000 |  |  | Will be sent separately |  | BOD: 7.03 TSS: 2.20 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 12:00 AM
06/06/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 12:00 AM
07/11/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | 12:00 AM
05/17/2023 | Alternative | RoutineScheduled | 05-160-0417 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000 | Whitewater |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | [] | NO | Septic | Clear | [14 empty] | Inspected | - two vents on blower cover broken, need to be replaced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/23/2023 | 12:00 AM
01/03/2023 |  | Reportable Incident | 04-190-041 | Surry | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [17 empty] | Craig replaced Zoehler 152 pump, pump on/off float, alarm float, float tree, aerator, & check valve. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/03/2023 | Jan 1 1900 11:30AM
09/14/2023 | Alternative | RoutineScheduled | 101-STS-93217 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/21/2023 | Alternative | Reportable Incident | 157-17-0017 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the alarm and red light being on. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. The timer is set to 4 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/21/2023 | 12:30 PM
09/28/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/17/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | Dec 30 1899 2:02PM
09/05/2023 | Alternative | Routine/Scheduled | C-05-111-0227 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | Jan 1 1900 11:00AM
10/10/2023 | Alternative |  | 07-120-0080A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1000 | 750 | 250 | Pump | Gravity | Mound | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/10/2023 | Dec 30 1899 11:00AM
11/13/2023 | Alternative |  | 17-142-0391 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/21/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/13/2023 | Alternative | RoutineScheduled | 17-142-0208 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["Distribution Pump Operation","BlowerCompressorAerator Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/28/2023 | Alternative | RoutineScheduled | 13-100-0472 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 500 | AQUASAFE |  | Pump | Pressure | Mound | UV | 450.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Pumped Out | PUMPED SEPTIC TANK EVERYTHING WORKING AS IT SHOULD REPLACED MUSHROOM VENT AND CLEAN OUT ON DRAIN FIELD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | 12:35 PM
03/31/2023 |  | Pump-Out Only | 228-17-0123 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [8 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/31/2023 | Jan 1 1900 10:00AM
09/26/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [7 empty] | 09/26/2023 | Sample Chamber | 45.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/05/2023 | Alternative | Routine/Scheduled | 166-11-186 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 5.000000 | 25000 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 50.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 07:16 PM
06/10/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/21/2023 | Alternative | Routine/Scheduled | 02-142-0326 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - original to residence. Processing Tank - RSV, recirc pump and effluent screen serviced. Treatment Module - media drapes & spray grid serviced. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/22/2023 | Dec 30 1899 9:00AM
10/19/2023 | Alternative | RoutineScheduled | 05-197-A4 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  | ["Disinfection"] | [19 empty] | Tablets not touching effluent. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
09/09/2023 | Alternative | RoutineScheduled | 2111-06-153m | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Level Sensor Operation"] | ["Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | 7.400000 |  |  | 1.600000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
12/12/2023 | Alternative | Pump-Out Only |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [8 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | Dec 30 1899 10:00AM
04/03/2023 | Alternative | Routine/Scheduled | 093-05-0388 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | Dec 30 1899 1:30PM
08/29/2023 | Alternative |  | 10-125-157 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 8 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/29/2023 | 12:00 AM
11/10/2023 | Alternative | RoutineScheduled Component Maintenance | SWT-05-533 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
01/04/2023 |  | RoutineScheduled | 175-14-0051 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 02:21 PM
10/24/2023 | Alternative | RoutineScheduled | 01-192-214 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | WHITEWATER |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 6 - Blue Crystal tablets installed 12 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/24/2023 | 12:00 AM
09/12/2023 | Alternative | RoutineScheduled | 001-STS-91842 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 2.000000 | 2000 | Septic Tank | PuraFlo | Gravity | Pressure | Pad | Not Applicable | 880.000000 | ["None"] | ["None"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/03/2023 | 10:40 AM
01/07/2023 | Alternative | Initial Visit | SD-12-301 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 2000 | Mini Plant |  | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 03:35 PM
10/26/2023 | Alternative | Routine/Scheduled | 175-STS-13891 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/26/2023 | Dec 30 1899 3:00PM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20471 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter"] | ["Effluent Screens" ,"Auxiliary Filter"] | YES | Musty | Clear | [5 empty] | 06/08/2023 |  | 23.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/07/2023 | 06:25 AM
10/11/2023 | Alternative | RoutineScheduled | 2019-143-0038 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Recirculation Pump","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/28/2023 | Alternative | RoutineScheduled | 07-100-0968 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | BIOCOIR |  | Pump | Gravity | Pad | Not Applicable | 600.000000 | [] | [] | YES | [16 empty] | Pumped Out | SEWAGE PUMP REPLACED ALARM WORKING SLUDGE JUDGE SEPTIC TANK 2" FROM BOTTOM EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | 02:50 PM
04/26/2023 | Alternative | RoutineScheduled Component Maintenance | 175-03-0597 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"BlowerCompressorAerator Operation"] |  | NO | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/15/2023 | 02:02 PM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Effluent filter was clogged and caused the level to be high. Inlet side had a significant amount of grease. Recommend pumping | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/06/2023 |  | Routine/Scheduled | 2011-143-0026 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Hoot |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/06/2023 | 11:38 AM
07/17/2023 | Alternative | Initial Visit | 041-STS-260673 | Chesterfield | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesterfield | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream (was full of paint residue). Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter (full of paint). The UV is not working. Need to pump and clean out the Clearstream, pump tank, and septic tank due to the paint in the tanks. The timer is set to 5 minutes every 2 hours. Did not take samples due to the UV not working. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/17/2023 | Dec 30 1899 2:15PM
07/03/2023 | Alternative | RoutineScheduled | 121-STS-13582 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 |  | Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["Dispersal System Operation","SludgeScum Accumulation"] | NA | Septic | [15 empty] | Pumped Out | 07-03-2023 - replaced Microfast blower - completed required inspection 07-21-23 - pumped and cleaned septic tank, recommend pump chamber be cleaned on next service date | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | 12:00 AM
03/23/2023 |  | Reportable Incident | 234-17-473 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | None | [16 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/23/2023 | Jan 1 1900 9:00AM
09/25/2023 | Alternative | Reportable Incident | 800-STS-14889 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the light going on and off (does not make alarm sound). Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream (was stopped up) and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The alarm was muted on arrival. The septic tank has a lot of grease and paper. The timer is set to 5 minutes every 1 hour. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | Dec 30 1899 3:30PM
06/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Micro Fast Needs Pumping | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | Dec 30 1899 12:05PM
04/19/2023 |  | Routine/Scheduled | 2017-143-0085 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 4 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/19/2023 | 09:30 AM
02/14/2023 |  | RoutineScheduled | 179-17-0276-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The air release valve housing & lid for the lower drip field should be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
02/06/2023 |  | RoutineScheduled | 179-08-0037-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
10/26/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | MicroFast | Pump | Pressure | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [7 empty] | 10/26/2023 | Pump Chamber | 2.000000 | [5 empty] | Attached to this report |  | 0scum 10' of loose sludge, pump tank clean, blower working, filter clean pump, floats, alarms working, Put on timed dosed. Field Dry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/04/2023 | 10:30 AM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/26/2023 | Alternative | RoutineScheduled Component Maintenance | 179-16-0083-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Level Sensor Operation" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Level Sensor Operation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for a property sale inspection. Septic tank was pumped prior to site visit. Inspected septic tank and it was in good condition. The treatment in the recirculation tank looked very good. Dug up distribution box and video inspected header lines and drainfield. All header lines and drainfield trenches were in good condition and getting equal flow. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
06/14/2023 |  |  |  | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
07/03/2023 | Alternative | RoutineScheduled Component Maintenance | SD-09-66 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Pump flow rate meets scouring velocity, but is a little below Bord Na Mona's recommended minimum rate. Pump is now about 10 years old. Recommend replace with stronger pump at next year's inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 04:50 AM
07/18/2023 | Alternative | RoutineScheduled | 109-06-0514 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Alarm call, Found outdoor septic breaker had tripped, water level retunred to normal after. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/30/2023 | 09:30 AM
02/13/2023 |  | RoutineScheduled | SWP-02-206 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
05/17/2023 |  | Routine/Scheduled | 234-13-8 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | Jan 1 1900 8:25AM
05/24/2023 | Alternative | Routine/Scheduled | -STS-43173 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["Attached Growth Medium","Distribution Pump Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/24/2023 | Jan 1 1900 9:45AM
03/20/2023 |  | RoutineScheduled | 177-10-0144-ST | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | The EZ set riser & lid on the outlet side of the Septic Tank are damaged and should be replaced. We also recommend pumping the Septic Tank and the Aerobic Treatment Unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
04/25/2023 |  |  | 19-142-0116 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Microfast | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/12/2023 | 12:00 AM
12/11/2023 | Alternative | Reportable Incident Component Maintenance | SWT-95-471 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Complaint inspection. System was on high level due to leaks on both tanks. Septic tank has 3 leaks: wedge lid, inlet pipe and outlet riser adapter. Pump tank has 3 leaks: inlet pipe, outlet pipe and wedge lid also recommend to seal outlet riser. Tanks were full of water, so we don't know if mid seam has any leaks. Zone #1 gallons per minute were high due to broken adapter, replaced adapter so wet spot should dry out. Will send proposal for sealing leaks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
10/16/2023 | Alternative | RoutineScheduled Component Maintenance | 179-16-0205-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Media is partially clogged due to the use of laundry detergent with quates in it. Two compartment septic tankm needs to be pumped out in the next 6 months. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
02/01/2023 |  | Reportable Incident | 177-STS-87619 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | [14 empty] | Will be sent separately | Inspected | Nine year old blower was making a raspy bearing noise and drawing slightly higher amps. Replaced blower. New blower pulling 3.24 amps. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
04/04/2023 |  | Initial Visit | 182-07-0127 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation","Dispersal System Operation"] | [17 empty] | Pumped Out | Blower replaced. Septic and pump tank pumped out | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/27/2023 | 12:00 AM
02/02/2023 |  | Routine/Scheduled | 550-STS-6561 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream, cleaned the filter in the aerator, and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the mesh screen in the spinfilter. There is visible wetness on the drainfield - most likely from rain - once it dries need to keep an eye on it. The timer is set to 7.5 minutes every 1 hour. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | Jan 1 1900 10:15AM
08/14/2023 | Alternative | RoutineScheduled | 182-04-0173 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  |  | Drip | Not Applicable |  | ["Attached Growth Medium","Control Operation","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation"] | [18 empty] | FAST unit cleaned. Blower panel replaced | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/15/2023 | 12:00 AM
01/11/2023 |  | Initial Visit | 228-19-0108 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 3.000000 |  | 8.000000 | [5 empty] | Owner called due to a red light being on - no alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the filter in the septic tank. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Replaced the UV light bulb and replaced the buzzer. Need to dig up and seal around risers and the aerator should be raised. The timer is set to 5 minutes every 2 hours. Took initial BOD and Fecal samples. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/11/2023 | Jan 1 1900 12:00PM
05/31/2023 | Alternative | RoutineScheduled | 19-160-0003 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2500 | Aquasafe |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | YES | Septic | [6 empty] | 05/31/2023 | Sample Tap | 346.000000 |  |  | 102.000000 |  |  | Attached to this report | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/13/2023 | 12:00 AM
12/07/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-24708 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | [17 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
11/09/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-03-463 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Control Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | Annual inspection. Roots at both wedge lids (septic and pump tank) provide points of infiltration. Recommend adding a riser to grade for septic tank inlet, and cleaning/resealing the pump tank wedge lid. Pump from 2005 has slowed to less than the minimum flow for a 5-pod Puraflo. Recommend replace and shorten pump piping to accommodate adding pump blocks. Peat is worn out and 3 out of 5 pods have serious ponding. Recommend replace peat ASAP to ensure properly treated effluent for the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
05/18/2023 | Alternative | RoutineScheduled | SD-89-422 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Effluent Screens"] | ["Effluent Screens"] | YES | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Annual inspection. Flow rate has slowed about 25% since last major service in 2014. Need to flush laterals. Pump may also be wearing out. Recommend inspecting pump and possibly replacing based on age. Pump was poorly plumbed at installation. Recommend eliminating the camlock (already has a 3" union) and adding a 3" ball valve (has no shut-off valve now). Check valve should be replaced and piping/ union brought up for easier access. If this work is done, both tanks should be pumped out and the concrete lid for pump tank replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/23/2023 | Alternative | RoutineScheduled | 08-113-022 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets added 15 - Bio Max tablets added | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/23/2023 | 12:00 AM
02/01/2023 |  | RoutineScheduled | 127-STS-33900 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 |  | EZ Treat 600 |  | Pump | Pressure | Pad |  |  | ["Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/09/2023 | Jan 1 1900 12:00PM
06/02/2023 |  |  | 2019-143-0093 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Ecoflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 12:00 AM
04/25/2023 |  | Routine/Scheduled | 234-13-73 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | Jan 1 1900 10:05AM
02/20/2023 |  | Routine/Scheduled | 177-11-0248-SR | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Rappahannock | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1250 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [17 empty] | Effluent filter cleaned. Peat needs to be replaced. Riser on septic tank is leaking. Septic needs pumpout. System is working but very slow. 3/13/23 - MW reached out to O&M provider (Dominion Onsite) to see if issues have been rectified. 3/21/23 - O&M provider has stated they have sent him multiple proposals for the peat replacement and the owner has not moved forward with it. MWebb sent out a NOAV. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 02/20/2023 | 11:28 AM
05/16/2023 | Alternative | Routine/Scheduled | C 800-16-0105 | Suffolk | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | routine Service. Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. U.V. - bulb and housing serviced - Bulb / ballast NOT functioning. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/30/2023 | Dec 30 1899 8:45AM
05/19/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/23/2023 | 09:32 AM
04/05/2023 |  | Reportable Incident | 177-STS-88024 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | None | [14 empty] | Will be sent separately | Inspected | Replaced middle zone (2) return side air release valve that was destroyed by a lawn mower. Installed new valve box and lid. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
03/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Hott's Septic Service LLC | 1942001301 | Joshua | Hott | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | 12:00 AM
01/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
08/16/2023 | Alternative | RoutineScheduled | 033-STS-89642 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Two of the lines (2/5) appeared to be more nitrified and receiving more effluent. Distribution Box was uncovered and Dialflows were adjusted. System should return to proper design function now. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/18/2023 |  | RoutineScheduled | 2059-99-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | SBR |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation"] | NA | Musty | Clear | 7.900000 |  |  | 2.000000 |  | 03/21/2023 | Sample Chamber | 2.000000 |  |  | 1.000000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/03/2023 | 12:00 AM
01/24/2023 | Alternative |  | 139-06-0240 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Erica and Stephen | Sharp | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/25/2023 | Alternative | RoutineScheduled | SD-06-414 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-12"sludge 0"scum/ Microfast-24"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ Septic-Microfast Tank requires pump out due to sludge levels/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms are functioning properly/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/24/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/02/2023 | Alternative |  | {FIPSCode}-STS-4677 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 08/02/2023 |  | 9.070000 |  |  | 9.800000 |  |  | Will be sent separately |  | BOD: 9.07 TSS: 9.80 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/02/2023 | 12:00 AM
03/16/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/16/2023 |  | RoutineScheduled | 179-12-0201-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Septic tank in high level due to clogged filter, cleaned and water level went back to normal. Spoke to customer about grease building up in septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
03/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | UV |  | ["Dispersal System Operation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles"] | NA | [17 empty] | 2 airr release valves need replaced broken on zone 1 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/13/2023 | Dec 30 1899 7:05AM
11/14/2023 | Alternative | RoutineScheduled Component Maintenance | 177-07-0083-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Distribution Pump Operation" ,"Recirculation Pump" ,"Attached Growth Medium"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
10/12/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | 12:00 AM
04/26/2023 |  | Routine/Scheduled | 2015-143-0160 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Processing Tank - recirc - recirc pump, media drapes & spray grid serviced. Processing Tank - discharge - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/27/2023 | 06:30 AM
01/27/2023 | Alternative | Initial Visit | 115-STS-96006 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 17.000000 | [7 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream. Changed the filter in the aerator. Installed a 3/4" brass check valve and replaced broken fittings on the headworks. The timer is set to 2 minutes every 2 hours. Took initial BOD sample. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/27/2023 | 10:00 AM
05/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/19/2023 | Alternative | RoutineScheduled Component Maintenance | 2045-02-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Chlorination |  | ["Effluent Screens"] | ["Effluent Screens"] | YES |  |  | 6.600000 | 11.800000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 10/16/2023 | 12:58 PM
08/04/2023 | Alternative | RoutineScheduled | VAG408232 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Sand |  |  | Gravity | Discharge | Chlorination |  | ["Other"] | [] | [18 empty] | No discharge at this time. Plant infringement around system components to be cleared by management. Concrete lid on pump tank compromised and to be replaced as well | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/04/2023 | 12:00 AM
04/06/2023 | Alternative | RoutineScheduled | 015-STS-333860 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["None","Effluent Screens"] | ["None","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/06/2023 | 12:00 AM
12/29/2023 | Alternative |  | 18-100-0018 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
05/11/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Gravity | Gravity | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
01/25/2023 |  | Routine/Scheduled | 228-14-0301 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | Replaced UV ballast | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/25/2023 | Jan 1 1900 8:45AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/03/2023 |  | Routine/Scheduled |  | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. BioFilter - ponding present - peatmoss spent - requires replacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | 09:45 AM
11/13/2023 | Alternative | RoutineScheduled | 162-16-0038 | Nelson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | SEPTIC TANK ONLY | AQUA SAFE | Gravity | Gravity | Trenches | UV |  | ["None"] | ["None"] | NA | [17 empty] | THE SYSTEM DID NOT NEED TO BE PUMPED. THE EFFLUENT FILTER WAS PULLED AND CLEANED. THE BLOWER FILTER WAS PULLED AND CLEANED. THE TREATMENT UNIT WAS OPPERATING AS DESIGNED. THE UV LAMP WAS PULLED AND CLEANED. THE CONTROL WERE OPPERATING AS DESIGNED. THERE WERE NO VISIBLE LEAKS INTHE LEECH FIELD. THE LIDS WERE SECURED. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | 12:00 PM
03/29/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
11/10/2023 | Alternative | RoutineScheduled |  | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1200 | BEST 1 |  | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | YES | Musty | Cloudy | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/05/2024 | 10:15 AM
05/04/2023 |  | Reportable Incident | 033-13-0086-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to failed high level float in discharge tank and failed wiring sending a false high level alarm for recirc tank. Replaced alarm float in discharge tank and replaced wiring from panel to recirc tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
01/24/2023 | Alternative | Routine/Scheduled | 151-04-043 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1500 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 03:39 PM
03/20/2023 |  | Reportable Incident | 07-163-0090 | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | ["Attached Growth Medium","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Petamoss Biofilter Changeout. 03/20/2023 - septic tank pumped - replaced effluent screen with new. 03/23/2023 - biofilter changeout. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/24/2023 | Jan 1 1900 7:00AM
10/25/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 750 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/18/2023 |  | Routine/Scheduled | 234-17-462 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | Jan 1 1900 11:50AM
05/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/20/2023 | Alternative | Routine/Scheduled | 151-12-0082 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Clearstream |  | Gravity | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 45.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 06:32 PM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance | {FIPSCode}-STS-12817 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Chlorination |  | ["Disinfection" ,"Effluent Screens"] | ["Disinfection" ,"Effluent Screens"] | YES | Musty | Clear | 6.300000 | 8.700000 | [6 empty] | 0.000000 |  |  |  |  | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 10/16/2023 | 12:58 PM
09/28/2023 | Alternative | Routine/Scheduled | 093-13-0059 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/28/2023 | Dec 30 1899 10:42AM
08/17/2023 | Alternative | RoutineScheduled | 17-113-088 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","Control Operation"] | YES | Musty | Clear | [15 empty] | 4 - Blue Crystal tablets installed 14 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/17/2023 | 12:00 AM
08/07/2023 | Alternative | Routine/Scheduled | 234-19-210 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | Dec 30 1899 10:05AM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
05/08/2023 | Alternative | RoutineScheduled | 133-STS-97743 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/25/2023 | Alternative | RoutineScheduled | 2019-143-0063 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Norweco Singulair |  | Pump | Pressure | Mound |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","Auxiliary Filter"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/25/2023 | 12:00 AM
01/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["Level Sensor Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Air pre-filter cleaned as preventative maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
04/10/2023 |  | Initial Visit | 145-05-0031 | Highland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Blue Ox | [6 empty] | ["Auxiliary Filter","Dispersal System Operation"] | ["Auxiliary Filter","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | 12:00 AM
08/09/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-2004 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | Dec 30 1899 2:40PM
12/21/2023 | Alternative | Initial Visit | 143-STS-16858 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 500 | MicroFast |  | Gravity | Gravity | Discharge | UV |  | ["None"] | ["None"] | NA | [17 empty] | First annual inspection. 20" of accumulated solids in septic tank. 2" of solids in treatment unit. Cleaned UV bulb. UV bulb disconnected from electrical connector while cleaning. Re-installed UV bulb and tightened connector. Cleaned blower air filter. Adequate aeration and good treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2024 | 07:03 PM
05/05/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | MicroFast | Pump | Pressure | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [17 empty] | 18" of sludge and 4" of scum in holding side, 12' of sludge in fast side, Recommending pumping. Alarms and pump working, Field is dry. 1269:1:25 run time 8837 events | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | 11:45 AM
11/07/2023 | Alternative |  |  | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | [9 empty] | [] | [] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/07/2023 | 12:00 AM
10/05/2023 | Alternative | RoutineScheduled | 061-16-255 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | sludge checked, cleaned filters, system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/06/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic / Ecopod ATU Treatment Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-4"sludge 2"scum/ Ecopod ATU-14"sludge 0"scum/ Pump Tank- 2"sludge 0"scum/ No pump out needed at this time but the Ecopod Tank may need pump out by next year/ Blower air filter cleaned and the blower is working correctly/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-1807 ETM-102h 20m/ Pump2-1768 ETM-100h 33m/ Peak-37/ High-21/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/28/2023 | Alternative | RoutineScheduled Component Maintenance | 175-16-0011 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | 01:58 PM
11/09/2023 | Alternative | RoutineScheduled | 182-01-0415 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter"] | [18 empty] | follow up to determine lack of return from drip field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/09/2023 | 12:00 AM
05/15/2023 | Alternative | RoutineScheduled | 109-07-0338 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation","None"] | ["Distribution Pump Operation","Effluent Screens"] | NA | Musty | [15 empty] | Inspected | Sludge levels- minimal scum and 5" Sludge trace in Septic tank. Tank was pumped after my visit in 2020 , Septic tank ar normal level, Peat still looks new and shows some age, the level in lower and could add some new peat atop the exhisitng to extend the life, No roots observed in Peat, In general good condition for age, has had little use. We may arrange later this summer to add peat. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 05:30 PM
08/30/2023 | Alternative | Routine/Scheduled | 146-01-0305 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Puraflo |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None |  | 6.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | Dec 30 1899 9:40AM
11/27/2023 | Alternative |  | 17-100-0507 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 12:00 AM
04/18/2023 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 01:35 PM
07/28/2023 | Alternative | Routine/Scheduled | 136-11-0260 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Drip | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Aeration Tank - normal level - mixing present - compressor serviced. U.V. disinfection - bulb and housing serviced. Pump Tank - float sensors, pump and controls operating. Drip Field - headworks serviced - field flushed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | 08:30 AM
07/31/2023 | Alternative | RoutineScheduled | 181-02-0335 (LEGACY ALT. SYSTEM) | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | Septic Tank Only | AdvantexAX20 | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The textile sheets were sprayed off. The recirculating pump was pulled and cleaned. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | 04:25 PM
01/13/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 2.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | INstalled effluent filter Do not wash paint brushes in sinks | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
01/21/2023 |  | RoutineScheduled | 133 16 0262 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20 |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 14" of accumulated solids in septic tank. Cleaned recirculation pump basket filter. Flushed treatment unit spray manifold. The discharge pump tank has 4" of accumulated solids. Tested floats, pumps and alarm. The septic tank and treatment unit may need to be pumped out next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/16/2023 | 07:03 PM
11/16/2023 | Alternative | Routine/Scheduled | 151-14-0122 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level 3" of solids with about 8" of sludge -Discharge/Pump Tank: At normal level Pump and floats functioning properly Pump replaced last year -Aeration: At normal level Pulled and cleaned wier and defuser Alarm float working -Air Pump/Blower: Air pump working properly Was rebuilt last year Pulled and cleaned filter -Control Panel: Visual and audible alarms working Air pump pulling 1.5amps Discharge Pulled 11.5 amps -Distribution Box: Plastic dbox located in a overgrown bryer patch Was in good condition and all lines taking water last year Customer needs to clean up dbox and drainfield area -Drain Field: Showing no signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/17/2023 | 02:47 PM
07/13/2023 | Alternative | Reportable Incident | 166-10-175 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm and the aerator not running. Serviced system. Checked the pump, panel, and floats (ok). Installed an aerator rebuild kit. Changed the filter in the aerator and changed the mesh screen in the spinfilter. The Clearstream needs to be pumped as well as the septic tank. The timer was set at 8 hours every 1 minute changed it to 8 minutes every 1 hour. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/13/2023 | 05:00 PM
05/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Whitewater ATU | none | Pump | Gravity | Drip | Not Applicable |  | ["SludgeScum Accumulation"] |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | ATU needs pumping. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | Dec 30 1899 12:05PM
06/15/2023 | Alternative | RoutineScheduled | 08-142-0306 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/13/2023 | 12:00 AM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-91736 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Media is clean, Treatment is crystal clear. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
11/13/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 1.000000 | 1530 | Advantex RT |  | Pump | Pressure | Drip | Not Applicable | 125.000000 | ["Distribution Pump Operation","Effluent Screens"] | ["Control Operation","Distribution Pump Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | replaced pressure gauge & valve on return line, directed flow away from floats. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | 06:00 PM
10/18/2023 | Alternative | RoutineScheduled | 166-18-028 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters, checked sludge, system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/03/2023 |  | RoutineScheduled | 10-192-161 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Aquaklear |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2023 | 12:00 AM
05/09/2023 |  | RoutineScheduled | 147-16-0107 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Clearstream |  | Gravity | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/09/2023 | 12:00 AM
10/24/2023 | Alternative | RoutineScheduled Component Maintenance | VAG408340 | Rockingham | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | UV |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Blower panel and uv system needs replacing | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/22/2023 | 09:18 AM
10/23/2023 | Alternative |  | 099-06-0365-ST | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/20/2023 | Alternative | Reportable Incident | 136-13-0257 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | System is a microfast. Air blower is making a loud screeching noise due to bearings going bad. System hasn't been pumped or looked at in 10 years since System and house were built. The septic tank so much sludge and solids the whole sludge judge is full. Customer wants to due one thing at a time so I built individual estimates. Informed them to do pump and refill before they get the blower replaced so it has clean water to blow into with no resistanc | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 01:40 PM
05/23/2023 |  |  | 2013-143-0103 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Norweco | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 12:00 AM
10/11/2023 | Alternative | RoutineScheduled | 07-197-A6 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 6.000000 |  | 0.000000 | [11 empty] | Aerator running, clear, no odor, both tablets stocked | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
05/18/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 2.000000 | 2000 | Micro-Fast | n/a | Pump | Pressure | Drip | Not Applicable | 100.000000 | ["BlowerCompressorAerator Operation","Effluent Screens"] | ["Effluent Screens","Level Sensor Operation","BlowerCompressorAerator Operation","Control Operation"] | YES | Musty | Clear | [15 empty] | The entire system is operational and in compliance with the health department regulations | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 02:00 PM
07/29/2023 | Alternative | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 | 1500 Gallons | [7 empty] | [] | [] | [18 empty] | Pumping Only | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/29/2023 | 12:00 AM
12/12/2023 | Alternative | RoutineScheduled | 182-14-0084 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [18 empty] | FAST needs to be pumped | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 12:00 AM
01/23/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Attached Growth Medium"] | ["Effluent Screens","Attached Growth Medium"] | NA | [16 empty] | Inspected | Routine Inspection - and Peat moss replacement- Septic tank & Pump Tank were both pumped by Foutz prior to our visit. Effluent filter cleaned, Pump is operational, Alarm is operational. 44629 vs 41085 Pump Cycle count,720.28hr vs 664.12Hr about 3541 cycles and 56 hours pumped since last inspection. Peat moss varies in condition from very poor to like new. Pods 1 and 3 are the worst with peat ponding and signs of breakdown. Pods 2 and 4 are draining but very aged. Pod 5 peat in like new and was added afterwrds during expansion of home. All peat was turned. Extensive roots maybe getting into the drainline due to the plant frowth around the tanks. Reccomend to replace peat in pods 1-4 and additionaly investigate if root blocking a drain pipe or d box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | 09:30 AM
06/15/2023 | Alternative | RoutineScheduled | 150-07-0215 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 3.000000 | 2900 | septic tank | Delta Whitewater | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens"] | ["SludgeScum Accumulation","Level Sensor Operation","Distribution Pump Operation","Control Operation","BlowerCompressorAerator Operation","Effluent Screens"] | YES | Musty | Clear |  |  | 40.000000 | [12 empty] | Septic tank less than 1" fog, 6" sludge. Delta Whitewater 40% SS. Cleaned effluent filter. Serviced aerator. Pump, alarm, floats, controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/23/2023 | 07:25 PM
04/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/16/2023 | Alternative | RoutineScheduled | SD-91-197 | Culpeper | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | Pungent | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the Septic Tank & the ATU due to sludge accumulation in the ATU. As previously noted, we recommend replacing the concrete lid on the pump tank and repairing the pump line. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/02/2023 | 07:17 AM
07/27/2023 | Alternative | Follow-Up Component Maintenance | -STS-27104 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"SludgeScum Accumulation"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | (Note: both tanks pumped out by Butler 2 days ago.) Pump had a date code of 10/03 and was believed to be one of the reasons for a low flow rate of 75 gpm. Installed new pump (same model, E294), brass check valve, sch 80 union, and shutoff ball valve. Also replaced the 3" piping in tank and brought it up so as to make pump removable without entering the tank to retrieve it. Set new pump on 4" blocks to give it some separation from accumulated sludge. Added water to tank and perfomed a drawdown (pumped about 7" of water first to fill the 3" force main). New pump did approximately 124 gpm @ 21.6 gpi. Also replaced all 3 floats as general maintenance (alarm float was 8 years old, other 2 were quite a bit older). Replaced concrete lid on pump tank. No further action required or recommended at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:19 PM
10/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/12/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 | 1500 gallon-Septic W/Fast and 1500 Pump | Septic | MicroFast | Pump | Pressure | Drip | Not Applicable | 75.000000 | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Dispersal System Operation","SludgeScum Accumulation","Level Sensor Operation"] | NA | [17 empty] | 3.5' overall liquid depth with 1" of scum & 8" of sludge in septic tank. pump tank clean. Floats, pump, blower, alarms all working. Field dry. Risers don not fit the best. Added some bolts. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 10:30 AM
07/12/2023 | Alternative | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [8 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | 12:48 PM
02/07/2023 | Alternative | RoutineScheduled | 159-06-0190 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1250 | Clearstream |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/13/2023 | 12:00 AM
09/21/2023 | Alternative | RoutineScheduled Component Maintenance | 015-STS-334434 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 2.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced panel 1 pump nm2 Replaced panel 3 beacon | This AOSS should now return to normal function after having provided the above state routine maintenance | 10/13/2023 | 01:07 PM
02/22/2023 |  | RoutineScheduled | 13-163-0139 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Clearstream |  | Pump | Gravity | Trenches |  |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | 12:00 AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
01/30/2023 |  | RoutineScheduled | 177-13-0127 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
09/26/2023 | Alternative | Reportable Incident Component Maintenance | 154-12-0056 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Complaint inspection. Water backing up into house due to hard grease clogging inlet T in septic tank, removed hard grease from T and pushed garden hose in sewer line with zero tip to clear line. Water started flowing good, had tenant run hot water in tub for 10 minutes and to flush all toilet to verify everything was cleared. Septic tank needs pump out due to sludge levels in treatment side and due to trash in scum layer (wipes and cigar rete butts) treatment looks clear and media is not clogged. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
04/27/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Lower line was cameraed and there were no signs of an issue. DSS adjusted dial flows and releveled the box. The field appears to be evenly distributed. Advise homeowner to monitor and notify if there are any changes | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/12/2023 | Alternative | RoutineScheduled | 103-STS-95842 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | system checked - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/28/2023 | Alternative | RoutineScheduled |  | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.600000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/12/2024 | 04:00 PM
10/09/2023 | Alternative | Routine/Scheduled | 157-14-0073 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The Clearstream tank is pretty dirty - possibly needs to be pumped. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | 04:00 PM
01/05/2023 |  | RoutineScheduled | 177-STS-90219 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation"] | NA | None | Clear | [5 empty] | 01/05/2023 |  | 10.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. RECIRC: HL 3, LL 23, OVERRIDE 222. DISCHARGE: HL 31, OVERRIDE 47. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
07/12/2023 | Alternative | RoutineScheduled | 115-11-0195 | Campbell | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Central | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1500 | Septic Tank | Ecoflo | Pump | Gravity | Trenches | Not Applicable | 750.000000 | ["Auxiliary Filter"] | [] | [18 empty] | Premier Tech effluent filter on output of septic tank is not there needs to add a new filter to keep debris from entering ST 500's | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/26/2023 | 04:30 PM
09/11/2023 | Alternative | RoutineScheduled | SD-04-063 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Drip | Not Applicable | 750.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/22/2023 | 12:00 AM
12/20/2023 | Alternative |  | 101-13-0077 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Dan | Cooper | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/15/2023 | Alternative |  | 087-STS-6429 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Carrington Pump & Irrigation | 1942001121 | John | Carrington |  |  | Norweco |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 12:00 AM
08/16/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
11/22/2023 | Alternative | Follow-Up Component Maintenance | SWP-04-18 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | installed new AX 20 module lid. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
03/16/2023 | Alternative | RoutineScheduled | 061-STS-21303 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Cloverleaf Environmental Consulting, Inc | 1942001135 | Robert | Charnley |  |  | EZ-Treat |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NO | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/11/2023 |  |  | 2006-143-0171 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | 12:00 AM
05/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | a sample will be taken for the peat fiber . Badly broken down. Also 2nd pump tank needs pumped out. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
02/01/2023 |  | RoutineScheduled | 15-100-0209 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | AQUASAFE |  | Pump | Pressure | Mound | UV | 980.000000 | [] | [] | [18 empty] | EVERYTHING WORKING PROPERLY. FIXED 2 BROKEN 1 1/4" CLEANOUTS AT END OF FIELD. ADJUSTED TIMER. CUSTOMER PUT DIRT AROUND MOUND. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/14/2023 | 02:35 PM
02/08/2023 |  | RoutineScheduled | 179-17-0410-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
06/22/2023 | Alternative | RoutineScheduled Component Maintenance | 179-15-0032-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Control Operation"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. 32 psi. Alarm buzzer still ok. Tracks on drip field as if a vehicle was driven there, left note to customer to not do that on field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
11/16/2023 | Alternative |  | 09-184-5004 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/16/2023 |  | 6.430000 |  |  | 12.800000 |  |  | Will be sent separately |  | BOD: 6.43 TSS: 12.8 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | 12:00 AM
11/16/2023 | Alternative | Routine/Scheduled | -STS-5287 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Above normal Level upon arrival due to hydraulically overloaded drainfield Pumped and cleaned system upon approval Refilled to prevent from floating -Recirculation Tank: Pumped and cleaned system All float and pump are functioning properly however they are Aged Pulled and cleaned biotube filter, Floats, and pump screen -RSV (Recirculating Splitter Valve): Pulled and cleaned and made sure it was free of debris -Discharge/Pump Tank: Pumped and cleaned and refilled with water hose to prevent from floating All floats and pump are functioning properly Inlet riser has root intrusion -Media Sheets: Cleaned media sheets Flushed and brushed laterals Flushed media module until water ran clear -Control Panel: 120v into panel All audible and visual alarms are functioning however customer keeps audible unplugged -Drip Field: Blowing in multiple areas | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/17/2023 | Dec 30 1899 1:41PM
03/13/2023 |  | RoutineScheduled | 12-125-066 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","SludgeScum Accumulation","Effluent Screens","Control Operation","Auxiliary Filter"] | YES | Musty | Clear | [15 empty] | 5 Chlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/13/2023 | 12:00 AM
08/16/2023 | Alternative | RoutineScheduled | 033-STS-87958 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/07/2023 |  | RoutineScheduled | 179-12-0262-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
12/05/2023 | Alternative |  | 12-113-118 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/05/2023 |  | 9.270000 | [5 empty] | Will be sent separately |  | BOD: 9.27 TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 12:00 AM
04/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/29/2023 | Alternative | RoutineScheduled Component Maintenance | 179-17-0410-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
10/11/2023 | Alternative | RoutineScheduled | SD-11-261 / SD-12-270 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Dispersal System Operation","Effluent Screens","None"] | ["Attached Growth Medium","Dispersal System Operation","SludgeScum Accumulation","Effluent Screens","None"] | YES | Sulphitic | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | 12:00 AM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"Distribution Pump Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Musty | Clear | [5 empty] | 06/12/2023 |  | 201.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | Dec 30 1899 11:24AM
01/16/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1500 | Septic | pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/16/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
05/26/2023 | Alternative | Follow-Up | 159-04-323 | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Replenished peat. Rebuild pump headworks. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
10/09/2023 | Alternative | RoutineScheduled | 177-STS-87918 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/12/2023 | Alternative | Routine/Scheduled | 17-142-0336 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Annual Maintenance: -Septic Tank: Water level high due to clogged effluent screen. Flushed and cleaned effluent screen and water level returned to normal. Inlet tee appears to be intact. Outlet tee appears to be intact. Not due for pump out -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Recirculation at Rest Voltage: 122.8 Recirculation Amperage: 10.9 -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Discharge at Rest Voltage: 121.9 Discharge Amperage: 11.3 -Media Sheets: Cleaned media sheets. Checked and confirmed spray pattern is good -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Control Voltage: 122.6 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | Dec 30 1899 2:20PM
07/03/2023 | Alternative | Routine/Scheduled | 228-18-0020 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/03/2023 | Dec 30 1899 9:00AM
12/11/2023 | Alternative | RoutineScheduled Component Maintenance | 179-17-0436-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
04/11/2023 | Alternative | RoutineScheduled | 115-05-0126 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Septic Tank Only |  | Pump | Pressure | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Sludge level-under 1" Scum & 10-12" Sludge in Septic tank. Pump Tank 4-6" fine sludge trace. Effluent bio filter screen was clean. Alarm is functional and pump is operational, Float switches both operate as should. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 09:30 AM
06/30/2023 | Alternative | Routine/Scheduled | 02-160-0103 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | 10:30 AM
10/26/2023 | Alternative | RoutineScheduled Component Maintenance | 177-06-0511-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Treatment looks very poor due to fabric softner and water softner regen is going into the septic system. Advised home owner this needs to stop as it effects the treatment in the system. Homeowner to make arrangments to pump out pump tank due to sludge levels. D-box and headers replaced by another company. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
05/23/2023 | Alternative | RoutineScheduled | SD-09-61 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation"] | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection and maintenance completed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
12/07/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-23329 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
01/24/2023 |  | RoutineScheduled | SWP-04-53 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for presale inspection. The first d-box had new growth roots in it not allowing equal flow to the drainfield. Removed roots and retimed d-box. Typical life expectancy for peat moss is 15 to 20 years. The peat moss is age appropriate and in satisfactory condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
03/03/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
11/13/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0241-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"Control Operation"] | ["SludgeScum Accumulation"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Annual inspection. Recommend adding riser and lid to grade on inlet end of septic tank to stop infiltration at the buried wedge lid. Installer ran individual strands of wire from control panel, through 1" LB (buried), and through 1" hole (no conduit or sleeve) into pump tank. Cord connections were made in the pump tank with lots of black tape. Cords need to be connected in a proper junction box, or run through conduit directly into the control panel. The 1" hole in riser is just below grade and a point of infiltration. Septic tank was originally equipped with a filter alarm. The alarm box and VRS sensor have failed, need to be replaced. The 4x2 rubber boot for the force main to sleeve connection is torn and needs to be replaced. On a previous visit, groundwater was seen running through the 4" sleeve. All 5 Puraflo pods had 4-6" of standing water and are not providing any treatment. This could eventually lead to drainfield failure and should be replaced asap. A repair proposal will be provided to the owner. Note: septic tank was pumped out earlier today by Marshall's Septic. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
03/29/2023 |  | RoutineScheduled |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 2-3 0-3 | 0-1 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] |  | None | Clear |  |  | 9.000000 | [11 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 11:00 AM
11/25/2023 | Alternative | Routine/Scheduled | 07-160-0234 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/25/2023 | 12:00 PM
04/13/2023 |  | RoutineScheduled | 175-06-0512 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Pump to drip field needs replacing. Puraflo peat needs replacement | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/02/2023 | 04:23 AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance | {FIPSCode}-STS-12817 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Chlorination |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | 6.800000 | 5.600000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 07/17/2023 | 12:46 PM
11/14/2023 | Alternative | Routine/Scheduled | 228-02-0577 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Gravity |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | Dec 30 1899 2:45PM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
05/15/2023 |  | RoutineScheduled | SD-04-201 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"Effluent Screens" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the septic tank due to scum & sludge accumulation in the tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
03/16/2023 |  | Routine/Scheduled | 2001-143-0062 | Henrico | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Gravity | Gravity | Discharge | Chlorination | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Real Estate Inspection - Annual service - Primary septic tank - normal level - effluent screen serviced. Aeration Tank - normal level - mixing present - compressor serviced. Chlorination units serviced. Supplemental air for discharge not functioning. Discharge point clear of debris and free- flowing. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/20/2023 | 07:00 AM
05/01/2023 |  | RoutineScheduled | 133 05 1023 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | LPD |  | Pump | Pressure | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Routine yearly inspection, Septic Tank under trace scum and 8" sludge trace. Pump tank 6" sludge, Alarm and pump both test operational, Floats switches operational. Checked drainfield -accounted for- all look good.No pumping is needed this year- Counter 9 caps on the LPD drainfield. 5 on one side of main line and 4 on the otherside of yard. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/29/2023 | Alternative | Routine/Scheduled | 03-172-0204A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Not due for pump out. Recirculation pump plumbing has exceeded life expectancy -RSV (Recirculating Splitter Valve): Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. Noted groundwater infiltration within discharge riser -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Media lid safety support struts have failed -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Programming states that discharge is having excessive overrides in discharge. Did drawdown test within discharge and found that it's pumping 0.5" per minute. Adjusted discharge timer to meet permit specifications for 100 gallons per cycle. Control panel has exceeded life expectancy -Distribution Box: Water level normal. Distribution box lid is fractured -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | Dec 30 1899 3:30PM
07/10/2023 | Alternative | Follow-Up | 175-19-0024 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | [18 empty] | Service call only: Replaced faulty pump. Installed Zoeller N-98 115 volts. Counts: Pump-1624 ETM-73h 41m/ Peak-0/ High-14/ Tested and working properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/20/2023 | Alternative | Routine/Scheduled | 150-07-020 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | [8 empty] | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - rsv, recirc pump, and effluent screen serviced. Treatment Module = media drapes and spray grid serviced - bridging present. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 02:20 PM
07/25/2023 | Alternative | RoutineScheduled | 175- | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank | Pump Tank to Sand Filter to Spray Pump Tank | Pump | Pressure | Discharge |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NO | [17 empty] | Septic Tank-3"sludge 0"scum/ Pump Tank to Sand Filters-1"sludge/ Pump Tank to Spray Heads-0"sludge/ No pump out needed at this time/ Sand turned in the sand filters and functioning properly/ Spray heads and timer working correctly/ Controls, pumps, floats and alarms functioning properly/ No ponding or spongy areas on the spray areas/ Counts: Pump1-037515 High Alarm-2,168/ Pump2-000437/ High Alarm-999955 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/08/2023 | Alternative | RoutineScheduled Component Maintenance | SD-04-292 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity |  | Chlorination |  | ["Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
05/26/2023 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Aquarobic Mini Plant | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 12:41 PM
05/12/2023 |  | Pump-Out Only | 234-15-217 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/12/2023 | Jan 1 1900 9:00AM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/21/2023 | Alternative | Follow-Up | SD-04-13 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank and pump tank pumped out byothers prior to peat replacement. Degraded peat was removed by hand with pitch forks/shovels and new peat was installed. Peat was purchased from Driller Services. Degraded peat was disposed at Spotsylvania Refuse. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
04/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Ecoflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/23/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/23/2023 | Dec 30 1899 1:35PM
12/11/2023 | Alternative | Routine/Scheduled | S 800-17-0012 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/11/2023 | Dec 30 1899 9:34AM
09/20/2023 | Alternative | RoutineScheduled | 15-120-0241A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Septic Pro of Virginia | 1942001780 | Eric | Tambourine | 1.000000 | 1000 | Ecopod E60N |  | Pump | Pressure | Drip | Not Applicable | 360.000000 | ["Effluent Screens","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Effluent Screens","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [14 empty] | Pumped Out | Pumped septic tank, cleaned effluent filter, flushed field, reset return pressure, programmed dosing panel based on drawdown. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/25/2023 | Dec 30 1899 12:30PM
01/10/2023 |  | Routine/Scheduled | 228-14-0126 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | Jan 1 1900 1:42PM
10/27/2023 | Alternative | RoutineScheduled | 12-142-0107 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | All In Septic Services | 1942001442 | Dennis | Mitchell | 1.000000 | 1250 | ADVANTEX AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Other"] | ["Auxiliary Filter"] | NA | Musty | Clear | [14 empty] | Inspected | SLUDGE/SCUM ACCUMULATION - SEPTIC 8", TREATMENT TANK 2" **TANK RISER NEEDS REPLACED, UNABLE TO SECURE LID TO TANK | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/27/2023 | Dec 30 1899 3:00PM
04/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | air blower filter was cleaned. Anua and pump tank need pumped out. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
03/29/2023 |  | RoutineScheduled | 08-197-A2 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Multiflo |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/29/2023 | 12:00 AM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance | 182-18-0262 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Trees have been recently planted on/near the end of the drainfield lines. The homeowner is contacting the landscaper to remove the trees and an installer to assess and repair the lines in the appropriate manner. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
10/12/2023 | Alternative |  | 179-STS-92016 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/04/2023 | Alternative | Reportable Incident | 157-01-116 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Arrived on site found panel in alarm. Discharge tank was at normal level. Air pump was not running. Diaphrams are torn. Septic tank was flooded due to a clogged filter. Made recommendations and sent by email. Pulled and cleaned filter onsite | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 09:38 AM
07/05/2023 | Alternative | Initial Visit |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex | [6 empty] | ["None"] | [] | [18 empty] | system start up | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | 12:00 AM
07/14/2023 | Alternative | Pump-Out Only | 128-10-023 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Pumped trash tank and aeration tank empty as recommended during last service visit. Processing tank refilled with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 08:50 AM
04/25/2023 |  | Routine/Scheduled | {FIPSCode}-STS-3098 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | Jan 1 1900 10:30AM
02/24/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed N137 effluent pump & 2" brass check valve. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | Dec 30 1899 11:23AM
05/22/2023 |  |  | 15-113-096 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 05/22/2023 |  | 4.920000 |  |  | 1.600000 |  |  | Will be sent separately |  | BOD: 4.92 TSS: 1.60 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/22/2023 | 12:00 AM
04/08/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/09/2023 | 12:00 AM
09/15/2023 | Alternative | Pump-Out Only |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Aquarobic Mini Plant | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 01:06 PM
02/16/2023 |  | RoutineScheduled | 179-11-0021-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
03/29/2023 |  | RoutineScheduled | 10-192-121 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Discharge | UV | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Level Sensor Operation","SludgeScum Accumulation","BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/19/2023 | Alternative | RoutineScheduled | 159-11-039 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Clearstream |  | Gravity | Gravity | Pad | Not Applicable |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | 12:00 AM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/10/2023 | Alternative | RoutineScheduled | 023-STS-42917 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Western Virginia Water Authority | 1942001145 | Michael | Doss |  |  |  |  | Gravity | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | NA | None | Clear | [5 empty] | 08/10/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | Jan 1 1900 12:15PM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/08/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/04/2023 | Alternative | RoutineScheduled | SD-02-471 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | [9 empty] | [] | [] | [18 empty] | Repair | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/29/2023 | 08:50 AM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/06/2023 | Alternative | RoutineScheduled | 166-04-440 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | system check - okay, checked sludge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/31/2023 |  | RoutineScheduled | 107-07-0635 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers |  |  | 0.5 FAST |  | Gravity | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Dark Brown | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/06/2023 | 08:30 AM
07/05/2023 | Alternative | Initial Visit | 163-STS-336674 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 2.000000 |  | EZ Treat |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation","Effluent Screens","Recirculation Pump"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | 05:00 PM
01/16/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
04/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/08/2023 | Alternative | RoutineScheduled | 109-13-0076 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Aqua Klear |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | NA | Musty | [15 empty] | Inspected | Sludge level- Septic tank 1" scum and 8" slduge- 25" slduge amount of sludge in treatment, Good aeration, Discharge tank 5" sludge- cleaned airfilter. Good aeration. Cleaned Effluent filter. System is operational pump run time 101hr 38 min vs 75hr 56 min and 1274 cycles vs 921 cycles last visit, Flushed filter and drip while running pump in test. Returned to replace alarm control in December- | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
10/11/2023 | Alternative | RoutineScheduled Component Maintenance | 154-14-0220 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
02/22/2023 | Alternative | Initial Visit | 150-03-257 | King William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial site Visit. Primary septic tank - normal level - riser leaking. Aeration Tank - normal level - compressor diaphragm failure - repaired. Pump Tank - float sensors, pump and controls operating. DBox - not found - Absorption field dry. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/23/2023 | 07:15 AM
10/26/2023 | Alternative | Routine/Scheduled | 177-STS-87228 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 400 |  |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [17 empty] | Fuji maintenance procedure performed. Replaced air filter. The middle treatment chamber appears to be clogged. There is a lot of grease in the trash tank. Grease should never be put down the drain. Tank will need to be completely pumped out and refilled at next visit. The outside faucet is turned off in the house. We need a water hookup for a hose to be able to keep parts of the system clean. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/26/2023 | 11:09 AM
11/28/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | EcoPod | Pump | Gravity |  | UV |  |  |  | NA | Musty | Clear | 7.100000 | 21.800000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 12/06/2023 | Dec 30 1899 9:34AM
08/29/2023 | Alternative | Initial Visit | 550-STS-6895 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 5.000000 |  | 1.000000 | [5 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Could not locate valve boxes. The timer is set to 5 minutes every 1 hour 50 minutes. Took initial BOD and Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/29/2023 | Dec 30 1899 2:00PM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
05/26/2023 | Alternative | Reportable Incident | 234-17-243 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the floats and panel (ok). On arrival the pump was loud before cleaning - filter was stopped up - tank should be pumped and cleaned and the Clearstream tank should be pumped and cleaned. Cleaned the filter in the Clearstream, cleaned the UV light bulb, and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 8 minutes every 2 hours. There is wet spots on the drainfield - need to keep an eye on it. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/26/2023 | Dec 30 1899 10:30AM
09/08/2023 | Alternative | Routine/Scheduled | 234-15-367 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | Dec 30 1899 10:30AM
05/23/2023 | Alternative | RoutineScheduled | 07-173-013 | Prince Edward | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1500 | Septic | Delta Df 60 | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/23/2023 | Dec 30 1899 2:00PM
11/16/2023 | Alternative | Reportable Incident | 136-07-0084 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Clearstream. Air pump housing light was on. Diaphragms were busted. Customer approved to do the rebuild. Rebuilt the air pump and cleaned the defuser. Everything working properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:41 AM
09/20/2023 | Alternative | Routine/Scheduled | S 800-17-0384 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. -Aeration: Water level normal. Flushed and cleaned weir. Flushed and cleaned diffuser. Checked and confirmed high level alarm float is functioning properly. -Air Pump/Blower: Checked and confirmed aerator is functioning properly. Flushed and cleaned aerator air intake filter. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/06/2023 | Dec 30 1899 2:27PM
09/25/2023 | Alternative | RoutineScheduled Component Maintenance | 179-07-0322-ST | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Media starting to show its age. Alarm floats were very close with timer enabler float adjusted them. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
11/15/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None | Clear | [15 empty] | This report got missed when November Reports were submitted. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/15/2024 | 10:45 AM
10/25/2023 | Alternative | Routine/Scheduled | 03-120-0640AE | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/25/2023 | Dec 30 1899 5:02PM
10/10/2023 | Alternative | RoutineScheduled | 05-100-0463 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | ECOFLO |  | Pump | Gravity | Mound | Not Applicable | 600.000000 | [] | [] | YES | [17 empty] | SLUDGE JUDGE SEPTIC TANK 4-5" FROM BOTTOM EVERYTHING WORKING AS IT SHOULD. PEAT IN GOOD CONDITION | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 09:05 AM
07/20/2023 | Alternative | RoutineScheduled | 19-142-0087 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/12/2023 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Norweco Singulair ATU |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Effluent Screens"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | 10:20 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | EcoPod | Pump | Gravity |  | UV |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | Musty | Clear | 6.900000 | 18.600000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 08/29/2023 | Dec 30 1899 3:58AM
01/12/2023 | Alternative | Routine/Scheduled | 157-17-0085 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Multiflo FTB |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary Septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Aertion Tank - mixing present - compressor serviced - socks clean Pump Tank - float sensors, pump and controls operting. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | 08:00 AM
08/09/2023 | Alternative | RoutineScheduled | 14-160-0136 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | King's Alternative Septic | 1942001112 | William | King, II | 1.000000 | 1000 | BioMicrobics Microfast 0.5 |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["None"] | ["None"] | NA | [17 empty] | System is working as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/17/2023 | 12:00 AM
11/17/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | [17 empty] | Septic Tank-2"sludge 0"scum/ Microfast ATU-0"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ UV-Light sleeve cleaned but the bulb and insert require replacement / Controls, pump, floats and alarms are working properly/ Counts: Pump-2089 ETM-379-h 16m/ High-12/ Peak-8/ On-11m 45s Off-1h 43m Peak off-1h 22m/ Watermeter-0,086,178.73/ Sewer pipe cleanout cap and plug require replacement/ No breakout or spongy areas on the drip field and dosing properly. Returned on 11/22/2023 to replace the cleanout cap, UV-Light bulb and insert/ All repaired were completed and the system is now functioning properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
02/13/2023 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Ecoflo | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/17/2023 | 11:05 AM
10/28/2023 | Alternative | Reportable Incident | 073-STS-95540 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Cajun Air. Power feeds to the system are tripping again. Customer already turned them back on and the system was at normal level when I arrived. I confirmed everything is working properly. I pumped the discharge tank down as far as I could | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | 08:38 AM
04/19/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
09/06/2023 | Alternative | Reportable Incident | 147-18-0036 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | N/A | [17 empty] | AOSS - Alarm event - system in alarm since 09/01/2023 - found compressor diaphragm failed - compressor re-built on property and system returned to proper operating status. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/07/2023 | Dec 30 1899 12:30PM
02/28/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Gravity | Gravity | Mound | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
04/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The system appears to be functioning as designed at this time. The field is slightly overgrown and difficult to tell that is going on. No surfacing effluent was observed. There appears to possibly have been vehicles driven on or near the drainfield. This is strongly discouraged. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/17/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | Dec 30 1899 12:26PM
12/01/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Clear | 7.510000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 01:40 PM
11/02/2023 | Alternative | Routine/Scheduled | 136 04 534 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal level 6 in of sludge less than 1 in of solids Pulled and cleaned filter Riser showing signs of leaking -Discharge/Pump Tank: Normal level 5 in of suspended solids Tested floats and pump all working as should However floats are aged All plumbing intact and pump properly moving water Riser is showing signs of leaking -Aeration: Normal level 1 in of suspeded solids Pulled and cleaned diffuser Pulled and cleaned weir Air line and weir intact and working properly Riser is just below grade showing signs of leaking in -Air Pump/Blower: 120 volts coming in Visual alarm light works however audible buzzer does not Pulled and cleaned filter Air pressure sensor intact and properly working Pump pulled 2.2 amps Dog box intact -Control Panel: 120 volts coming in All visual and audible alarms functioning properly Pump pulled 11.4 amps All components functioning properly however panel is aged -Distribution Box: Normal level 4 lines all intact however 2 lines have roots intruding throughout them otherwise the other 2 lines are taking water properly -Drain Field: Showing signs of surfacing, dark green grass in one area to the left of dbox | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | 11:25 AM
05/24/2023 |  | RoutineScheduled | SP-05-27 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Drip | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/28/2023 | 12:00 AM
03/31/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Hydro-Action ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
09/21/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/21/2023 | Dec 30 1899 9:05AM
11/15/2023 | Alternative | RoutineScheduled Component Maintenance | SD-10-109 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity |  | Chlorination |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | The sandfilter is holding water. Owner is planning to replace sand next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
06/14/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Visual alarm was replaced. Issues could not be replicated when troubleshooting and the system appears to be functioning as designed at this time. Advise homeowner to monitor alarms and notify if there are any changes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/06/2023 | Alternative | RoutineScheduled | C 800-13-0004 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Environmental Services of Virginia | 1942001182 | Steve | Haley | 1.000000 | 450 | CS600NC3T |  | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/06/2023 | 12:00 AM
12/12/2023 | Alternative | RoutineScheduled | 015-STS-337880 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 RT |  |  | Pressure | Trenches | Not Applicable |  | ["Septic Tank Baffles"] | ["Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 12:00 AM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance | 165-STS-333615 | Rockingham | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 4.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Drip Zones 3,5,6,7,8 are saturated | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 08/23/2023 | 06:57 AM
03/29/2023 |  | RoutineScheduled | 107-98-0273 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 2250.000000 | [] | [] | [8 empty] | 03/29/2023 |  | 14.000000 |  |  | 11.800000 | 70.320000 |  |  |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 02:30 PM
07/25/2023 | Alternative |  | 07-113-327 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/25/2023 |  | 8.210000 |  |  | 16.000000 |  |  | Will be sent separately |  | BOD: 8.21 TSS: 16.0 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/25/2023 | 12:00 AM
09/04/2023 | Alternative | RoutineScheduled | 171-18-0020 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 14" of accumulated solids in septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. 0" of solids in recirculation portion of treatment unit. 10" of solids in discharge portion of treatment unit. Tested floats, pumps and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/24/2023 | 07:03 PM
07/12/2023 | Alternative | RoutineScheduled | 175-18-0380 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Advantex Recirculation Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | YES | [17 empty] | System in alarm upon arrival found clogged hydraulic filter and trash in the return valve/ Cleaned and now functioning properly/ Septic- Advantrx Tank-4"sludge 3"scum/ Pump Tank-3"sludge/ No pump out needed at this time/ Controls, pumps, floats and alarms functioning properly/ Pump intake cleaned/ Counts: Recirc. Pump cycles-113566/ Recirc. Pump Run Time-632h 37m/ Discharge Pump Cycles-7076/ Discharge Pump Run Time-1281h 11m/ Watermeter-0,334,242/ No breakout or spongy areas on the drip field and now dosing properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
07/21/2023 | Alternative | Reportable Incident | 136-15-0010 | Gloucester | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Pad | Not Applicable | 450.000000 | ["Control Operation","Distribution Pump Operation","Recirculation Pump"] | [19 empty] | Lightning Strike - fried both control panels ... temporary motherboard installed in AdvanTex controls - logic controller ordered for Discharg Panel. Pump and Haul as needed till components arrive. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/24/2023 | 09:45 AM
03/30/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [17 empty] | Septic Tank-6"sludge 3"scum/ Microfast-6"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Replaced faulty alarm buzzer / Controls, pumps, floats and alarms now functioning properly/ Blower air filter cleaned and blower working correctly/ Counts: Pump1-399 ETM-14h 7m/ Pump2-381 ETM-13h 37m/ Peak-8/ High-11 On-2m 12s Off-6hrs/ No breakout or spongy areas on the drainfield and dosing properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
10/13/2023 | Alternative | Initial Visit |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to some dampness. Serviced system. Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Installed an aerator rebuild kit. Replaced the alarm light bulb and replaced the buzzer. Meet with the pumping company and pumped and cleaned out the Clearstream tank and pump tank. The timer is set to 6 minutes every 2 hours. Need to go back to perform a draw down test, set pressures, replace valve box on the drainfield, hook pressure switch and cut the UV back on (due to the pumping of tanks). | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/13/2023 | Dec 30 1899 12:00PM
12/07/2023 | Alternative | Routine/Scheduled | 136-03-0333 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Customer Thomas, Brook Property Address 9309 Glass Road, Hayes, VA 23072 USA Technician Jacob Gallihugh Date Serviced 2023-12-07 Was customer present for service? No Type of System Alternative Type of AOSS System Ax20 to distribution box Trash Tank Condition of above Component Notes for above Component Normal Level 24" of sludge and 3" of of solids No signs of infiltration Inlet tee intact Recirculation Tank Condition of above Component Notes for above Component Normal level 18" of suspended solids All floats and pump are functioning properly however floats are Aged Pulled and cleaned biotube filter, pump screen, and floats RSV (Recirculating Splitter Valve) Condition of above Component Notes for above Component Structural integrity appears OK Flushed caged Disassembled caged and made sure it was free of debris Discharge/Pump Tank Condition of above Component Notes for above Component Normal Level 6" of suspended solids All floats and pump are functioning properly however floats and plumbing are Aged Floats are not secured properly Root intrusion around forcemain Media Sheets Condition of above Component Notes for above Component Sprayed off media sheets Flushed and brushed laterals Flushed media module until water ran clear Control Panel Condition of above Component Notes for above Component 120v All audible and visual alarms are functioning properly Recirc pump pulled 10.3amps Discharge pump pulled 10.8amps Distribution Box Condition of above Component Notes for above Component Concrete distribution box has cracks on all 4 walls. At normal level with 3 lines balanced and taking water Drain Field Condition of above Component Notes for above Component No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 11:57 AM
12/22/2023 | Alternative | Follow-Up Component Maintenance | 179-STS-87443 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | ["Control Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Follow up. Replaced recirc pump (230v) with new 115v pump to correct mistake that was made at installation time. New pump working good making treatment spray pretty good, treatment should get better. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 07:39 AM
12/04/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/05/2023 |  | Routine/Scheduled | 228-18-0019 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/05/2023 | Jan 1 1900 12:35PM
02/23/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
07/10/2023 | Alternative | RoutineScheduled Component Maintenance | 179-13-0361-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Effluent Screens" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | Food packaging wrappers were observed in the septic tank. Plastic wrappers should not be flushed into your septic system. Plastic will not degrade and will clog your effluent filter. It may be advisable to pump the septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
09/05/2023 | Alternative | RoutineScheduled | 13-137-0180 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1000 | Advantex |  | Gravity | Pressure | Drip |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/19/2023 | 12:00 AM
04/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Loudoun Environmental Treatment | 1942001460 | Raymond | Kirkpatrick | 3.000000 | 1500,1000,1000 | EZ treat |  | Pump | Pressure | Drip | UV | 600.000000 | ["None"] | ["None"] | YES | Musty | Cloudy |  | 0.000000 | [13 empty] | Will send separately | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | Dec 30 1899 1:55PM
11/30/2023 | Alternative | RoutineScheduled | 04-184-5004 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.500000 | 7.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
04/25/2023 | Alternative | RoutineScheduled | SD-14-282 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Observed tiny black ants in all pods. Sprayed with Raid and advised owner to consult pest specialist for additional treatment. Some roots remaining in top header line (in d-box), did not appear to be living. Added Root-Ex as a precaution. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
01/20/2023 | Alternative |  | 003-STS-32047 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Dawson | Garrod | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/10/2023 |  | RoutineScheduled | 182-95-0381 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.880000 | [14 empty] | Not enough flow to grab a formal sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/31/2023 | 11:45 AM
06/29/2023 | Alternative | Routine/Scheduled | 053-STS-9933 | Dinwiddie | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Aqua Klear |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/29/2023 | Dec 30 1899 3:36PM
10/06/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1200 |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA |  |  | 7.400000 | 5.600000 | [13 empty] | Ann Mason Building in back of buidling-Aerobic system | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/11/2023 | Dec 30 1899 4:05PM
03/10/2023 | Alternative | RoutineScheduled | 128-06-032 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | [9 empty] | ["None"] | ["None"] | [18 empty] | Pete moss inspected and in good condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 12:00 AM
01/24/2023 |  | Routine/Scheduled | 550-STS-6640 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 01/24/2023 |  | 2.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 7:41AM
07/28/2023 | Alternative | RoutineScheduled | 107-18-0237 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | 12:00 AM
01/24/2023 |  | Routine/Scheduled | 550-STS-6597 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 01/24/2023 |  | 6.000000 |  | 1.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 8:00AM
09/25/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | Dec 30 1899 1:25PM
06/01/2023 | Alternative |  | 86-192-068 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 06/01/2023 |  | 2.150000 | [5 empty] | Will be sent separately |  | BOD: 2.15 TSS: BDL | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/01/2023 | 12:00 AM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2024 | 12:23 PM
06/07/2023 | Alternative | Routine/Scheduled | 085-STS-32915 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 0.000000 | 0 |  |  | Pump | Gravity | Trenches | Not Applicable | 10000.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service - Community pump station / absorption field. Pump Tank - float sensors, and controls operating - discharge pumps serviced. Hydraulic splitter valve - serviced - operating properly DBoxes - FOUR - all boxes intact and balanced properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | Dec 30 1899 10:45AM
11/02/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity |  | UV |  |  |  | NA | Musty | Clear | 7.800000 | 19.100000 | [11 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | Dec 30 1899 2:02PM
01/20/2023 |  | RoutineScheduled | SWP-04-942 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Slimy material in recirc tank and sheets as if they were using scented beads or liquid softeners. Left copy of Do's and don'ts. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
01/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
11/07/2023 | Alternative | RoutineScheduled Component Maintenance | SD-04-567 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Peat is still in good shape for its age. Septic filter is still in place (housing is cracked due to lack of support legs) and will eventually need to be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
12/27/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 0.000000 | [] | [] |  | Musty |  | 7.820000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/12/2024 | 07:03 PM
07/07/2023 | Alternative | RoutineScheduled Component Maintenance | 177-11-0112-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Water level was high in all tanks due to a leaking commode. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
10/25/2023 | Alternative | Initial Visit |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantes AX20RT |  | Pump | Gravity | Trenches |  |  | ["Control Operation"] | ["Control Operation"] | NA | [17 empty] | Initial start-up inspection. Verified proper installation. Set recirculation pump timers to homeowner indicated occupancy. Tested floats, pumps and alarm. Repositioned float switches for recirculation pump and discharge pump as per manufacturer service bulletin for this unit's serial number range. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 07:03 PM
10/03/2023 | Alternative | Routine/Scheduled | 05-142-0540 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | None | [6 empty] | 02/19/2024 |  | 8.000000 |  |  | 15.500000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/31/2024 | Dec 30 1899 10:02AM
08/09/2023 | Alternative | RoutineScheduled | 2007-143-0055 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Other"] | ["Other"] | [17 empty] | Pumped Out | Replaced Blower | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
02/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Advantex Recirculation Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | [18 empty] | Septic Tank-8"sludge 2"scum/ RecirculationTank-3"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Controls, pumps, floats and alarms functioning properly/ Recirculation pump intake cleaned and Advantex media in good condition / Recirc pump run counts-1981.1 Cycles-764.24/ Discharge pump : On-1m 32s Off- 6hrs. Counts: Pump1-129.6 cycles-4534/ Pump2-129.6 cycles-4534/ Total cycles-9068.0 Total run-259/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/22/2023 | Alternative | RoutineScheduled | S 800-12-0267 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | JEF Septic LLC | 1942001131 | Jason | Fulbright | 1.000000 | 10000 | Advantex |  | Pump | Gravity | Trenches | Not Applicable | 2250.000000 | [] | [] | NA | None | Clear | 7.430000 | 6.250000 |  |  |  | 09/22/2023 | Pump Chamber | 1.000000 |  |  | 1.000000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/19/2023 | Dec 30 1899 3:00PM
11/30/2023 | Alternative | Routine/Scheduled | 10-172-0112A | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/30/2023 | Dec 30 1899 10:42AM
12/06/2023 | Alternative | RoutineScheduled | 127-STS-33725 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Carrington Pump & Irrigation | 1942001121 | John | Carrington | 3.000000 |  | Norweco with HKBFR |  | Pump | Pressure | Drip | UV |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
07/07/2023 | Alternative | Reportable Incident | 166-10-075 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Tree fell crushing risers and control panels. Rebuilt risers and replaced controls | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
09/25/2023 | Alternative | RoutineScheduled | 06-183-346 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 10 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/25/2023 | 12:00 AM
12/11/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Routine annual, nothing to report | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/11/2023 | 12:00 AM
10/16/2023 | Alternative | RoutineScheduled | 169-STS-26843 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | FAST |  | Pump | Pressure | Trenches | UV | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
03/21/2023 |  | Routine/Scheduled | 087-STS-6335 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 3.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/21/2023 | 02:37 PM
05/05/2023 | Alternative | RoutineScheduled | 15-120-0184A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 3200 | 1200 | 1000 | Pump | Pressure | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Recirculation Pump","Level Sensor Operation"] | YES | None | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/05/2023 | 12:00 AM
10/24/2023 | Alternative | RoutineScheduled Component Maintenance | 015-STS-337269 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Pad | UV |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Disinfection" ,"Dispersal System Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Disinfection" ,"Dispersal System Operation"] | NA | [7 empty] | 10/24/2023 |  | 42.000000 | [5 empty] | Will be sent separately | Inspected | Need to add more mulch after removing weeds New uv bulb installed Added grate on discharge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
06/02/2023 |  | RoutineScheduled | 175-15-0263 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-6" sludge 2"scum/ Microfast-4"sludge/ Pump Tank-0"sludge/ No pump out needed at this time/ Controls, pump, floats and alarms functioning properly/ Blower air filter cleaned and blower working correctly/ Counts: Pump-1956 ETM-204h 6m/ High-26/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/20/2023 | Alternative | RoutineScheduled Component Maintenance | -STS-92235 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
10/20/2023 | Alternative | RoutineScheduled Component Maintenance | 196-06-459 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Three Rivers | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Ecoflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Peat was ponding and has roots in it, added Root Destroyer and fluffed it and started to drain good. Recommend adding treatment every year as needed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
04/03/2023 |  | Routine/Scheduled | 033-17-0183-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1060 |  |  | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | [17 empty] | System checked and appears to be operating normally. Aerator-5331:37, sludge-133:05, clear-111:17. Next visit scheduled for 10/11/2023. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | 10:18 AM
08/25/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 12:17 PM
04/07/2023 |  | Routine/Scheduled |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - normal level - RSV recirc pump effluent screen serviced. Treatment module - media drapes & spray grid serviced. Pump Tank - float sensors,pump and controls operating. Dbox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | Jan 1 1900 8:30AM
08/09/2023 | Alternative | Routine/Scheduled | 10-118-0021 | Charles City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Puraflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/09/2023 | Dec 30 1899 4:47PM
10/16/2023 | Alternative | Routine/Scheduled | 03-142-0183 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out. -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. -RSV (Recirculating Splitter Valve): Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Media lid safety support struts have failed. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact. -Drain Field: Found no signs of surfacing on dispersal field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | Dec 30 1899 9:44AM
03/13/2023 |  | Initial Visit | 001-STS-92742 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | JEF Septic LLC | 1942001131 | Jason | Fulbright | 1.000000 | 500 | Fuji Clean | UV Disinfection Unit - Salcor | Pump | Gravity | Trenches | UV | 500.000000 | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | 7.390000 | 3.760000 | 0.000000 |  |  | 02/28/2023 | Pump Chamber | 6.000000 |  | 0.000000 | 7.600000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/23/2023 | 12:00 PM
05/17/2023 |  | Initial Visit | 90-120-0375A | Chesterfield | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Rejected | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit - ALARM ISSUE - Service Provider NOT responding! Control panel signage indicates Madison Environmental has been service provider. Treatment Module has partially surfaced, breaking plumbing. Processing Tank - high level - RSV, recirc pump and effluent screen serviced. Treatment Module - partially surfaced - possibly has fractured module and broken anti-flotation wings - plumbing repaired - media drapes and spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. Underground consult placed to have exploratory excavations to determine cause of treatment module surfacing - | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/30/2023 | Jan 1 1900 9:00AM
01/11/2023 |  | Reportable Incident | 2013-143-0157 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Norweco | [6 empty] | ["Other"] | ["Other"] | [18 empty] | Repaired broken dripfield line and added a pressure gauge to the pump tank. Maintenance is overdue. We sent a quote for maintenance October 2022. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/01/2023 | 12:00 AM
07/12/2023 | Alternative |  | SWP-05-235 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
09/22/2023 | Alternative | RoutineScheduled | 175-14-0118 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-8"sludge 6"scum/ Microfast ATU-8"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower is working correctly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-31611 ETM-2527h/ Watermeter-0661770/ 12" x 20" riser on the Microfast ATU and the junction box on the pump tank needs replacement/ No breakout or spongy areas on the drip field and is dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
12/13/2023 | Alternative | RoutineScheduled | 08-183-278 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 12 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/13/2023 | 12:00 AM
09/25/2023 | Alternative | Routine/Scheduled | S 800-17-0207 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | Dec 30 1899 1:24PM
03/31/2023 | Alternative | RoutineScheduled | 151-11-0091 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | KC Forge Environmental Service, LLC | 1942001034 | Kent | Cuthbertson | 4.000000 | 45000 | 15000 | 15000 | Pump | Gravity | Trenches | UV | 17900.000000 | ["Other"] | ["Other"] | YES | [8 empty] | Sample Chamber | [6 empty] | Attached to this report |  | Loss of one treatment train due to FOG caused higher than allowed BOD. Reseeding of bacteria is underway and will correct the treatment within 3 to 4 days | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/30/2023 | 03:00 PM
05/08/2023 |  | RoutineScheduled | 175-17-0021 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 05/08/2023 | Sample Chamber | 3.000000 | [5 empty] | Attached to this report |  | Septic Tank-4"sludge 0"scum/ Microfast Tank-0"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-272 On-2m 5s Off-6h ETM-9h 9m/ Peak-0/ High-2/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
05/19/2023 | Alternative | RoutineScheduled | 154-14-0148 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Trenches | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/28/2023 | 12:00 AM
03/07/2023 |  | RoutineScheduled | 182-08-0287 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Auxiliary Filter","Dispersal System Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/16/2023 | 12:00 AM
02/20/2023 | Alternative | RoutineScheduled | 061-16-250 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Dispersal System Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Biweekly inspection. In the past 12 days, the system pumped an average of 2133.7 gals/day at 360.6 gals/dose (avg.) for a total of 25,605 gallons. Earlier today, Dave Stewart and crew dug up the wet spot in zone 2 and repaired 2 leaks at manifold saddle tees, and replaced 2 sections of kinked tubing. Ran a test cycle prior to covering up the repairs. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
07/27/2023 | Alternative | RoutineScheduled | 2007-143-0121 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/25/2023 | Alternative | Reportable Incident | 234-03-11324 | Chesapeake | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Rejected | EHD - Chesapeake | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Discharge | Chlorination | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Peatmoss Biofilter Media Changeout 05/22/2023 - septic tank and pump basin pumped empty by MDM Septic Service to allow Biofilter Media to drain and dry. - Effluent screen serviced. Pump Basin - float sensors, pump and controls operating. 05/25/2023 - Biofilter media removed - new media installed. Chlorination tablet feeder & Dechlor tablet feeder serviced. Discharge point free of debris. | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 06/01/2023 | Dec 30 1899 7:15AM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-118 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Septic tank lid was missing gasket, Replaced. Media starting to show its age, evaluate next year for peat replacement (replace rods as needed). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
11/22/2023 | Alternative | RoutineScheduled | 196-10-031 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Redmond's Plumbing & Electrical, Inc. | 1944001234 | Duane | Redmond | 3.000000 | 1000 | 600 |  | Pump | Gravity | Trenches | Not Applicable | 150.000000 | [] | [] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/23/2023 | 12:20 PM
11/28/2023 | Alternative | RoutineScheduled | 151-15-0037 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Advantex AX-RT |  | Gravity | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Recirculation Pump","Level Sensor Operation","Control Operation"] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 12:00 AM
11/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced float in pump tank | This AOSS should now return to normal function after having provided the above state routine maintenance | 12/06/2023 | 03:05 PM
03/07/2023 | Alternative | RoutineScheduled | 104-09-0158 | Amherst | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1000 | Puraflo |  | Pump | Pressure | Pad | Not Applicable | 450.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | 04:00 PM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance | 175-02-0462 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
02/02/2023 |  | Routine/Scheduled | {FIPSCode}-STS-3709 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | Jan 1 1900 2:50PM
04/13/2023 | Alternative | Routine/Scheduled | 149-STS-10646 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/13/2023 | Dec 30 1899 2:49PM
03/17/2023 | Alternative | Reportable Incident | 073-STS-100701 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | [18 empty] | COSS - Maintenance - GMP2018-02 Replaced distribution box with new 8 port concrete DBox. spliced to existing conveyance line. Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/20/2023 | 08:45 AM
05/05/2023 | Alternative | RoutineScheduled | SD-06-81 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation","Dispersal System Operation","SludgeScum Accumulation","Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/05/2023 | 09:45 AM
10/06/2023 | Alternative | Routine/Scheduled | 151-10-0165 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the panel (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/06/2023 | 08:30 AM
05/09/2023 | Alternative | RoutineScheduled | 103-STS-102083 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/31/2023 | Alternative | RoutineScheduled | 179.05.141 | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | replaced st effluent filter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/20/2023 | Alternative |  | 085-STS-33429 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/12/2024 | 12:00 AM
08/17/2023 | Alternative | Routine/Scheduled |  | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Pump tank - float sensors, pump and controls operating. DBox - corner fractured - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | 09:15 AM
07/05/2023 | Alternative | Routine/Scheduled | 228-13-0516 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | Dec 30 1899 11:53AM
12/13/2023 | Alternative | Routine/Scheduled | 127-STS-35170 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 750 |  |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 1:30PM
05/24/2023 | Alternative | Routine/Scheduled | 166-07-209 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank normal level - effluent screen serviced. Biofilter - peatmoss in excellent condition - raked / turned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 11:30 AM
08/03/2023 | Alternative | RoutineScheduled | 04-160-0135 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Septic | [15 empty] | Inspected | - recommend both tanks be pumped and cleaned - unable to hear alarm nor confirm that alarm works - recommend riser lid be replaced and riser be extended to ground level (approx 2.5ft) - brush needs to be removed from tanks to continue service | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/05/2023 | 12:00 AM
01/03/2023 |  | Routine/Scheduled | 234-17-371 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2023 | Jan 1 1900 9:15AM
02/11/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 2.000000 | 2000 | ANUA BioCoir |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. Treatment was converted form PuraFlo peat to ANUA BioCoir. Septic tank - 1st section 10" of solids, second section 10" of solids. 6" of solids in recirculation tank. Cleaned very clogged septic tank filter. Water level in septic tank was elevated due to the clogged solids filter. Once cleaned, the septic level returned to normal. Tested pump, controls and alarm. Good spray patterns on treatment unit spray nozzles. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 07:03 PM
06/01/2023 |  | Routine/Scheduled | 93-142-0148 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | None |  | Pump | Pressure | Trenches | Not Applicable |  | ["Dispersal System Operation","SludgeScum Accumulation"] | ["Dispersal System Operation","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Pumped septic tank. Flushed LPD. System appears to be operating normally | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/12/2023 | Jan 1 1900 8:30AM
12/07/2023 | Alternative | Follow-Up Component Maintenance | SD-05-289 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Chlorination |  |  |  | NA | [9 empty] | 46.000000 | 0.030000 | 2419.600000 | 164.000000 |  |  | Will be sent separately | Inspected | **SAMPLING/TESTING RESULTS ONLY** Dissolved Oxygen 8.40 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
02/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
04/10/2023 |  | Reportable Incident | SP-05-52 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to floats being out of adjustment, pump being out of time and posible running toilet. Some ponding in pods. Infiltration on outlet riser and inlet wedge lid. Proposal to be sent to correct floats, auger all 5 pods and correct infiltration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
01/17/2023 |  | RoutineScheduled | 153-STS-19068 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | [17 empty] | Septic-5"sludge 0"scum/ Microfast-4"sludge/ Pump Tank-0"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working properly/ Controls, pump, floats and alarms functioning properly/ UV-Light bulb is blown and requires replacement/ Returned on the same day and replaced the UV-Light Bulb, now functioning properly/ Counts: Pump-1723 ETM-259h 7m/ High-21/ Water Meter-104,222.48/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
08/14/2023 | Alternative |  | {FIPSCode}-STS-8940 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 08/14/2023 |  |  |  |  | 1.600000 |  |  | Will be sent separately |  | TSS: 1.60 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/14/2023 | 12:00 AM
05/02/2023 |  |  | 09-184-5001 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 05/02/2023 |  | 2.040000 |  |  | 3.000000 |  |  | Will be sent separately |  | BOD: 2.04 TSS: 3.00 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | 12:00 AM
02/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/01/2023 | Dec 30 1899 2:21PM
01/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
06/14/2023 |  |  | 177-17-0246-SR | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
06/19/2023 | Alternative | Routine/Scheduled | 800-11-0310 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | Dec 30 1899 12:05PM
08/09/2023 | Alternative | RoutineScheduled Component Maintenance | 177-07-0258-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Effluent Screens" ,"Recirculation Pump" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
05/15/2023 |  | Routine/Scheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  | 600.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/22/2023 | 10:09 AM
05/05/2023 | Alternative | Routine/Scheduled |  | Richmond City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Richmond | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3500 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 35.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/05/2023 | Dec 30 1899 3:12PM
10/12/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 8.030000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 03:45 PM
01/24/2023 |  | Routine/Scheduled | 550-STS-6636 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [19 empty] | 01/24/2023 |  | 2.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 10:00AM
04/29/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | MultiFlo ATU |  | Gravity | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | Annual inspection. Septic tank - Less than 1" solids crust, 13" of accumulated solids on bottom of septic tank. Excellent treatment quality, adequate aeration. Removed solids from Multi-Flo "socks". Treatment unit very sudsy, | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 07:03 PM
10/20/2023 | Alternative | Follow-Up Component Maintenance | 099-06-0337-SP | King George | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Cleared trees and brush from drainfield area and additional 10 ft. buffer. Cleared brush near tanks. Repaired broken dripfield piping. (This piping has been broken for approximately 2 years.) System tested; only 3 GPM, should be 7.5 GPM. Debris hauled off. Will follow up in 2 weeks to re-check rates. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/01/2023 | 06:08 AM
10/19/2023 | Alternative | RoutineScheduled | -STS-20410 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic/ Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | NA | [7 empty] | 10/18/2023 | Sample Chamber | 35.000000 | [5 empty] | Attached to this report |  | Septic Tank-2"sludge 2"scum/ Microfast-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ During inspection found 2 header pipes were broken and requires repair, both lines were capped off until repairs can be made / No breakout or spongy areas on the drainfield itself Returned and replaced the broken pipes, system now dosing properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/16/2023 | Alternative | RoutineScheduled | 175-14-0164 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Disinfection","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Disinfection","Level Sensor Operation"] | NA | [17 empty] | Septic Tank-10"sludge 4"scum/ Microfast-18"sludge/ Pump Tank-2"sludge/ Pump out required on the Septic- Microfast Tank/ Blower air filter cleaned and blower working correctly/ Replaced faulty redundant off float during inspection / Controls, pump, floats and alarms now functioning properly/ Counts: Pump-6081 ETM-786h 6m on-8m 13s off-1h 51m/ Watermeter-621,121.99/ Uv-light is faulty and requires replacement/ No breakout or spongy areas on the drip field. Returned on 6/24/2023 to replace the UV-Light with a Jet UV-Light and now functioning properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/12/2023 | Alternative | Routine/Scheduled | 136-11-0170 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - high level on arrival - effluent screen clogged - serviced. Processing Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - Plastic - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/25/2023 | 01:30 PM
05/16/2023 |  | Reportable Incident | {FIPSCode}-STS-67847 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"SludgeScum Accumulation" ,"Control Operation" ,"Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Owner noticed wet spot near septic tank. This was due to pump tank being in high level for some period of time. Pump tank lid is a foot above grade, whereas both septic lids are buried below grade. It was easier for effluent to seep out of buried septic lid than to overflow pump tank. Recommend adding risers to grade for septic tank and adding an effluent filter. Pump tank was in high level due to a failed pump which presumably failed due to clogged sand filter H-pipes. Most of the orifices were plugged. Cut off 1 hard-cap from 2 of the H-pipes and flushed out sludge, then installed 1.5" female adapters with screw-on caps (limited stock on hand). For best maintenance, all 4 legs of all 3 H-pipes need to have screw-on caps. Dug up d-box to check for roots (previous history) and added a root killer (Root-Ex). Cycle counter is seized, needs replaced. Alarm horn is burnt out, needs replaced. High level alarm float appears to be stuck on but initially was not closed so alarm light was not lit. That alarm float should be replaced. The timer and override floats were working correctly. Installer did not set the pump on blocks (but should have). Pump tank has 5" of sludge and needs pumped out ASAP. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
08/15/2023 | Alternative | RoutineScheduled | DISCHARGE | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 12:00 AM
06/14/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Sealed pump tank casing. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/15/2023 | Dec 30 1899 12:05PM
01/06/2023 |  | Routine/Scheduled | 234-13-187 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/06/2023 | Jan 1 1900 9:30AM
08/09/2023 | Alternative | Routine/Scheduled | 550-STS-6682 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | Dec 30 1899 12:25PM
05/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/17/2023 |  | Routine/Scheduled | 234-14-217 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | Jan 1 1900 9:00AM
04/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | 11:24 AM
05/10/2023 |  | Follow-Up | 175-02-0293 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Follow up inspection. Pump out recirc tank, cleaned pump vault and bio-tube filter. Sheets are stretched and need replacement. O-ring on RSV is damaged we will replace to see if it stops the leak, if don't work the whole assembly will need replacement. Ax-20 unit lid starting to show its age may need replacement soon. Will send proposal for repairs. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
03/10/2023 |  | RoutineScheduled | 195-STS-26918 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/10/2023 | 12:00 AM
10/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
01/24/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 750 | MultiFlo ATU |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","SludgeScum Accumulation"] | ["Auxiliary Filter","SludgeScum Accumulation"] | NA | [17 empty] | Annual inspection. 14" of accumulated solids in septic tank. Cleaned drip manifold screen filter. Tested pump and pressure bell. Effluent in discharge pump tank very clean. MicroFast unit has very little clear water or separation and should be pumped out. Septic tank and treatment unit pumped out on 2-8-2023. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 07:03 PM
06/14/2023 | Alternative | Routine/Scheduled | 800-STS-14487 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 10000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 10000.000000 |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen / grate serviced. Secondary septic tank - normal level - effluent screen serviced. Processing Tank - float sensors, recirc pumps (3) serviced, Blower serviced. Media drapes & spray grid serviced. Pump Tank - float sensors, pumps (5) serviced. Distribution boxes (10) intact - absorption fields (5) no indications of surfacing. Control panel | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | Dec 30 1899 10:45AM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | One lateral appears to be more nitrified than others but is not showing signs of hydraulic saturation or surfacing effluent. Recommend balancing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/03/2023 |  | Routine/Scheduled | 033-10-0158-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [17 empty] | System checked. Air filter cleaned. System appears to be operating normally. Last 25 feet of drainfield are overgrown and needs to be cleared and maintained as lawn. Tank is due for a pumpout by end of June. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | 11:41 AM
09/19/2023 | Alternative | RoutineScheduled Component Maintenance | 177-06-0026-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Effluent Screens"] | ["Control Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
05/08/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Based on sample peat does need to be change this year | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
02/22/2023 | Alternative | RoutineScheduled | 109-STS-32276 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2250 | Norweco |  | Pump | Pressure | Mound | Not Applicable |  | [] | ["Auxiliary Filter","Effluent Screens","Dispersal System Operation"] | YES | Musty | Clear | [14 empty] | Inspected | Septic Sludge/Scum Accumulation - 12" Norweco Bio Filter Cleaned Effluent Filter Cleaned and Drip Tubing Flushed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | 11:30 AM
10/23/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/23/2023 | Dec 30 1899 9:00AM
03/29/2023 |  | Routine/Scheduled | 196-11-052 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 35.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 05:36 PM
01/31/2023 |  | RoutineScheduled | 16-183-003 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 4 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/31/2023 | 12:00 AM
07/12/2023 | Alternative |  | 177-07-0412-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
12/21/2023 | Alternative | Routine/Scheduled | 041-STS-260100 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Trash Tank Condition of above Component Notes for above Component Normal Level 2" of sludge and 1" of solids Tank appears intact No signs of infiltration Equalization Tank Anaerobic Filtration tank Condition of above Component Notes for above Component Normal Level 7" of sludge and less than 1"of solids Cleaned media Discharge/Pump Tank Condition of above Component Notes for above Component Normal Level All floats and pump are functioning properly No signs of infiltration in tank Aeration Condition of above Component Notes for above Component Normql level Flushed aeration and recirculation lines. Checked and confirmed aerator is functioning properly. Flushed effluent line. Air Pump/Blower Condition of above Component Notes for above Component 120v to panel All audible and visual alarms are functioning properly Pulled and cleaned air filter Air pump pulling .919amps Control Panel Condition of above Component Notes for above Component 120v coming into panel All audible and visual alarms are functioning properly Pump pulled 12.04amps LPD Condition of above Component Notes for above Component No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | Dec 30 1899 8:45AM
04/07/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1500 | Septic | pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/11/2023 | Alternative | Routine/Scheduled | 073-STS-92542 | Gloucester | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Discharge | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - recommend pumpout. Aeration Tank - normal level - mixing present - compressor serviced. U.V. - Bulb and housing serviced. Pump Tank - float sensors, pump and controls operating. Discharge Point - signage present - rodent guard present | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/12/2023 | 07:32 AM
07/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["Disinfection","BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation"] | ["Disinfection","BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-8"sludge 0"scum/ Microfast-18"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ Pump out of the Septic-Microfast Tank is required due to sludge levels/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-3940 ETM-728h 14m/ Peak-26 ETM-205h 26m/ High level-23/ On-11m 30s Off-3h/ UV Light sleeve cleaned but the bulb requires replacement/ No breakout or spongy areas on the drip field and dosing properly. Returned on 7/31/2023 and replaced the uv-light bulb, now functioning properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
04/26/2023 |  | RoutineScheduled | 177-13-0064-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 0-0 0-0 | 0-0 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Level Sensor Operation","Distribution Pump Operation","Control Operation","BlowerCompressorAerator Operation","Attached Growth Medium"] |  | None | Clear |  |  | 0.000000 | [11 empty] | Inspected | sysyem pumped out by others. system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | 09:00 AM
02/17/2023 | Alternative |  | 124-STS-2379 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Blue Ridge | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
04/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/12/2023 | Alternative | RoutineScheduled | 153-STS-20277 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Other"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-8"sludge 0"scum/ Microfast ATU-8"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-1955 ETM-207h 26m On-7m 9s Off-2h 28m Peak off-1h 36m/ Peak-14/ High-26/ W@atermeter-0067151.8/ Pump Tank Riser is broken and requires replacement 12" x 30" / No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/04/2023 | Alternative |  | 13-197-A1 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  | [] |  |  | None | Clear | 7.000000 | 5.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
07/14/2023 | Alternative | Reportable Incident | 136-xx-legacy | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Orenco Advantex |  | Pump | Pressure | Trenches | UV | 450.000000 | Septic Tank Baffles | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | System in alarm and overflowing at spider valve. Pumped 500g from septic tank for return storage. Pumped 500g from treatment system until float returned to off position. Service tech found recirc forcemain fractured - not dosing recirc properly and causing hydraulic overload to discharge side of tank. - Repaired. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/17/2023 | 08:30 AM
02/02/2023 |  |  | 196-12-026 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
08/30/2023 | Alternative | Initial Visit | 161-STS-42621 | Roanoke | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Gravity | Gravity | Discharge | UV |  | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation"] | NA | [16 empty] | Pumped Out | The 1500 Gallon septic tank was pumped and cleaned. The blower filter was cleaned. The blower pipe was broke in the treatment unit before it went into the water so the blower was not treating the effluent. The pipe was dug up and repaired. The treatment unit is now operating as designed. The UV bulb was not working and it was discovered that the housing was so black that it could not be cleaned. The outer housing and UV bulb was replaced and is operating as designed. The discharge pipe was dug up and extended for future sample draws. A discharge sign was added at the point of discharge. The controls were operating as designed. The lids were secured. The samples were not taken because the system will take awhile to clean back up. The system is now operating as designed. | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 09/13/2023 | Jan 1 1900 9:50PM
03/02/2023 |  | RoutineScheduled | 175-03-0079 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
02/28/2023 |  | RoutineScheduled | 17-152-009 | Lee | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Clearstream |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/28/2023 | 12:00 AM
10/27/2023 | Alternative | RoutineScheduled | VAG408299 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 1.000000 |  | FAST | Constructed Wetlands | Gravity | Gravity | Discharge |  |  | [] | ["BlowerCompressorAerator Operation"] | NA | None | [16 empty] | Not discharging at time of inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/12/2023 | 09:45 AM
04/19/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Ecoflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | filter clog and was replaced | This AOSS should now return to normal function after having provided the above state routine maintenance | 05/22/2023 | 11:15 AM
06/08/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation"] | NA |  | Clear | [13 empty] | Will be sent separately | Inspected | Soil excavated and the broken vent pipe fitting and sanitary tee removed. New sanitary tee installed and test cycle run to verify repair. Area backfilled and seed applied. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 06:43 AM
07/25/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["Other"] | ["None"] | YES | [17 empty] | Needs Audible Alarm | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/01/2023 | 12:00 AM
02/24/2023 |  | Routine/Scheduled | 15-142-0040 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Delta Environmental Products, UC Series |  | Gravity | Gravity | Trenches | Not Applicable | 900.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Primary septic tank - normal level Processing Tank - normal level - mixing present - compressor serviced. DBox intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/27/2023 | Jan 1 1900 8:00AM
01/19/2023 | Alternative | RoutineScheduled | 154-16-0316 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco | Norweco | Pump | Pressure | Mound | Not Applicable | 750.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 12:00 AM
12/06/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump |  | Trenches | Not Applicable |  | ["None"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 12:00 AM
02/02/2023 |  | Reportable Incident | 087-STS-6332 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 4.000000 | 8000 | None | None | Pump | Gravity | Trenches | Not Applicable | 2000.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | COSS - Maitenenance - GMP2018-02 Replaced damage distribution box with new 12 Port concrete DBox. Spliced to existing conveyance line. Spliced to existing header lines. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/06/2023 | 07:30 AM
05/31/2023 | Alternative | Follow-Up |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  | 600.000000 | Distribution Pump Operation | Distribution Pump Operation | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/06/2023 | 10:06 AM
01/23/2023 |  | RoutineScheduled | 101-05-0364 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Advantex |  | Gravity | Pressure | Trenches | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 12:00 AM
08/22/2023 | Alternative | RoutineScheduled | SD-15-68 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2500 | septic | Microfast | Gravity | Pressure | Discharge | UV |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/28/2023 | 08:40 AM
03/24/2023 |  | Routine/Scheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Orenco Advantex |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","Control Operation","Level Sensor Operation"] | ["Auxiliary Filter","Control Operation","Level Sensor Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/02/2023 | 12:43 PM
11/07/2023 | Alternative | RoutineScheduled Component Maintenance | 175-14-0210 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Level Sensor Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Recirc trough in atu was completely submerged. Heavy inflow or clogged media could cause that. Treated effluent is still clear, just not crystal clear. Will reevaluate next year. Drip rates elevated in both zones but nothing surfacing and no soggy spots. Monitor for now. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
07/17/2023 | Alternative | RoutineScheduled | 115-10-0225 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | Sludge levels-Scum layer 1"in. and 12" in. sludge in Septic tank -Recirc zone 6" Sludge and 8-10" Sludge in Discharge zone of tank. Cleaned effluent screen, cleaned bio filter- dirty. Flushed and Brushed Sprayer maniflod, flushed system. pumps are functional, alarm functional, sprayed off media, tested floats. AX20RT POD#410337 RTU121078 System was having xtreme high override cycles. Possible due to clogging of filter or infiltration. We had lots of rain at the same time. 7/14 pump ran 81 min 7/15 ran 47 min, on 7/16 it had 172 min discharge pump run time. Possible infiltration. Reccomended to owner to address run off and help provide a path for water to flow away from the area with the tanks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/30/2023 | 09:30 AM
12/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1125 |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/27/2023 | Dec 30 1899 12:30AM
04/11/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | EcoPod | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The blower was repaired. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/02/2023 |  | Reportable Incident | 2006-143-0302 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 3.000000 | 2800 | Septic Tank | Premier Tech EcoFlo | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Cloudy | [14 empty] | Pumped Out | Service call report that system ponding around EcoFlo pump vault. System pumped down, troubleshooting revealed that pump and floats non-functioning. Replaced pump and floats, pump, alarm, floats all working properly now. EcoFlo service done, cleaned trays, effluent filter, peat deteriorated, nearing end of life span. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/06/2023 | 12:00 AM
05/31/2023 | Alternative | RoutineScheduled | 98-160-0344 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2500 | LPD |  | Pump | Pressure | Trenches | Not Applicable |  | [] | ["Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | NA | Septic | Dark Brown | [14 empty] | Inspected | - pump is not functioning - both tanks need to be pumped/cleaned | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12:00 AM
07/19/2023 | Alternative | RoutineScheduled Component Maintenance | 175-18-0039 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [5 empty] | 07/19/2023 |  | 21.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
10/25/2023 | Alternative | RoutineScheduled Component Maintenance | {FIPSCode}-STS-67146 | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation"] |  | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | 1) We recommend removing the Microfast lid, treating & cleaning the filter media and then pumping the tank afterwards. 2) The blower is not working and should be replaced along with the air filter assembly. We recommend installing the new blower on the septic tank and running new wiring from the panel to the blower. 3) We recommend installing a 12? EZ Set riser and lid on the inlet of the septic tank. Currently there is no access to this tank. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/01/2023 | 07:38 AM
04/11/2023 |  | RoutineScheduled |  | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 300 | Micro Fast 0.5 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | Routine inspection- 2 in scum and 16 inch sludge in front and back of fast, May pump this year. Contact Foutz. Blower working cleaned air filter, Found effluent pump locked up and burned out, 22awg gauge Pump float wires shorted and were the cause. we removed shorted wire section and reconnected.. The alarm float which is now operational. Floats mounted to float tree. Left both original floats however, Returned and replaced Goulds effluent pump and system is now operational . | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/30/2023 | 09:30 AM
09/26/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Annual maintenance, sand mound renovated, total chlorine .06, which is .01 higher than needed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/26/2023 | 12:00 AM
02/24/2023 |  | RoutineScheduled | 05-137-0321 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | EcoFlow |  | Gravity | Gravity | Trenches | Not Applicable | 500.000000 | [] | ["Attached Growth Medium","Dispersal System Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/25/2023 | 12:00 AM
03/08/2023 | Alternative | Reportable Incident | 057-STS-101113 | Essex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | AOSS - Repair Install - VDH Permit 128-22-0081 - Pumped existing septic tank empty, crushed and removed. Installed new 1500g processing tank for BioMicrobics 0.5 FAST. Installed pad 30' x 30' at 42" depth. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/09/2023 | 07:00 AM
11/13/2023 | Alternative | Reportable Incident | 073-STS-94384 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm - did too much laundry. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 3 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 03:45 PM
01/31/2023 |  | RoutineScheduled |  | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Advantex |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
01/10/2023 |  | Routine/Scheduled | 08-174-0057 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump tank - float sensors, pump and controls operating. BioFilter - 4 modules - Peatmoss in fair condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/11/2023 | Jan 1 1900 12:00PM
06/21/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | DSS repaired issues with junction boxes. The system should return to functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/19/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Best 1 |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
08/10/2023 | Alternative | RoutineScheduled | 181-05-0097 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | 12:00 AM
11/02/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-92460 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
08/31/2023 | Alternative |  |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/10/2023 |  |  | 06-142-0521 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | EcoFLo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/15/2023 | 12:00 AM
03/14/2023 | Alternative | RoutineScheduled | VAG401971 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] | [19 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/30/2023 | 08:40 AM
04/06/2023 |  | Initial Visit |  | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - InitialVisit - Alarm Issues Primary septic tank - normal level - effluent screen serviced. Processing Tank - recirc - recirc pump, media drapes, spray grid serviced. Processing Tank - discharge - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | Jan 1 1900 7:30AM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | One of the pumps is not functioning. Lots of scum in pump chamber. Recommend pumping all tanks. Drainfield is waist high grasses. Recommend mowing and keeping it shorter, but there were no signs of failure in the field. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
06/29/2023 | Alternative | RoutineScheduled | SD-08-213 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 50.000000 | ["Attached Growth Medium","SludgeScum Accumulation","Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/06/2023 | 12:00 AM
05/02/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
06/08/2023 | Alternative | Reportable Incident | 136-08-0014 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced failed compressor with new. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:30 PM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/28/2023 | Alternative | Follow-Up | 085-STS-33971 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the solenoid, replaced the fitting, replaced the UV bulb, and replaced the UV tube. The timer is set to 2 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/28/2023 | Dec 30 1899 10:00AM
02/16/2023 |  | RoutineScheduled | 17-120-0335A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Carrington Pump & Irrigation | 1942001121 | John | Carrington |  |  | Norweco |  | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Level Sensor Operation","Distribution Pump Operation","Effluent Screens","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/16/2023 | 12:00 AM
11/15/2023 | Alternative | Reportable Incident | 228-13-0543 A | Virginia Beach | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to a possible float problem. Serviced system. Checked the pump and panel (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The pressure switch on the aerator is not hooked up. Fixed the grade on the pipe in the Clearstream. Replaced the override float. The UV is not working - cord, bulb, and tube burnt up - will need to replaced - possibly need to replace circuit board or ballast as well. The timer is set to 6 minutes every 2 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 11/15/2023 | Dec 30 1899 4:30PM
10/10/2023 | Alternative | RoutineScheduled | 05-100-0463 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | ECOFLO |  | Pump | Gravity | Mound | Not Applicable | 600.000000 | [] | [] | YES | [17 empty] | SLUDGE JUDGE SEPTIC TANK 4-5" FROM BOTTOM EVERYTHING WORKING AS IT SHOULD PEAT IS IN GOOD CONDITION | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 10:00 AM
05/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/29/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | [9 empty] | ["None"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | 12:00 AM
12/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 12/20/2023 | Sample Chamber | 8.000000 | [5 empty] | Attached to this report |  | Septic Tank-4"sludge 4"scum/ Microfast ATU-2"sludge 0"scum/ Pump Tank-0"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-398 ETM-23h 26m/ Pump2-392 ETM-23h 3m/ Peak-9/ High-10/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
09/21/2023 | Alternative | Follow-Up Component Maintenance | 179-06-0455-SWP | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Terra lifted drain lines. Replaced pump. Septic tank and pump tank pumped out by others prior to peat replacement. Degraded peat was removed by hand and new peat was installed. Peat was purchased at Driller Services, degraded peat was disposed at Spotsylvania Refuse. Drain piping needs to be re-plumbed from pods to distribution box. Distribution box and headers need to be replaced. Proposal to be sent for the additional repairs needed. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/02/2023 | 05:18 AM
05/01/2023 |  | Routine/Scheduled | 234-13-457 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | Jan 1 1900 12:05PM
12/13/2023 | Alternative | RoutineScheduled | 181-10-0056 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 4.000000 | 4000 | Ecopod | Biomicrobics MicroFAST | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | Filters checked and cleaned. Pumps, control panels, and floats all functioning properly. No apparent leaks in system or drain field area. Lids were properly secured | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 07:15 PM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
04/28/2023 | Alternative | RoutineScheduled | 115-08-0094 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 2000 | Septic Tank | EcoPod | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | NA | [16 empty] | Inspected | Replaced Blower motor - System has good aeration and was operational. Pump and alarm operatrioal - all system runs on one 20 amp breakers, owner may want to run 3 separate circuits for the blower pump and alarm control in the future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
01/12/2023 | Alternative |  | 151-15-0063 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1200 | Microfast |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/17/2023 | 12:00 AM
10/02/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank To Puraflo Pump Tank | Pump Tank to LPD Trenches | Pump | Pressure | Trenches | Not Applicable |  | ["Attached Growth Medium","Dispersal System Operation"] | ["Attached Growth Medium","Dispersal System Operation"] | YES | [17 empty] | Septic Tank-3"sludge 1"scum/ Pump Tank to Puraflo Modules-1" sludge 0"scum/ Pump Tank to LPD Trenches-1" sludge 0"scum/ Controls, pumps, floats and alarms are functioning properly/ Puraflo peat turned in all modules and is in good condition at this time/ Counts Puraflo Pumps: Pump1-008935 ETM-0028469/ Pump2-009423 ETM-0029742/ Cleaned LPD Globe Valves/ No breakout or spongy areas on the LPD Trench area and no signs of unequal distribution. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/30/2023 | Alternative |  | SD-15-033 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan |  |  | Karrie & Dave | Parker | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Gravity | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 12:01 PM
03/23/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | McKim Septic & Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | [] | [18 empty] | 2 air release valves replaced | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/28/2023 | Dec 30 1899 3:00PM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/03/2023 |  | Follow-Up | 179-06-0417-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to review past proposal with homeowner. Showed him the repairs that need to be done. Updated proposal to be sent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
10/17/2023 | Alternative | RoutineScheduled | 2017-143-0050 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Aqua Klear |  | Pump | Pressure | Pad |  |  | [] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Effluent Screens","Control Operation","Level Sensor Operation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | 12:00 AM
04/11/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | UV |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
11/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Micro fast | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 11/01/2023 | Sample Chamber | 6.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/03/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/20/2023 | Alternative | Routine/Scheduled | 10-137-0103 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Air filter cleaned. Treatment tank checked. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | Dec 30 1899 10:06AM
10/17/2023 | Alternative | Routine/Scheduled | 093-13-0128 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | Dec 30 1899 10:20AM
03/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
10/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1500 |  |  | Pump | Gravity | Trenches | Not Applicable | 650.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/15/2023 | Dec 30 1899 2:20PM
02/06/2023 |  | Pump-Out Only | 228-03-0301 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | Jan 1 1900 10:00AM
04/25/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
04/27/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The peat fiber looks very broken down sample taken will update after the results come in | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Distribution box has lots of roots in in. Restricting flow from the modules to the field. Alarm was not functioning. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
06/09/2023 |  | Initial Visit | 015-STS-338377 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 1.000000 |  | Advantex RT |  | Gravity | Pressure | Drip | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | NO | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 03:20 PM
11/04/2023 | Alternative | RoutineScheduled | 109-17-0094 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | EZ Treat |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. Septic tank solids - First section - 12", second section - 12". 8" of accumulated solids in both ends of recirculation tank. 4" of solids in discharge pump tank. All spray heads in treatment unit not clogged with good spray patterns. Tested floats, pumps and alarms. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 07:03 PM
04/12/2023 |  | RoutineScheduled | 196.05.746 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/18/2023 | Alternative | RoutineScheduled Component Maintenance | 175-04-0590 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
11/22/2023 | Alternative | Routine/Scheduled | 166-11-065 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 |  |  | Pump | Gravity | Pad |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 75.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/22/2023 | 04:47 PM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance | 099-13-0114-SR | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
10/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/23/2023 |  | RoutineScheduled |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith | 1.000000 |  | EZ Treat Sandfilter | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | 3 air release lids broken | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/27/2023 | 07:00 PM
05/18/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Puraflo |  |  |  | Drip |  |  | ["Attached Growth Medium","Dispersal System Operation","Auxiliary Filter"] | ["Attached Growth Medium","Dispersal System Operation","Auxiliary Filter"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/18/2023 | 12:00 AM
06/19/2023 |  |  | 033-15-0134-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Multi-Flo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
05/09/2023 |  | RoutineScheduled | 177-10-0131-ST | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Blower 3.84 amps | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/10/2023 | 05:56 AM
10/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank | Pump Tank to Puraflo Modules to Discharge LPD Pump Tank | Pump | Pressure | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-4"sludge 0"scum/ Pump Tank to Puraflo Modules-3"sludge 0"scum/p Tank to LPD Trenches-2"sludge 0"scum/ No pump out needed at this time/ 5 modules ponding water- To be addressed by others/ Interior Panel, pumps, floats and alarms are functioning properly/ Counts: ETM1-0049227/ ETM2-0048163/ Dosing to Puraflo-On-1m Off-1.5h/ No breakout or spongy areas on the LPD Trench Area. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12:00 AM
10/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 10/25/2023 |  | 6.000000 | [5 empty] | Will be sent separately | Inspected | Keep drainfield trimmed and free of brush and trees Repaired recirc float Lab sample normal | This AOSS should now return to normal function after having provided the above state routine maintenance | 11/22/2023 | 09:18 AM
11/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Primary tank pumped | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
03/24/2023 |  | RoutineScheduled | 167-STS-15634 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Disinfection","BlowerCompressorAerator Operation","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/24/2023 | 12:00 AM
12/06/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected | Pumps will not alternate. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/08/2023 | Dec 30 1899 8:29AM
09/28/2023 | Alternative | RoutineScheduled Component Maintenance | 175-11-0268 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
11/06/2023 | Alternative | Component Maintenance | 166-02-562 | Northumberland | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. Other conventional maintenance performed | Approved | EHD - Three Rivers | Redmond's Plumbing & Electrical, Inc. | 1944001234 | Duane | Redmond | [9 empty] | [] | ["BlowerCompressorAerator Operation","Distribution Pump Operation"] | NA | None | [17 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/06/2023 | 05:00 PM
02/06/2023 |  | Routine/Scheduled | 228-09-0433A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | Jan 1 1900 2:53PM
10/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 10/18/2023 |  | 2.000000 | [5 empty] | Will be sent separately | Inspected | Tree Down blocking lower entrance please clear Please keep drainfield mowed and maintained | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
04/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/17/2023 | Alternative |  | 101-16-0320 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Rebecca | Klaff | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/28/2023 | Alternative | Routine/Scheduled | 147-19-0005 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/28/2023 | Dec 30 1899 10:38AM
03/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/09/2023 |  | Routine/Scheduled | {FIPSCode}-STS-2722 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Discolored | 7.000000 | [14 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/09/2023 | Jan 1 1900 2:00PM
06/03/2023 |  | RoutineScheduled | -STS-92993 | King George | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Rappahannock | Assure Plumbing & Septic LLC | 1942001502 | Assure | LLC | 2.000000 | 1000 | 1000 | 1000 | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | YES | Musty | [16 empty] | Replaced failed peat and converted to coir Upsized pump and set timer settings Cleared drain line from pods with jetter | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 06/06/2023 | 05:00 PM
06/15/2023 | Alternative | Pump-Out Only | C09-180-0140 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner |  |  | Whitewater | [6 empty] | [] | [] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/16/2023 | 12:00 AM
06/26/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The peat is showing signs of its age, but appears to still have good texture and is not very saturated. Informed the homeowner that while the peat is approaching the end of its life, at this point we believe it is still functioning as specified by the manufacturer. Recommended that the homeowner trim up some of the plants around the modules to make access easier for future operators. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | bad recirc alarm float bad return line gauge all recirc floats replaced and gauge | This AOSS should now return to normal function after having provided the above state routine maintenance | 01/15/2024 | 10:39 AM
04/28/2023 |  | Initial Visit | VAG408388 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 1.000000 |  | FAST ATU |  | Gravity | Gravity | Discharge | Chlorination |  | ["Disinfection"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation"] |  | None | [17 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/07/2023 | 10:30 AM
07/10/2023 | Alternative | Routine/Scheduled | 800-STS-14240 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed a 3/4" brass check valve on pump headworks. The timer is set to 2 minutes every 2.5 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | Dec 30 1899 1:45PM
05/15/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Attached Growth Medium"] | ["Effluent Screens","Attached Growth Medium"] | NA | [16 empty] | Inspected | Septic Tank 1" scum and 6-8 "in sludge, Recirculation zone trace of scum 5"sludge and discharge 6" sludge, Cleaned effluent filter, Cleaned septic tank effluent filter, Discharge pump run time 0.5 hours and 168 cycles. Recirc pump run time 9.8 hours and 5,042 cycles count. System jjust began to trend data 13 days ago, No alarms or alerts in history. Memory is possibly corrupted. it took about 3 -4 years to trend data and go into normal mode from startup. No recent alarm in history but date is corrupted- System is fully operariotnal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
05/19/2023 | Alternative | Reportable Incident | 103-STS-102270 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | COSS - Voluntary Upgrade - Permit 151-23-0043 Pumped existing septic tank empty - filled with flowable fill. Installed new septic tank and pump tank in accordance with permit. Pressure tested forcemain Installed new absorption field in area indicated on permit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 02:00 PM
07/21/2023 | Alternative | RoutineScheduled Component Maintenance | 061-STS-25027 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection, new client. Owner unaware if anyone came back to collect the 180 day BOD sample. The RO (bottom) float in the drip tank had failed (stuck on) and the drip pump union was missing its o-ring (causing a steady drip during pump cycle). Advised owner to quickly contact his installer on all of these issues quickly before warranty runs out. One nozzle in EZ-Treat pod was not spraying. Flow restored by removing and cleaning that nozzle. Also cleaned dirty intake on recirc pump. Zones are different sizes so doses are different sizes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 07:01 AM
02/24/2023 |  | RoutineScheduled | 191-07-0004 | Sussex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Delta DF Series |  | Pump | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Level Sensor Operation","Distribution Pump Operation"] |  | Musty | Cloudy | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/24/2023 | 12:00 AM
03/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
06/09/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 2000 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/09/2023 | Alternative | RoutineScheduled | 181-14-0108 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did need to be pumped for a routine pump out, but the land owner was advised that access to the tank needed to be improved before the pumping could take place. The pumping will be done at a later date. The blower filter was cleaned. The controls were operating as designed. There were no visible leaks in the leech field. The treatment unit was in good operating condition. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | 01:30 PM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/21/2023 | Alternative | RoutineScheduled | C102-07-0035 | Alleghany | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | Septic Tank Only | AdvantexAX20 | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system didn't need to be pumped. The effluent filter was pulled and cleaned. The recirculating pump was pulled and sprayed off. The RSV valve was pulled and cleaned. The spin filter was cleaned. The textile sheets were sprayed off. The pressure was adjusted on the AX20 pod. The controls were operating as designed. There were no leaks in the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/24/2023 | Jan 1 1900 8:50PM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Hydro-Action ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/29/2023 |  | Initial Visit | 182-13-0054 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip |  |  | ["Septic Tank Baffles","Dispersal System Operation"] | ["Dispersal System Operation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | 12:00 AM
03/15/2023 | Alternative | Initial Visit | 171-16-0023ES | Pittsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Pittsylvania-Danville | Acres of Virginia, Inc. |  | Melvin | Collins | 1.000000 | 1000 | Sand Filter Bed |  | Gravity | Gravity | Discharge | Chlorination | 300.000000 | ["None"] | ["None"] | [18 empty] | Water samples are out of limits. A second sample should be taken. waiting on customers response. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/23/2023 | 12:30 PM
06/01/2023 |  | Routine/Scheduled | 234-13-84 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | Jan 1 1900 1:15PM
07/21/2023 | Alternative | RoutineScheduled Component Maintenance | 061-18-375 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation"] | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Treatment looks very good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 07:01 AM
12/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Distribution Pump Operation"] | ["Control Operation" ,"Level Sensor Operation" ,"Distribution Pump Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Manifolds out of level in first 2 pods. Replaced broken tie straps. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
05/16/2023 | Alternative | RoutineScheduled | 001-STS-93528 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1000 | Septic Tank | Puraflo | Gravity | Pressure | Pad | Not Applicable | 450.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/25/2023 | 02:40 PM
08/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1875 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/26/2023 | Alternative | Reportable Incident Component Maintenance | 177-08-0030-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to failed timer float. Replaced timer float. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-91863 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Dispersal System Operation"] | ["Level Sensor Operation" ,"Dispersal System Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | 90-Day Inspection Defective time float in pump tank was replaced by the installer. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
05/15/2023 | Alternative | RoutineScheduled | 154-05-0355 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
09/22/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Annual, pumped, replaced/fluffed some peat | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/22/2023 | 12:00 AM
04/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
05/02/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Micro Fast tank needs to be pumped and washed down. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | Dec 30 1899 12:05PM
12/18/2023 | Alternative |  | 181-04-0389 | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Acres of Virginia, Inc. |  | Melvin | Collins | 1.000000 | 1500 | Ecoflo |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/12/2024 | 02:00 PM
05/15/2023 |  | Reportable Incident | 177-17-0061-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due plc being locked up and not getting inputs from the discharge tank. Cycled control breaker and plc started working again. Spoke with orenco rep and he will stop by and reflash the plc. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
03/10/2023 |  | RoutineScheduled | 043-05-0109 | Clarke | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lord Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | LPD system | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/13/2023 | 07:05 AM
06/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | [7 empty] | 06/08/2023 | Sample Chamber | 59.000000 |  | 1600.000000 |  |  |  | Attached to this report |  | Septic Tank-6"sludge 6"scum/ Microfast-18"sludge Pump Tank-2"sludge 0"scum/ Pump out required on the Septic-Microfast Tank/ Blower air filter cleaned and working correctly/ UV-Light sleeve cleaned/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-4427 ETM-1071h 23m/ Peak-13 ETM-463h 12m On-15m 15s Standard Off-3h Peak Off-1h 48m / Watermeter-281,250.11/ No breakout or spongy areas on the drip field. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/30/2023 | Alternative | RoutineScheduled | 133-STS-97265 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Repaired fouled diffuser. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/02/2023 | Alternative | RoutineScheduled Component Maintenance | 177-07-0282-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
03/16/2023 |  | RoutineScheduled | 179-08-0157-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | ["Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Bushes were cut down. No roots inside pods this time. Septic tank was pumped. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
09/08/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
04/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/27/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 11500 | Microfast |  | Pump | Pressure | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Restaruant pump tank and Grease traps-Lots of grease and feminine products Both tanks need pumping Told Chris and Foutz they need pumping -please confirm it was pumped on next visit - Pump & Alarm operational - Septic tank near mens shower 2" scum and 10- 12" sludge - Boat dock#7 Pump station 1-2" scum and 5-6" sludge- Pump and alarm functional. Pump station #10 near unit #74 - New pump runs good. Trace of sludge- Septic treatment area- Fast treatment system septic holding/dosing Minimal scum trace to 8" sludge, treatment system 14-20" sludge. Cleaned Blower air filter, both pumps and alarms operational, Pump #1 6394.87 vs 6376.57Hr = 18.3Hrs and 2626 cycles vs 2427cycles = 199 cycles, Pump #2 6024.06 Hr vs 6007.14Hr = 16.92 Hrs and 2627 Cycles vs 2422 cycle = 205 Cycles The pump tank had a 2-6" sludge trace. Noticed septic odor in air -System is Fully opperational | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | 09:30 AM
11/28/2023 | Alternative | RoutineScheduled | C04-180-0035 | Roanoke | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Fast Biomicrobics |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | NA | [16 empty] | Inspected | New client exhisting home. Sludge levels-- -scum on top and 26" cludge on bottom of tank may need pumping this spring. Fast unit has good aeration. Pump tank has 12" of sludge. and 6-10" sludge in Septic tank. System was pumping to drain field constantly, After trouble shooting for bad bottom OFF float. Replaced it and pump began to work as designed. Searched the yards for more components and found air relief valves header box. Replaced pressure gauge has pressure going to drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/28/2023 | Dec 30 1899 9:30AM
05/17/2023 |  | RoutineScheduled | 12-163-0060 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Norweco |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Level Sensor Operation","Distribution Pump Operation","Dispersal System Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | 12:00 AM
08/01/2023 | Alternative | Routine/Scheduled | S 800-17-0101 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 2.000000 | [7 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The septic tank needs to be pumped (over 2' of sludge). The timer is set to .85 minutes every 2 hours. Took 5 year BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/01/2023 | Dec 30 1899 9:00AM
07/12/2023 | Alternative | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 |  |  | Pump | Pressure | Trenches |  | 750.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/13/2023 | 02:52 PM
12/14/2023 | Alternative | RoutineScheduled | 182-08-0376 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 5.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 10:15 AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
01/06/2023 |  | RoutineScheduled | 04-197-242 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/06/2023 | 12:00 AM
10/25/2023 | Alternative | RoutineScheduled | C-06-111-0169 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | Septic Tank Only | AdvantexAX20RT | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The recirculating pump was pulled and sprayed off. The textile sheets were sprayed 0ff. The laterals were flushed and cleaned. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/09/2023 | Dec 30 1899 12:45PM
05/17/2023 | Alternative | RoutineScheduled | 175-17-0088 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | EcoVirginia LLC | 1942001235 | William | Poindexter | [9 empty] | ["Effluent Screens","Auxiliary Filter"] | ["Effluent Screens","Auxiliary Filter"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/05/2023 | 12:00 AM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance | 175-06-0561 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] |  | NO | [15 empty] | Will be sent separately | Inspected | Effluent filter is below top of the tank and is not serviceable. need to remove filter and extend and replace filter so it can be serviced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | 12:58 PM
01/05/2023 |  | Reportable Incident | 234-19-056 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/05/2023 | Jan 1 1900 8:30AM
08/08/2023 | Alternative | RoutineScheduled | 181-11-0163 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | Septic Tank Only | AdvantexAX20 | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The recirculating pump was pulled and cleaned. The textile sheets were sprayed off. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/16/2023 | 12:55 PM
04/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance | 182-12-0266 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Added Riser and pumped tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
06/07/2023 |  |  | 00-142-0515 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Puraflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Inspected | Slight root intrusion in first pod, instructed homeowner to use root killer in the system as directed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | 12:00 AM
10/19/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [13 empty] | Replaced aerator and alarm float | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/19/2023 | Dec 30 1899 11:20AM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
01/20/2023 |  | RoutineScheduled | 05-125-086 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Advantex should be pumped and manifold needs to be cleaned to function properly. Air release valve in the field is broken and there is effluent surfacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
10/16/2023 | Alternative | RoutineScheduled | 02-197-A2 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  | [] |  |  | Musty | Clear | 6.500000 | 5.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
08/02/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/12/2023 | 01:27 PM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/06/2023 |  |  | SP-05-463 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
01/31/2023 |  |  | 17-192-081 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/31/2023 |  | 2.010000 |  |  | 0.000000 |  |  | Will be sent separately |  | BOD: BDL TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | 12:00 AM
01/30/2023 |  | RoutineScheduled | SWP-05-469 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
12/18/2023 | Alternative | Routine/Scheduled | 12-120-0082A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Biomicrobics MicroFAST |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/18/2023 | Dec 30 1899 8:10AM
11/02/2023 | Alternative | Routine/Scheduled | 127-STS-34077 | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 2.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/02/2023 | Dec 30 1899 3:49PM
03/23/2023 |  | Reportable Incident | {FIPSCode}-STS-2806 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/23/2023 | Jan 1 1900 10:00AM
12/26/2023 | Alternative |  |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Auxiliary Filter"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
02/14/2023 |  | RoutineScheduled | SWP-01-219 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Septic Tank Baffles" ,"Effluent Screens" ,"Control Operation"] | ["Effluent Screens" ,"Septic Tank Baffles" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Zone number 1 has gallons per minute slightly higher due to a small leak on check valve flapper, not enough to pressurize both zones at the same time. Will check next year. Peak counts 5782, peak etm 998923. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
11/20/2023 | Alternative | Pump-Out Only | 128-13-0022 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | pump and refill | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 02:36 PM
02/07/2023 | Alternative | Initial Visit | 115-10-0166 | Campbell | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 2.000000 | 4500 | Septic Tank | AdvantexAX20 | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation","Effluent Screens","Septic Tank Baffles"] | ["Control Operation","Effluent Screens","Septic Tank Baffles"] | YES | [17 empty] | The system did not need to be pumped. There was a lot of brush grown up around the system. The brush was cleaned up and weeded. There were two broken lids on the tanks. They were replaced. The effluent filter was cleaned. The pump screens were also cleaned. The textile sheets were sprayed off. The controls were not operating as designed. The alarms were cut off at the panel by the previous operator and restored to operating conditions. There were no visible leaks in the leech field. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/25/2023 | 01:05 PM
05/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/21/2023 | Alternative | RoutineScheduled | 001-STS-93013 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn |  |  | FUJI CLEAN CEN-5 |  | Pump | Gravity | Mound | UV | 450.000000 | [] | [] | YES | [17 empty] | SLUDGE JUDGE FUJI-5-6" FROM BOTTOM EVERYTHING WORKING AS IT SHOULD REPLACED FLOAT | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 11:00 AM
03/21/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 2.000000 |  | Clearstream | Clearstream | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Effluent Screens" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
05/17/2023 | Alternative | RoutineScheduled | 175-03-0573 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | EcoVirginia LLC | 1942001235 | William | Poindexter | 3.000000 |  | Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter","Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Auxiliary Filter","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | 12:00 AM
12/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 12/27/2023 | Sample Chamber | 485.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/23/2023 |  | Initial Visit | 095-STS-5087 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Fuji |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial visit - system permitted / installed 2020 Primary septic tank - normal level Processing Tank - Trash Tank - normal level - aeration tank - mixing present, compressor serviced - sludge return operating and flushed. Pump tank - float sensors, pump and controls operating. DBox - intact - Unknown if required 180 day lab sampling obtained by installer, or previous service provider. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 9:00AM
09/01/2023 | Alternative | RoutineScheduled | 97019481 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  | LPD Trench |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 | [] | ["SludgeScum Accumulation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/26/2023 | 12:00 AM
03/06/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/06/2023 | 12:00 AM
05/19/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/22/2023 | 11:15 AM
01/03/2023 |  |  | 051-STS-17412 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/03/2023 |  | 2.120000 |  |  | 1.100000 |  |  | Will be sent separately |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/03/2023 | 12:00 AM
03/20/2023 |  | RoutineScheduled |  | Warren | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 03/20/2023 |  | 12.000000 | [5 empty] | Will be sent separately | Inspected | Only 2 lines of 4 installed in field will require a follow up inspection | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/28/2023 | 02:17 PM
08/03/2023 | Alternative | Routine/Scheduled |  | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | Dec 30 1899 9:15AM
02/17/2023 |  |  | SWP-04-936 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
03/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
04/21/2023 |  | Routine/Scheduled |  | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. BioFilter - peatmoss in fair condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/24/2023 | Jan 1 1900 9:00AM
07/26/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/28/2023 | Dec 30 1899 11:00AM
03/15/2023 |  | Initial Visit | VAG408488 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex | [6 empty] | ["Septic Tank Baffles"] | ["Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/16/2023 | 12:00 AM
04/03/2023 |  | RoutineScheduled | 179-13-0292-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | UV |  | ["Control Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Alarm call by owner. Cleaned clogged Biotube filter. The conduit at the bottom of the control panel has pulled out of the panel. This may be how the ants are getting into the panel. We recommend adding flex conduit to extend the conduit back into the panel. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
10/06/2023 | Alternative | Reportable Incident | 03-137-0120 | Goochland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm Call: -Upon arrival, I found the control panel in alarm condition indicating system is in high level. Checked discharge pump and found that it had failed. Checked discharge tank and found in high level with pump plumbing still exposed. Pump plumbing is about 40" below grade and out of serviceable reach. Noted signs of groundwater infiltration around base of discharge riser. Discharge floats are not properly secured and have exceeded life expectancy. Upgrading discharge riser requires removal/ cutting back landscaping. Homeowner stated that he will take care of landscaping Repair 10/09: -Installation of 36" Riser on the Pump Tank-Installation of a water-resistant SB4 Junction Box inside a Riser includes Conduit and Grommet Kit -Installation of 3 new Floats Installation of a Float Tree Assembly to secure Floats -Installation of a Plumbing Kit -Installation of a Liberty Pump Tested all components upon completion and everything is working as it should | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/20/2023 | Dec 30 1899 12:24PM
08/25/2023 | Alternative | Routine/Scheduled | 09-120-0103 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Hoot |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/25/2023 | Dec 30 1899 8:54AM
11/29/2023 | Alternative | Initial Visit | 085-STS-34564 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 8.000000 |  | 500.000000 | [5 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. The grade on the pipe in the Clearstream is not okay - needs to be addressed and/or fixed. The system has an Orenco control panel. There are too many 120v circuits in the Clearstream panel. Took initial BOD and Fecal samples. NOTE : The Fecal sample was high - system should function properly after service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/29/2023 | Dec 30 1899 3:30PM
05/23/2023 | Alternative | Pump-Out Only | 157-05-267 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Pumped primary septic tank and aeration tank as recommended from prior service visit. Aeration tank refilled with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 09:00 AM
08/23/2023 | Alternative | RoutineScheduled Component Maintenance | 175-06-0804 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
01/24/2023 |  | Initial Visit | 146-01-0061 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Biofilter - Five Modules - peat moss in poor condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | Jan 1 1900 10:30AM
04/07/2023 |  | Reportable Incident |  | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Delta Environmental Products, UC Series |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Routine Service. Pumped trash tank empty - serviced. Aeration Tank - pumped empty - compressor serviced - refilled with fresh water for restart - mixing present. Pump Tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | Jan 1 1900 8:30AM
10/17/2023 | Alternative | RoutineScheduled Component Maintenance | 177-14-0027-SWP | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity |  | UV |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Disinfection" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens" ,"BlowerCompressorAerator Operation"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | As noted previously, the Salcor UV unit is no longer working. We recommend installing a new Orenco UV unit and new wiring. It will be necessary to excavate by machine through the rock-lined swale to install the new wiring. Effluent sample results to be sent separately. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/01/2023 | 07:38 AM
10/25/2023 | Alternative | RoutineScheduled | 001-STS-91682 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 2500 | MICROFAST |  | Pump | Pressure | Mound | UV | 1000.000000 | [] | [] | YES | [17 empty] | SLUDGE JUDGE REVEALED 8-9" FROM BOTTOM, 1" FROM TOP FOR GREASE TRAP SLUDGE JUDGE REVEALED 5-6" FROM BOTTOM, 2-3" FROM TOP FOR SEPTIC TANK EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/07/2023 | 01:35 PM
06/06/2023 | Alternative | Reportable Incident | 151-08-0126 | Lancaster | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | NO | [16 empty] | Pumped Out | Reportable Incident - Churchview Septic Service on property and pumping septic tank, pump tank and treatment unit. Residence is a "Rental" and had a leaking toilet that has flooded the system. Peatmoss biofilter completely degraded and requires replacing. Health Department has been on property and is aware of issues. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/19/2023 | 08:30 AM
12/06/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.140000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 12:45 PM
02/21/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | mow maintain around system and drainfield wipes keep area maintained | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
10/20/2023 | Alternative | Routine/Scheduled | 151-15-0011 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3000 | EcoPod |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 40.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 06:49 PM
04/28/2023 |  |  | 182-03-0137 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/28/2023 | 12:00 AM
05/01/2023 | Alternative | Routine/Scheduled | SD-08-336 (Phase II) | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Rappahannock-Rapidan | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | EZ Treat Sandfilter | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Dispersal System Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Effluent Screens"] | YES | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/08/2023 | 10:38 AM
09/12/2023 | Alternative | RoutineScheduled | 179-STS-91626 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 11692.000000 | [] | [] |  |  |  | 7.260000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/15/2023 | 04:00 PM
08/18/2023 | Alternative | RoutineScheduled | 07-118-0044 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Norweco |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/18/2023 | 12:00 AM
05/19/2023 |  | Routine/Scheduled | 550-STS-6549 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | Jan 1 1900 12:50PM
07/19/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | 12:00 AM
06/21/2023 | Alternative | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Pump | Gravity | Trenches |  | 750.000000 | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | 12:29 PM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/20/2023 | Alternative | RoutineScheduled | SD-87-33 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Cloverleaf Environmental Consulting, Inc | 1942001135 | Robert | Charnley |  |  |  |  | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/13/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-91774 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | 01:58 PM
04/10/2023 |  | Routine/Scheduled | 550-STS-6387 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | Jan 1 1900 9:00AM
11/02/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-205 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Water level was high in septic tank due to clogged filter, cleaned. Media had a little ponding due to slime on top, spoke to customer about Do's and don'ts (using liquid softeners). Roots in D-box, removed and added root-x. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
04/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
01/18/2023 |  | Routine/Scheduled | 149-STS-10375 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/18/2023 | Jan 1 1900 12:27PM
01/17/2023 |  | RoutineScheduled | 09-100-0021 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1250 | BIOCOIR |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | [] | [] | YES | [17 empty] | EVERYTHING WORKING PROPERLY. DISCHARGE PUMP AND FLOAT RECENTLY REPLACED, SEWAGE RECENTLY PUMPED, AND FIBER RECENTLY REPLACED. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/18/2023 | 11:50 AM
05/01/2023 |  | RoutineScheduled | 132-15-0100 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Norweco 960 |  | Pump | Pressure | Drip |  | 150.000000 | ["Control Operation","BlowerCompressorAerator Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | 09:05 AM
05/02/2023 |  | RoutineScheduled | {FIPSCode}-STS-6213 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Cloverleaf Environmental Consulting, Inc | 1942001135 | Robert | Charnley |  |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/16/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/16/2023 | Dec 30 1899 9:00AM
07/31/2023 | Alternative | RoutineScheduled | 18-177-1010 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 | 1000 | ATL |  | Gravity | Gravity | Mound | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | [8 empty] | 07/31/2023 | Sample Tap | [6 empty] | Will be sent separately | Inspected | - recommend that filter be cleaned more often | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/03/2023 | 12:00 AM
11/03/2023 | Alternative | RoutineScheduled | 019-STS-24199 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Yearly inspection visit - found and removed lots of roots in the original septic tank. Otherwise System has been shut down during the remodeling process and no occupants are living in the home this past year. System appears as opperational and will be restarted upon completion of construction. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
02/19/2023 |  | Routine/Scheduled | 041-STS-257814 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/19/2023 | Jan 1 1900 9:30AM
03/24/2023 |  | Routine/Scheduled | 087-STS-6250 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/24/2023 | 01:28 PM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/03/2023 |  | RoutineScheduled | 175-13-0493 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/10/2023 | 05:56 AM
10/31/2023 | Alternative | RoutineScheduled | 133-STS-100582 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [8 empty] | 10/31/2023 | [9 empty] | BOD = 18mg/l | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/19/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/23/2023 | 09:32 AM
09/05/2023 | Alternative | RoutineScheduled Component Maintenance | 177-11-0140-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
06/20/2023 | Alternative | Routine/Scheduled | 196-14-0013 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1500 | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 35.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 04:27 PM
05/15/2023 |  | RoutineScheduled | 177-08-0030-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium"] | ["Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Ants nest inside control panel, sprayed them. Media starting to show its age but still ok. Will evaluate next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/05/2023 | Alternative | RoutineScheduled Component Maintenance | VAG408136 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Pad | Chlorination |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 07/05/2023 |  | 24.000000 | [5 empty] | Will be sent separately | Inspected | Repaired air supply and vent Please add more mulch to et bed and clean out sample boxes | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
05/16/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
05/24/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Pressure | Pad | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Cleaned & flushed LPD lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/30/2023 | 10:30 AM
04/06/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | 12:00 AM
06/13/2023 | Alternative | RoutineScheduled | 07-163-0102 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Advantex |  | Gravity |  | Trenches |  |  | [] | ["Attached Growth Medium","Control Operation","Level Sensor Operation","Effluent Screens","Recirculation Pump","Distribution Pump Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/13/2023 | 12:00 AM
03/30/2023 | Alternative | Routine/Scheduled | 12-160-0176 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 05:30 PM
02/07/2023 |  | Initial Visit | 182-15-0187 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | Fixed air leak at blower. Cleaned filters | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/07/2023 | 12:00 AM
05/26/2023 | Alternative | Routine/Scheduled | 166-09-053 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. Biofilter - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 11:30 AM
12/06/2023 | Alternative | RoutineScheduled Component Maintenance | 101-04-0370 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
01/03/2023 |  | RoutineScheduled | 15-192-034 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Eljen |  | Gravity | Gravity | Mound | Not Applicable | 200.000000 | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2023 | 12:00 AM
09/07/2023 | Alternative | RoutineScheduled | 085-STS-33658 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/11/2023 |  | RoutineScheduled | 179-12-0318-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
04/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | Dec 30 1899 4:23AM
09/21/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/21/2023 | Dec 30 1899 10:35AM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/07/2023 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesapeake | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - high level - found panel turned OFF - re-activated - serviced RSV recirc pump and effluent screen. - system returned to normal level. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | Jan 1 1900 8:30AM
12/18/2023 | Alternative | RoutineScheduled Component Maintenance | 2002-93-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | Chlorination |  |  |  | NA | Musty | Clear | 7.100000 |  |  | 5.700000 | [9 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 12/20/2023 | 02:30 PM
09/01/2023 | Alternative | RoutineScheduled | 11-142-0183 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 12:00 AM
03/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Valve box riser cover needs to be replaced as it is broken. Low pressure does not appear to be functioning as designed. Homeowner is contacting company for repairs. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/04/2023 | 06:02 AM
10/26/2023 | Alternative | Follow-Up Component Maintenance | SWP-04-22 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Both tanks pumped out by others prior to peat replacement. Degraded peat was removed by hand and new peat was installed. Peat was purchased from Driller Services. Degraded peat was disposed at Spotsylvania Refuse. Replaced sample box and broken tufflite distribution box with quality at grade ?monster? distribution boxes. Replaced E140 pump with Champion CPSTEP 522 pump. Fixed settling at tanks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
02/10/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2024 | Dec 30 1899 5:34PM
08/01/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 12:00 AM
01/10/2023 |  | Routine/Scheduled | 05-120-0688 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. BioFilter - peatmoss in poor condition - raked / turned. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/11/2023 | Jan 1 1900 12:30PM
08/07/2023 | Alternative | Reportable Incident | 234-18-070 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream and cleaned the UV light bulb. Changed the filter in the aerator and changed the mesh screen in the spinfilter. Replaced the alarm light bulb. Could not locate the vacuum breakers. The timer is set to 8 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | Dec 30 1899 11:30AM
03/22/2023 |  | RoutineScheduled |  | Warren | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["Other"] | [] | [17 empty] | Inspected | Needs 4 Peat Pods Replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/22/2023 | 12:00 AM
01/16/2023 |  | RoutineScheduled | 179-STS-89885 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation" ,"Disinfection" ,"Level Sensor Operation"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Disinfection" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Leak in recirc tank riser (inlet). Off float for Discharge is stock close. Will contact installer. Replaced UV bulb. RECIRC: HL 11, LL 16, OVERRIDE 1547. DISCHARGE: HL 8, LL 20, OVERRIDE 15. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
10/12/2023 | Alternative | RoutineScheduled | SD-07-165 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable | 65.000000 | ["Effluent Screens","SludgeScum Accumulation","Control Operation","Attached Growth Medium"] | ["Effluent Screens","Distribution Pump Operation"] | YES | Septic | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 12:00 AM
10/01/2023 | Alternative | Routine/Scheduled | 041-STS-260562 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/01/2023 | Dec 30 1899 9:00AM
05/17/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski |  |  | 1 |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | Dec 30 1899 3:15PM
06/03/2023 | Alternative | RoutineScheduled | SD-14-244 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1000 | septic | Advantex | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | 08:40 AM
03/29/2023 |  |  | 18-172-0112AR | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 3000 | 1000 | 1000 | Pump | Pressure | Pad | UV |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] | YES | None | Clear | 8.000000 |  | 6.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | Jan 1 1900 12:15PM
05/15/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 RT |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens","Control Operation"] | NA | [16 empty] | Inspected | Septic Tank minimal scum and 6-8 in sludge, Recirculation zone trace of scum 6"sludge and discharge 5-12" sludge trace, Cleaned effluent filter, cleaned drip filter, discharge pressure good on drainfield. Flushed both valves. Discharge pump 54.8 hours and 803 cycles Recirc Pump run time 762.3 hours and 56,560 cycles. Check all all 6 floats and all respond to the panel. System is operational. Alarm history not available. it is connected to monitoring last years report of minutes run time for pumps was an eror and it was in hours. All looks operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
08/24/2023 | Alternative | Routine/Scheduled |  | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Biofilter - peatmoss in fair condition - raked / turned. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | Dec 30 1899 2:45PM
09/15/2023 | Alternative | Routine/Scheduled | 03-131-4063 | Floyd | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Aquarobic Mini Plant |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/15/2023 | 09:30 AM
02/17/2023 |  |  | 177-07-0041-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | EcoPod | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
09/21/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/21/2023 | Dec 30 1899 9:30AM
09/07/2023 | Alternative |  | 177-06-0668-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
05/25/2023 |  | Routine/Scheduled | 04-120-0644A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/25/2023 | Jan 1 1900 10:20AM
11/29/2023 | Alternative |  | 07-197-A8 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/29/2023 |  | 2.960000 |  |  | 1.100000 |  |  | Will be sent separately |  | BOD: 2.96 TSS: 1.10 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/29/2023 | 12:00 AM
08/17/2023 | Alternative | RoutineScheduled |  | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  |  | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/18/2023 | 12:00 AM
12/18/2023 | Alternative |  | 06-184-5004 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/18/2023 |  | 2.280000 |  |  | 11.400000 |  |  | Will be sent separately |  | BOD: 2.28 TSS: 11.4 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 12:00 AM
08/03/2023 | Alternative | Routine/Scheduled |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Routine Service Primary septic tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. - Recommend pumpout and refill. Pump Tank - float sensors, pump and controls operating. DBox - plastic - minor bulging / deformation - all laterals accepting effluent. 08/07/2023 - Aeration Tank pumped empty - refilled with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | 06:30 AM
07/26/2023 | Alternative | RoutineScheduled | 14-142-0013 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Distribution Pump Operation","BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/27/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Septic tank 0" scum, Sludge level-6". No scum in treatment and a 6" trace of sludge in Recirc tank and 7" trace of slduge Discharge zone. Media looked still clean and white, spray pattern was good, Cleaned eflfuent filter - minimally dirty. All Floats switched tested good. Pumps both opperate. Recir pump run time 715 minutes and 53080 cycles and dischartge pump run time 4.8 minutes and 181 cycles . System has a normal odor and nothing unusual noted. Does not need pumping this year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | 09:30 AM
07/18/2023 | Alternative | Initial Visit | 15-163-0075 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Virginia Septic Solutions LLC | 1942001500 | Justin | Barker | 1.000000 | 1000 | MicroFast 0.625 |  | Pump | Gravity | Trenches | UV |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | Musty | Clear | [15 empty] | Replaced aerator, and replaced entire uv system. Did not locate drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/18/2023 | 12:00 AM
09/05/2023 | Alternative | RoutineScheduled Component Maintenance | 108-10-0010 | Bath | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
06/13/2023 | Alternative | RoutineScheduled | 107-06-0608 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/13/2023 | 12:00 AM
09/07/2023 | Alternative | RoutineScheduled | 06-120-0785A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/22/2023 | 12:00 AM
10/05/2023 | Alternative | RoutineScheduled Component Maintenance | 175-03-0546 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Wanded (cleaned) sheets in just the first pod. Owner said outside alarm occasionally sounds, but not sure if in recirc tank or discharge tank. Recirc pump wires had some bare spots inside the splice box which had a couple of inches of water in it. Cut and stripped new connections for pump cord and removed water from the splice box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
07/18/2023 | Alternative | Initial Visit | 181-12-0024 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 2.000000 | 2500 | Septic Tank Only | MicroFast | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NO | [17 empty] | The system did not need to be pumped. The blower and spin clean filters were both cleaned. The treatment unit was operating as designed. The controls were operating as designed. There was return effluent returning to the pump tank so the drip field was operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | 02:45 PM
11/01/2023 | Alternative | Reportable Incident | 2014-143-0052 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | [] | [] | [18 empty] | Replaced clearstream blower | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/24/2023 |  | Routine/Scheduled | 175-STS-14861 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 2:00PM
07/05/2023 | Alternative | Reportable Incident | 2011-143-0099 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | NO | [17 empty] | Replaced blower and cleaned disc filter. Disc filter was clogged, system down to 8 psi. Clean filter psi at 22. System should return to normal operation. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/05/2023 | 12:03 PM
04/10/2023 | Alternative | Reportable Incident | 128-15-0037 | Essex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Rebuilt failed compressor. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
02/01/2023 |  |  | 18-192-146 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 02/01/2023 | [7 empty] | Will be sent separately |  | BOD: BDL TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/01/2023 | 12:00 AM
09/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
07/24/2023 | Alternative | RoutineScheduled | SP-05-358 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 0-3 | 0-0 | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear |  |  | 3.000000 | [11 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | 10:00 AM
06/22/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Pad | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | Dec 30 1899 11:25AM
11/13/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | Dec 30 1899 1:25PM
11/17/2023 | Alternative | Reportable Incident | 03-120-0104A | Chesterfield | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Advantex ax20. System in Alarm and high level. Found sirens logo unit was bad. Was able to pump the system way down to give storage. Customer approved to install a new ax20 mvp panel and she paid in full with cc. They won't be here Monday but the breaker panel is in the little storage room on the back side of the house. I left the power on but shut down the control panel. repair 11/20: ADVNT114 Installation of an Orenco MVP Control Panel on a Post includes installation on a backer board | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 11/28/2023 | Dec 30 1899 2:11PM
04/21/2023 |  |  | 09-163-0011 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Ecoflo |  |  |  | Mound |  |  | [] | ["Control Operation","Attached Growth Medium","Distribution Pump Operation","Level Sensor Operation","Auxiliary Filter"] |  | Musty | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/20/2023 | 12:00 AM
06/15/2023 | Alternative | RoutineScheduled | 2010-143-0140 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1250 | Clearstream |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | 12:00 AM
07/21/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1500 |  |  | Pump | Gravity | Pad | Not Applicable | 750.000000 | ["None"] | ["None"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | Dec 30 1899 3:20PM
08/23/2023 | Alternative | Routine/Scheduled | 08-195-376-EXP | Washington | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | BioCoir |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/23/2023 | Dec 30 1899 10:00AM
12/21/2023 | Alternative | RoutineScheduled | 132-07-0133 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2024 | 12:00 AM
07/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 07/21/2023 |  | 55.000000 | [5 empty] | Will be sent separately | Inspected | Repaired broken pipe outside of pump tank | This AOSS should now return to normal function after having provided the above state routine maintenance | 08/23/2023 | 06:57 AM
09/30/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | DeHaven's Backhoe Service Inc. | 1942001541 | Wayne | Edmonson | 2.000000 | 2000 | Puraflo |  | Pump | Gravity | Trenches |  | 150.000000 | ["Attached Growth Medium","Effluent Screens","Level Sensor Operation"] | ["Attached Growth Medium","Effluent Screens","Level Sensor Operation"] | YES | [17 empty] | Changed out peat moss replaced 2 floats | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/01/2023 | 12:00 PM
06/01/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0197-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. While onsite septic tank was pumped out. Recirc tank was disassembled pumped out reassembled and refilled eith a water truck. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
10/18/2023 | Alternative | Routine/Scheduled | RMOS-9J9FWT | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | 12:30 PM
08/09/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
03/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/05/2023 | Alternative | RoutineScheduled | 121-STS-11906 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Southwest Soils, Inc. | 1942001494 | Stephen D. | Dalton | 1.000000 | 1500 | Aqua Safe AS 600 | None | Gravity | Pressure | Trenches | Not Applicable | 600.000000 | ["Other","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Other"] | NA | None | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | 01:30 PM
05/31/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/31/2023 | 12:00 AM
04/12/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 2.000000 | 2500 | Advantex AX25RT |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | Musty | [15 empty] | Inspected | Cleaned Sprayer manifold and pulled and cleaned recirc pump, cleaned inlet screen and ran system in testmode. Spary pattern good. Sludge levels. Septic tank#1 2-4" in scum and 12-16" sludge, Septic tank #2 0 scum and 6" sludge, Treatment tank had 8-10" sludge on both the recirclaution and discharge side. Discharge pump is PF100511 1/2hp and 110v and 10 gpm. internet monitoring connected septic system is working. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
09/21/2023 | Alternative | Routine/Scheduled | 09-163-0026 | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Bionest |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/21/2023 | Dec 30 1899 8:58AM
03/06/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Pad | Not Applicable |  | ["SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-12"sludge 4"scum/ Microfast-19"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ Pump out required of the Septic Microfast Tank due to sludge levels/ Blower air filter cleaned and working properly/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-552 ETM-83h 52m/ Pump2-499 ETM-80h 3m/ High-10/ Peak-10/ No breakout or spongy areas on the Pad area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/30/2023 |  | RoutineScheduled | SP-05-399 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Septic tank might need pump out next year.. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
08/08/2023 | Alternative | Routine/Scheduled | 133-STS-94404 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 1.5 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | 02:30 PM
05/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Needs riser replaced and electrical box on riser attached. Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/29/2023 | 12:05 PM
04/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/05/2023 |  | RoutineScheduled | 154-15-0073 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
09/19/2023 | Alternative | RoutineScheduled | 04310061 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  | Microfast Drip |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 12:00 AM
04/27/2023 |  | Reportable Incident |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Peatmoss Biofilter Replacement. Pumped septic tank for storage and for drying - replaced outdated effluent screen with new. Replaced spent biofilter media with new. Replaced discharge pump and float sensors. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | 07:45 AM
04/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | When we arrived the septic tank filter was clogged and the level in septic was high. After filter was cleaned level went back to normal. Both the septic and the pump tank need pumped out. The force main camlock was spraying when pump ran. Installed new gasket and ran pump all fixed. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
02/21/2023 |  | Routine/Scheduled | 228-18-0323 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/21/2023 | Jan 1 1900 11:00AM
04/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/02/2023 | Alternative | RoutineScheduled | 015-STS-334560 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Distribution Pump Operation","Effluent Screens"] | ["Distribution Pump Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | replaced discharge pump | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/06/2023 | 12:00 AM
12/14/2023 | Alternative | RoutineScheduled Component Maintenance | 165-STS-335554 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Small filter clog cleared Recommend to keep drainfield cleared off of leaves | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
11/11/2023 | Alternative | RoutineScheduled | 2051-98-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Control Operation","Dispersal System Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | Musty | Clear | 7.200000 |  |  | 1.900000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/13/2023 | 12:00 AM
12/20/2023 | Alternative | Follow-Up | 14-177-1059 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner |  |  | Microfast | [6 empty] | [] | [] | [18 empty] | Infiltrator Riser Installation (18in) | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | 12:00 AM
12/05/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.790000 |  |  |  |  | 12/05/2023 |  | 8.000000 |  |  | 9.200000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/27/2023 | 01:45 PM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Alarm was on upon arrival. Audible had been unplugged and was plugged back in. Recirculation float was stuck down. The system should return to proper operation now. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/25/2023 | Alternative | RoutineScheduled | 113-STS-25897 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [5 empty] | 01/25/2023 |  | 21.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2023 | 08:47 AM
03/04/2023 |  | RoutineScheduled | 2095-04-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | Musty | Clear | 7.200000 |  |  | 2.100000 |  | 03/06/2023 | Sample Chamber | 15.000000 |  |  | 8.800000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/17/2023 | 12:00 AM
07/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/20/2023 | Alternative | Initial Visit | 015-STS-338423 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 2.000000 |  | EZ Treat |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | 05:25 PM
06/16/2023 | Alternative | Routine/Scheduled | 053-STS-10332 | Dinwiddie | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/16/2023 | Dec 30 1899 1:12PM
03/17/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Siphon | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Needs new UV Unit. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/31/2023 | Jan 1 1900 12:26PM
10/17/2023 | Alternative | RoutineScheduled | 150-17-0073 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [17 empty] | Pumped Out | Replaced Floats | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/06/2023 |  | RoutineScheduled | 181-05-0036 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | Best1 |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NO | [17 empty] | The system did not need to be pumped, however the system will be routinely pumped next year. The effluent and spin filters were both cleaned. The controls were operating as designed. There were no visible leaks in the drip field. The drip field was operating as designed. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | 09:55 AM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
04/21/2023 | Alternative | Routine/Scheduled | 157-11-0174 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Pumped out tanks. Replaced spinfilter screen, replaced the diffuser, and replaced the pump float. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/21/2023 | 12:00 PM
08/07/2023 | Alternative | RoutineScheduled | 015-STS-337888 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | AdvantexAX20RT | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | NO | [7 empty] | 08/07/2023 | Pump Chamber | 8.000000 |  |  | 4.000000 |  |  | Attached to this report |  | The system did not need to be pumped. The service was for the 180 day sample draw. The BOD and TSS samples were within the permitted limits. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/26/2023 | 03:10 PM
01/10/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic-8"sludge 3"scum/ Microfast-6"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working properly/ Controls, pumps, Floats and alarms functioning properly/ Counts: Pump1-184 ETM-21h 43m/ Pump2-184 ETM-21h 43m/ Peak-3/ High-4/ No breakout or spongy areas on the LPD Pad site. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/26/2023 | Alternative | Routine/Scheduled | 07-120-0593A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Due for pump out. Refill is required for proper operation and to prevent damage to components. -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Due for pump out. Refill is required for proper operation and to prevent damage to components. Recirculation pump has exceeded life expectancy. Recirculation pump plumbing has exceeded life expectancy. Recirculation floats have exceeded life expectancy. -RSV: Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Discharge pump has exceeded life expectancy. Discharge floats have exceeded life expectancy. Vortex filter is torn -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Control panel has exceeded life expectancy -Drip Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | Dec 30 1899 3:25PM
05/15/2023 |  | RoutineScheduled | SWP-02- | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation"] | ["Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
12/21/2023 | Alternative | RoutineScheduled Component Maintenance | 175-17-0435 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation"] | ["Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | None | Clear | [5 empty] | 12/21/2023 | Sample Tap | [6 empty] | Will be sent separately | Inspected | Annual inspection. Owner now has an effective water treatment system and treated effluent looks much better. Collected effluent sample for 5-year BOD test, waiting on lab results. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 07:39 AM
03/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic/ Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic-12"sludge 2"scum/ Microfast-20"sludge 0"scum/ PUMP OUT REQUIRED DUE TO SLUDGE LEVELS/ Blower air filter cleaned and blower working properly/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/27/2023 | Alternative | RoutineScheduled Component Maintenance | VAG408196 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity |  | Chlorination |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | bad blower panel replaced replace bottom float Please add additional floats | This AOSS should now return to normal function after having provided the above state routine maintenance | 01/15/2024 | 10:39 AM
06/15/2023 |  | RoutineScheduled | 101-19-0164 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 12:00 AM
11/22/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | MicroFast | Pump | Pressure | Drip |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","SludgeScum Accumulation"] | [18 empty] | 0 Scum, 10" of sludge, 48" overall liquid. Blower, alarms, pump, transducer working. Clog in the sewer line owner is going to unclog. pump runs, water level low to pump water. reading 1.5 on the transducer for start level, changed start level to 6.1 so PT has more water in it & not pumping dry, field dry. did not check return pressure. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | 12:30 PM
01/02/2023 | Alternative | Reportable Incident | 073-STS-101398 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Repair - Install of VDH Permit 136-22-0242 - GMP2018-02 Installed Infiltrator Poly tank as septic tank - risers to grade & effluent screen. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/03/2023 | 07:00 AM
09/26/2023 | Alternative | Routine/Scheduled | 147-13-0044 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Pressure | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/26/2023 | Dec 30 1899 12:52PM
12/28/2023 | Alternative | RoutineScheduled | 182-06-0386 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Pumping to be scheduled | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 12:00 AM
07/06/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | Dec 30 1899 12:46PM
10/17/2023 | Alternative | Reportable Incident | 10-173-103 | Prince Edward | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Septic | ECO FLO | Pump | Pressure | Mound |  | 350.000000 | ["Distribution Pump Operation","Control Operation"] | ["Effluent Screens","Dispersal System Operation","Control Operation"] | YES | Septic | Cloudy | [14 empty] | Inspected |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/17/2023 | Dec 30 1899 10:00AM
04/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NO | [17 empty] | System in alarm at arrival due to clogged Hydraulic filter-Cleaned/ Septic Tank-6"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Controls, pump, floats and alarms functioning properly/ Need to replace 3-zone solenoids and 2-filter solenoids in the hydraulic unit which are faulty/ Watermeter-2,866,220/ No breakout or spongy areas on the drip field but not dosing properly due to faulty solenoids. Returned on 4/24/2023 to replace faulty solenoids: Installed-3 NO zone solenoids, tested and now functional/ Replaced- 2 NC filter solenoids, tested and now functional/ Current Watermeter reading-2,867,569 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
07/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 12:00 AM
09/13/2023 | Alternative | RoutineScheduled | 095-STS-6604 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Hutchens Septic Services LLC | 1942001509 | Robert | Hutchens, Jr. | 1.000000 | 1500 | BioCoir NS500 | BioCoir Ns500 | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
05/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/15/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Puraflo |  |  | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles","Attached Growth Medium"] | ["Attached Growth Medium","Septic Tank Baffles"] | [18 empty] | Peat had been added to pods | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/15/2023 | 12:00 AM
10/03/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles","SludgeScum Accumulation","Recirculation Pump"] | ["Septic Tank Baffles","Auxiliary Filter","SludgeScum Accumulation","Recirculation Pump"] | [17 empty] | Pumped Out | Pump and floats replaced. Pump out all tanks | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/06/2023 | 12:00 AM
11/20/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | Dec 30 1899 12:15PM
04/03/2023 |  | Routine/Scheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [16 empty] | Pumped Out |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/18/2023 | 02:48 PM
06/01/2023 | Alternative |  | 05-192-278 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 06/01/2023 |  | 2.260000 | [5 empty] | Will be sent separately |  | BOD: 2.26 TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 12:00 AM
04/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/26/2023 | Alternative | RoutineScheduled | 94-184-5001 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 5.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
03/28/2023 |  |  | 2018-143-0073 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Aquaklear | [6 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
04/24/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
08/29/2023 | Alternative | RoutineScheduled | 185-STS-17515 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | ADVANTEX |  | Pump | Pressure | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","Disinfection","Distribution Pump Operation","Recirculation Pump","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Disinfection","Distribution Pump Operation","Level Sensor Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Recirculation Pump"] | NA | Musty | Clear | [15 empty] | 3 - Blue Crystal tablets installed 6 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/29/2023 | 12:00 AM
10/06/2023 | Alternative | RoutineScheduled Component Maintenance | 179-08-0237-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Broken lid and riser for sample box, replaced both. Roots in 4 pods, cut roots on the outside and left handles exposed to prevent roots from growing in and pulled roots out. Recommend to upgrade pump when it fails or if the rates decrease. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
03/21/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 | 500 | 1000 |  | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [17 empty] | When we arrived found inlet T clogged and airblower and uv light not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/14/2023 | Dec 30 1899 5:20PM
11/20/2023 | Alternative | RoutineScheduled Component Maintenance | 177-09-0074 SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | The peat in the Puraflo module is settling and showing some signs of aging. Peat replacement or the installation of a different treatment system may be recommended in the near future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
04/03/2023 |  | Routine/Scheduled | 234-15-218 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | Jan 1 1900 3:40PM
01/03/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [7 empty] | 01/03/2023 |  | 31.000000 | [5 empty] | Will be sent separately | Inspected | Clog on RSV cleaned Lab sample normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
04/30/2023 | Alternative |  | SD-10-247 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping micro fast. Strongly recommend clearing/mowing drainfield area before any brush gets too large. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/20/2023 | Alternative | RoutineScheduled | 121-STS-12411 | Montgomery | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - New River | King's Alternative Septic | 1942001112 | William | King, II | 1.000000 | 1000 | Aqua Safe AS500 |  | Gravity | Gravity | Discharge | UV | 250.000000 | ["Disinfection"] | ["Disinfection"] | NA | [17 empty] | Changed UV light, system is working correctly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/20/2023 | 12:00 AM
09/11/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Routine Annual, nothing to report | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/11/2023 | 12:00 AM
10/02/2023 | Alternative | RoutineScheduled | C-07-111-0053 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only |  | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The controls were operating as designed. There were no visible leaks in the LPD leech system. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | Dec 30 1899 6:05PM
10/17/2023 | Alternative | Routine/Scheduled | 093-13-0155 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | Dec 30 1899 1:00PM
04/27/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | uv light bulb needs replaced not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
05/31/2023 | Alternative | RoutineScheduled | VAG408508 | Rockbridge | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | AdvantexAX20RT | Pump | Gravity | Discharge | UV |  | ["Effluent Screens","Disinfection"] | ["Effluent Screens","Disinfection"] | YES | [17 empty] | The system did not need to be pumped. The system did not have a discharge at the time of visit so a sample draw was not taken. The UV light was not working at the time of visit so a new UV lamp was installed. The effluent filter was cleaned. The textile sheets were sprayed off. Both pumps were pulled and sprayed off. The evaporation bed was operating as designed. The controls were operating as designed. The lids were secured. | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 06/06/2023 | 11:20 PM
04/14/2023 |  | Follow-Up | 175-06-0512 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Drip pump & enable float replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 04:23 AM
10/30/2023 | Alternative | RoutineScheduled | 109-STS-31754 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | system check okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/18/2023 | Alternative | RoutineScheduled Component Maintenance | 179-14-0243-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite to inspect system. Two part microfast tank is in high level and blower is getting hot a shutiing down due to clogged media. Outlet riser leaks on pump tank. Proposal to be sent to repair the system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
03/20/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | k-rain was replaced and septic system is in working condition | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
01/15/2023 |  | RoutineScheduled |  | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2500 | septic | sand filter | Gravity | Pressure | Discharge | Chlorination |  | [] | [] | YES | Musty | Clear | [15 empty] | No Discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/18/2023 | 10:10 AM
08/16/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/30/2023 |  |  | 087-STS-6415 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 1.000000 | 1200 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","SludgeScum Accumulation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles"] | YES | Musty | Clear | 7.000000 |  | 7.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 12:00 PM
10/11/2023 | Alternative | RoutineScheduled Component Maintenance | 154-07-0252 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
08/08/2023 | Alternative | Routine/Scheduled | 234-16-307 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | Dec 30 1899 2:35PM
10/06/2023 | Alternative | Routine/Scheduled | 07-142-0070 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Outlet tee appears to be intact. Not due for pump out. No riser access -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Recirculation pump has exceeded life expectancy. Recirculation pump plumbing has exceeded life expectancy. Recirculation floats have exceeded life expectancy. -RSV: Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. Discharge pump has exceeded life expectancy. Discharge pump plumbing has exceeded life expectancy. Discharge floats are not properly secured. Discharge floats have exceeded life expectancy. Noted root and signs of groundwater infiltration within discharge riser -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Checked and confirmed spray height is good. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Control panel has exceeded life expectancy -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | Dec 30 1899 12:27PM
08/01/2023 | Alternative | RoutineScheduled | 39010 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
03/06/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Rejected | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity |  | UV |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | 6.800000 | 13.200000 |  | 0.000000 | [9 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | Dec 30 1899 3:58AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The inlet riser on the septic tank is damaged and requires replacement. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/31/2023 |  | Initial Visit | 182-15-0053 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST | [6 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | relaced blower | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/31/2023 | 12:00 AM
09/11/2023 | Alternative | Reportable Incident | 228-11-0539 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/11/2023 | Dec 30 1899 11:00AM
06/30/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [8 empty] | 06/06/2023 | Sample Tap | 24.000000 |  |  | 23.800000 | 29.000000 |  | Attached to this report |  | Results attached | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 08:45 AM
12/18/2023 | Alternative | RoutineScheduled Component Maintenance | 2045-02-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Chlorination |  |  |  | NA | Septic | Clear | 7.500000 | 18.400000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 01/16/2024 | 01:58 PM
09/25/2023 | Alternative | Routine/Scheduled | 15-120-0279A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Multiflo FTB |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/25/2023 | Dec 30 1899 11:13AM
03/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
01/03/2023 |  | RoutineScheduled | 08-100-0988 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Pad | Not Applicable | 600.000000 | [] | [] | YES | [17 empty] | Everything working properly. Recently pumped. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/13/2023 | 10:55 AM
05/16/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | [16 empty] | Inspected | Septic Tank minimal scum, 8" sludge, Pump Tank 10" sludge. Peat Pods peat is in good conditon for age. Turned peat and looks good, Cleaned Effluent filter. Alarm sounds indoors and pump runs on timers dosing. Floats appear to function, Pump run time 7775.33 hours and 15703 cycles. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
05/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
01/10/2023 |  | RoutineScheduled | 195-Discharge-21118 Grassy Ridge Road | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 3 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/10/2023 | 12:00 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/30/2023 |  | RoutineScheduled | 2032-96-153 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity |  | Chlorination |  | ["Control Operation" ,"Disinfection" ,"BlowerCompressorAerator Operation"] | ["Disinfection"] | NA | Septic | Cloudy | [13 empty] | Will be sent separately | Inspected | PC is not working PC has power but not screen | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 06/15/2023 | 12:05 PM
12/19/2023 | Alternative | Reportable Incident | 800-STS-15495 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/19/2023 | Dec 30 1899 10:00AM
12/28/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20192 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | 01:58 PM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
05/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 05/31/2023 |  | 87.000000 | [5 empty] | Will be sent separately | Inspected | 2 psi rb blower installed audible and visual alarm | This AOSS should now return to normal function after having provided the above state routine maintenance | 07/06/2023 | 08:40 AM
04/07/2023 |  |  | 11-142-0130 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Ecoflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Inspected | Replace 15x25" dbox lid | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | 12:00 AM
07/13/2023 | Alternative | RoutineScheduled Component Maintenance | 177-07-0196-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Small grass root on septic tank inlet riser, removed and sealed. HL 27, LL43, OVERRIDE 291. Treatment is crystal clear. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/18/2023 | 11:45 AM
05/22/2023 | Alternative | RoutineScheduled Component Maintenance | 179-15-0091-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
10/12/2023 | Alternative | RoutineScheduled | 09-197-A1 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 7.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
05/02/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity |  | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
08/21/2023 | Alternative | Routine/Scheduled | 05-142-0110 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | [17 empty] | Recirculation pump filter cleaned on 7/27/23 when clogged and caused alarm. Recirculation pump bottom float was down because Recirculation Spliter Valve (RSV) was stuck causing all effluent to go to discharge tank. The RSV was cleaned and the Advantex manifold and unit were flushed. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/21/2023 | Dec 30 1899 11:40AM
04/05/2023 | Alternative |  | 101-18-0404 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Jim & Frances | McBride | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/09/2023 |  | RoutineScheduled | SWP-05-136 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | The O-ring for the RSV is leaking and should be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
03/31/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | Delta Environmental Products, DF Series | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air release valve was repaired. System should resume proper function | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/27/2023 | Alternative | RoutineScheduled Component Maintenance | 182-04-0016 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 11/27/2023 |  | 48.000000 | [5 empty] | Will be sent separately | Inspected | Repaired zone valve which should help with the surfacing | This AOSS should now return to normal function after having provided the above state routine maintenance | 01/15/2024 | 10:39 AM
01/26/2023 |  | RoutineScheduled | 06-142-0263 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 |  | EcoPOD |  | Pump | Pressure | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | Jan 1 1900 8:35AM
05/10/2023 | Alternative | RoutineScheduled | 108-05-0043 | Bath | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | Delta Whitewater | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Dispersal System Operation"] | ["Auxiliary Filter","Dispersal System Operation"] | NA | [17 empty] | The system did not need to be pumped. The blower and spin filter were both cleaned. The controls were operating as designed. There were no visible leaks in the drip field. There was return effluent returning to the pump tank so the drip field was operating as designed. There was a pressure gauge added to the return line so the pressure could be adjusted to the desired pressure. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/06/2023 | 09:35 PM
05/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
07/10/2023 | Alternative | RoutineScheduled | 181-11-0059 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 2000 | MicroFast |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The blower filter was cleaned. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | 09:45 PM
07/05/2023 | Alternative | Reportable Incident | {FIPSCode}-STS-5042 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/05/2023 | Dec 30 1899 2:00PM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
04/18/2023 | Alternative | RoutineScheduled | 061-17-375 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation" ,"Distribution Pump Operation"] | ["Level Sensor Operation" ,"Control Operation" ,"Distribution Pump Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Owner uses very little water (average of about 1 dose per day) as indicated from number of dosing cycles recorded since last year. Pump is not accessible from ground surface, so piping needs to be corrected. Infiltration at pump tank concrete riser joint was observed a couple of years ago after a heavy rain - riser joint needs resealed. Peat is old but has had little use. It has lost some texture but otherwise is in very good shape (at least what is visible on top). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
08/30/2023 | Alternative | RoutineScheduled | 175-19-0149 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | YES | [17 empty] | Septic Tank-7"sludge 0"scum/ EZ-Treat Recirculation Tank-5"sludge 0"scum/ No pump out needed at this time/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-0,147,713 ETM-0761962 On-3m Off-10m/ Pump intake cleaned/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/21/2023 |  | Reportable Incident | S 800-19-0037 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | System pumped empty to enact a saturation test to find possible leaks in tanks and risers. ST = 0 at end of test had 28" - severe leak around inlet and outlet baffles. PT = 0 at end of test had 0" ... pump tank not an issue. Inlet and Outlet of septic tank re-sealed / parged. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | Jan 1 1900 10:00AM
12/04/2023 | Alternative | Pump-Out Only | 136-00-0439 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Pumped/ cleaned treatment tank Refilled with clean water | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 09:25 AM
04/27/2023 | Alternative | RoutineScheduled | 061-19-146 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank to Clearstream ATU | Pump Tank | Pump | Pressure | Drip | UV |  | ["Dispersal System Operation","BlowerCompressorAerator Operation"] | ["Dispersal System Operation","BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-0"sludge 0"scum/ Clearstream-0"sludge/ Pump Tank-0"sludge/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ Controls, pump, floats and alarms functioning properly/ Jet UV-Light functioning properly, sleeve cleaned/ Found broken drip tubing leaking in the drip field and repaired during inspection/ No breakout or spongy areas in the drip field and dosing properly after repair On-4m Off-2h 18m/ No counts or watermeter. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | Dec 30 1899 12:26PM
08/30/2023 | Alternative | RoutineScheduled | 115-06-0510 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Other conventional maintenance performed | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Septic Tank | Whitewater | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Musty | [15 empty] | Inspected | Septic tank Sludge levels-2-3" scum 12" still Heavy sludge (but improved since last year but still Need pumping again this year) -Treatment tank- Good aeration, 4-5" scum and too much sludge - needs pumping again. Cleaned blower airfilter. Blower alarm is tested good, Pump tested good, Reccomend to pumnp prior to our visit next year or sooner. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | 09:30 PM
08/24/2023 | Alternative | Reportable Incident Component Maintenance | 179-STS-90050 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for systemin alarm due to air locked pump. Tanks were pumped out prior to site visit. Released the air in the force main and redid all wire connections in the junction box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance | 182-17-0272 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 05/24/2023 |  | 27.000000 | [5 empty] | Will be sent separately | Inspected | Filter was clogged recommend every 3 or 6 month cleanings let us know if want us to perform | This AOSS should now return to normal function after having provided the above state routine maintenance | 07/06/2023 | 08:40 AM
10/09/2023 | Alternative | Reportable Incident Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Installed Norewco UV unit. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/16/2023 | Dec 30 1899 12:58PM
09/17/2023 | Alternative | RoutineScheduled | 061-STS-25205 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | septic | Microfast | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/17/2023 | 02:05 PM
11/09/2023 | Alternative | RoutineScheduled | VAG408480 | Rockingham | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Gravity | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation","Attached Growth Medium"] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation","Attached Growth Medium"] | [17 empty] | Pumped Out | FAST uncovered and cleaned. Tablet detection sensor removed. No discharge at this time | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 12/14/2023 | 12:00 AM
10/11/2023 | Alternative | Routine/Scheduled |  | Surry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Found at normal level, 4in of sludge and less than 1in of solids. Pulled and cleaned filter -Discharge/Pump Tank: Found at normal level. Found less than 1in of sludge and solids. Tested floats and pump all working as they should. -Peat Moss: Raked Peat on all modules. Peat is breaking down and compacting. Peat change will probably need changing next year -Control Panel: 120 volts audio and visual alarms working as they should. Tested timer. Pump pulled 9.7 amps. Wrote counts down on card -Chlorination/Dichlorination: Found at normal level, no chlorine tablets or dechlorination tablets found. -Distribution Box: Dbox lid is broken, 4 lines taking water. No cracks in dbox. -Drain Field: No signs of surfacing in drainfield area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | Dec 30 1899 3:37PM
05/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Strongly recommend clearing the mounds. The vegitation is starting to get larger and thicker closer to the mounds. Machines should not be used and it should be cleared by hand. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/23/2023 | Alternative | RoutineScheduled Component Maintenance | SP-05-445 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
05/01/2023 | Alternative | Routine/Scheduled | S 800-13-0153 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Drip | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | Dec 30 1899 12:25PM
10/03/2023 | Alternative | RoutineScheduled | 2014-143-0032 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Norweco |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation"] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/03/2023 | 12:00 AM
08/14/2023 | Alternative | RoutineScheduled | 154-98-0257 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 4.000000 | 3000 | Sand Filters (2) |  | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["Auxiliary Filter","Effluent Screens","Dispersal System Operation"] | YES | Musty | Clear | [14 empty] | Inspected | Sludge/ Scum Accumulation - Septic 6", Pump 0" 2 Sand filter tanks - sand clean and spraying properly 2 drip zones - system flushed effluent filter cleaned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/14/2023 | 12:00 PM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/27/2023 |  | RoutineScheduled | 177-STS-89491 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Recirculation Pump"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
08/16/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | [9 empty] | ["Auxiliary Filter"] | ["Auxiliary Filter"] | [18 empty] | Replace Peat Moss in 5 Pods/ install 1 Pump and 1 check valve | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/31/2023 | Dec 30 1899 4:30PM
09/11/2023 | Alternative | Routine/Scheduled | 10-120-0145A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Recirculation Pump","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/11/2023 | Dec 30 1899 11:51AM
06/20/2023 | Alternative | Routine/Scheduled | 550-STS-5883 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | Dec 30 1899 1:45PM
04/20/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/17/2023 | Alternative | Routine/Scheduled | 093-11-0065 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | Replaced aerator and UV control panel | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | Dec 30 1899 9:00AM
12/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
08/09/2023 | Alternative | RoutineScheduled | SD-09-312 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Septic tank | Pura flo | Pump | Gravity | Trenches | Not Applicable | 62.500000 | ["Attached Growth Medium","Level Sensor Operation"] | ["Attached Growth Medium","Level Sensor Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/22/2023 | 10:00 AM
12/19/2023 | Alternative | RoutineScheduled | 182-10-0279 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.640000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 09:45 AM
05/24/2023 | Alternative | RoutineScheduled | 061-STS-26987 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 65.500000 | ["Effluent Screens"] | ["Dispersal System Operation"] | YES | [17 empty] | System was turned into Microfast. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 11/08/2023 | 12:00 PM
08/01/2023 | Alternative | RoutineScheduled | 159-15-183 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | replaced UV bulb, cleaned atu filter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/19/2023 | Alternative | RoutineScheduled | 13-163-0064 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Clearstream |  | Pump | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/19/2023 | 12:00 AM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | UV |  |  |  | NA | Musty | Clear | 7.300000 | 9.200000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/11/2023 | Dec 30 1899 11:24AM
04/19/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Both solenoid valve assemblies struggle to stay closed due to worn/ weak diaphragms. Owner has verbally approved replacement. Septic tank and drip pump tank would benefit from pumping. Owner has already called and made an appointment with Septic Clean. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/01/2023 | Jan 1 1900 6:44AM
12/04/2023 | Alternative | RoutineScheduled | 06-184-5006 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/04/2023 | 12:00 AM
07/28/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [9 empty] | [] | [] |  |  |  | 7.830000 | [14 empty] | Flow meter isn't working. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 04:50 PM
02/21/2023 |  | Routine/Scheduled | 228-05-0655 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | Jan 1 1900 9:15AM
11/29/2023 | Alternative | RoutineScheduled Component Maintenance | 175-16-0299 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 09:34 AM
07/31/2023 | Alternative | Initial Visit | 115-STS-95507 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 5.000000 |  | 745.000000 | [5 empty] | Owner called due to the alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. Fixed the grade on the pipe in the Clearstream. The timer is set to 5 minutes every 2 hours. Took initial BOD and Fecal samples. NOTE - Fecal sample was high - system should function properly after service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | 09:45 AM
10/11/2023 | Alternative | RoutineScheduled | 07-197-023 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation"] |  |  | Musty | [16 empty] | Homeowner met me in the yard and advised that the pump has been messed up and he is waiting on y&y to come out to fix it. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
04/01/2023 | Alternative | Routine/Scheduled | R15-180-0076 | Roanoke City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/01/2023 | Jan 1 1900 9:30AM
10/12/2023 | Alternative | RoutineScheduled | 16-100-0414 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | AQUASAFE |  | Pump | Pressure | Mound | UV | 600.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | SLUDGE JUDGE SEPTIC TANK-3-4" FROM BOTTOM, 1" FROM TOP, SLUDGE JUDGE AQUASAFE LESS THAN 1/3 SOLIDS, EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 10:55 AM
11/09/2023 | Alternative | RoutineScheduled Component Maintenance | 175-15-0461 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Delta Environmental Products, UC Series | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 10:33 AM
05/24/2023 | Alternative | RoutineScheduled | 061-STS-26472 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/31/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic / Ecopod ATU Treatment Tank | Pump Tank | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-12"sludge 4"scum/ Ecopod ATU-20"sludge/ Pump Tank-3"sludge 0"scum/ Pump out required on the Septic-Ecopod Tank/ Blower air filter cleaned and the blower is working properly/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-1543 ETM-77h 24m/ Pump2-1489 ETM-74h 54m On-3m 4s Off-9h 56m Peak Off-7h 56m Dose-187.5 every 10hrs. / Peak-24/ High-15/ No breakout or spongy areas on the Drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/20/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 500 | Bio Microbics-Fast |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [16 empty] | Inspected | Contacted due to an alarm. Sludge level-scum layer 12" and septic zone 24"+ sludge in Septic zone of tank. Septic zone and grease traps need pumping. Blower makes good aeration in treatment tank, replaced 2014- Alarm operational, cleaned blower air filter. System Pumping is needed and we contacted Rotorooter. Pump tank as well, Checked the alarm and it is operational and the pump runs when called by the floats. Tank water level was at the correct height. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
04/12/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Advantex AX25 RT |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Septic tank minimal scum, Sludge level-3".Septic Tank #2 8" sludge, No scum in treatment and a 7" sludge in Recirc tank and 8" sludge Discharge zone. Cleaned effluent filter, ALarm lights but did not sound, all floats repsond correclty, Media looked good, spray pattern was good- minimally dirty. System has a normal odor and nothing unusual noted. Does not need pumping this year. Recirc runt time 1497.9 hrs or 801.2 hours since last visit and meter shows 10625 cycles vs 51408 Cycles last year, which means is clocked over99999 and is about 59216 cycles since last year , Discharge pump 317 hrs vs 181.2 hrs run and 2182 cycles vs 1235 cycles last year. System ihas monitoring connected but appears to have not called in since last september. 911days in service trended sine 11-2-20 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
03/28/2023 |  | RoutineScheduled | 175-02-0499 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
12/15/2023 | Alternative | Routine/Scheduled | 01-160-0317 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/15/2023 | 01:45 PM
03/13/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/20/2023 | 12:00 AM
05/04/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/04/2023 | 12:00 AM
12/11/2023 | Alternative | Reportable Incident | 103-STS-93166 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | power failure from house, electrician replaced main feed to control panel, system check - okay | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
01/13/2023 |  | Routine/Scheduled | 13-174-0056 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Trash Tank - normal level Aeration Tank - mixing present - aspirator serviced. Clarifier - effluent screen serviced Pump Tank - float sensors, pump and controls operating. Drip =- headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | Jan 1 1900 12:45PM
10/04/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Puraflo | none | Gravity | Gravity |  | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
10/11/2023 | Alternative | Routine/Scheduled | 147-16-0004 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/11/2023 | Dec 30 1899 4:14PM
03/09/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [7 empty] | 03/09/2023 |  | 78.000000 | [5 empty] | Will be sent separately | Inspected | Alarm unplugged | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
03/21/2023 |  | Reportable Incident | 550-STS-6492 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation"] | N/A | [17 empty] | Replaced control panel, timer enable float and alarm float. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/21/2023 | Jan 1 1900 9:30AM
05/08/2023 |  | RoutineScheduled | 177-STS-88933 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
05/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump 1 of 2 is not functioning at this time. Homeowner is reaching out to get pump replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
10/10/2023 | Alternative | RoutineScheduled | 099-07-0015-SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned pump and filters | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/24/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced E294 effluent pump. Drainfield area dry. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/15/2023 | Dec 30 1899 12:05PM
11/02/2023 | Alternative | Routine/Scheduled | 036-STS-34542 | Charles City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/02/2023 | Dec 30 1899 2:58PM
12/07/2023 | Alternative | RoutineScheduled | 14-184-055 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Not Applicable |  |  |  |  | None | Clear | 7.500000 | 8.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/12/2023 | Alternative | Routine/Scheduled | 810-STS-3916 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | Dec 30 1899 9:30AM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | 175-05-0428 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Conducted routine inspection to satisfy Prince William county's requirement for a S.A.P. inspection prior to their issuing a building permit. This system only has one tank (SBR) and it was pumped this morning by Extreme PSI. Tank had been refilled with enough fresh water to conduct inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
04/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/11/2023 | Alternative | RoutineScheduled | 101-06-0369 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Old Dominion Engineering | 1942001085 | Michael | Craun | [9 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Other"] |  | None | Clear | 3.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | 03:15 PM
11/03/2023 | Alternative | RoutineScheduled | 05-197-A5 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.500000 | 8.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
03/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | UV |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | Dec 30 1899 3:30PM
01/13/2023 |  | RoutineScheduled | 179-13-0067-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Level Sensor Operation" ,"Control Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Big O-ring for filter in head unit needs to be replaced broken (small leak). Regrowth in pump tank looks like is mixed up with broken down toilet paper. Spoke customer about it and gave him Do's and Dont's. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
01/13/2023 |  | RoutineScheduled | SWP-03-519 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Gravity | Gravity |  | Not Applicable |  |  |  | NO | Musty | Clear | [13 empty] | Will be sent separately | Inspected | 90-Day Inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
03/06/2023 |  | RoutineScheduled | 07-197-A15 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 3 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/06/2023 | 12:00 AM
03/24/2023 |  | RoutineScheduled | SWP-04-515 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
03/22/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | Enviro-Flo | none | Gravity | Gravity |  | Chlorination |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
10/26/2023 | Alternative | Routine/Scheduled | 159-06-0368 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Normal Level Less than 1"of sludge and less than 1"of solids Pulled and cleaned rsv No signs of infiltration -Recirculation Tank: Normal Level Less than 1"of suspended solids Pulled and cleaned biotube filter, pump, and floats Pump and floats functioning properly No signs of infiltration -RSV (Recirculating Splitter Valve): Flushed rsv Cleaned rubber boots Made sure inlet was clear of debris -Discharge/Pump Tank: Normal Level 4" of suspended solids All floats and pump are functioning properly No signs of infiltration -Media Sheets: Sprayed off media sheets Flushed and brushed laterals Flushed media module until water ran clear -Control Panel: 120 to all breakers Recirc pump pulled 10.79amps Discharge pump pulled 7.34amps -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | 07:59 AM
05/11/2023 |  | RoutineScheduled | 179-STS-88952 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Recirculation Pump"] | ["Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
07/10/2023 | Alternative |  | 06-113-241 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/10/2023 |  | 4.490000 | [5 empty] | Will be sent separately |  | BOD: 4.49 TSS: BDL | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/10/2023 | 12:00 AM
05/17/2023 | Alternative | Routine/Scheduled | 196.87.297 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Sandfilter, Non-recirculating |  | Pump | Pressure | Mound |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [5 empty] | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | 04:30 PM
01/19/2023 | Alternative | RoutineScheduled | SD-13-181 | Culpeper | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity |  | UV |  | ["Control Operation" ,"Disinfection" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Control Operation" ,"Attached Growth Medium" ,"Recirculation Pump"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The Orenco UV bulb is not working and should be replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/01/2023 | 12:05 PM
12/13/2023 | Alternative | Routine/Scheduled | 18-142-0034 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Septic Tank Condition of above Component Notes for above Component Water level normal. Inlet tee appears to be intact. Flushed and cleaned effluent screen. Not due for pump out. Recirculation Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Discharge/Pump Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Discharge pump is pulling 13.1 amps Discharge pump is rated for 12.7 amps @ 115 volts Media Sheets Condition of above Component Notes for above Component Cleaned media sheets. Checked and confirmed spray pattern is good Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | Dec 30 1899 9:45AM
11/07/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | LP |  |  | Pressure | Trenches | Not Applicable |  | [] | [] | [18 empty] | recommended scheduling of pumping to be done in 2024 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/07/2023 | 12:00 AM
08/07/2023 | Alternative | RoutineScheduled Component Maintenance | 179-15-0255-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Control Operation" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Both tanks ready for pumpout due to sludge levels. Wet spot in middle of drip field most likely due to return valve not holding up pressure. Will send proposal for pumpout and to replace return valve asap. Treatment is crystal clear. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
09/11/2023 | Alternative | Reportable Incident | 08-163-0100 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Came out for Alarm call - Customer stated he hit Junction box Found Junction box for recirc tank dug up and with hole in it. Customer also cut pump cord and alarm flat wire Tank was above normal Level Replaced all wires and pumped tank below alarm float | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | Dec 30 1899 10:28AM
06/27/2023 | Alternative | RoutineScheduled | 109-06-0305 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Multiflo |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Wiring issue insidne control box causing contactor to not work in RK panel | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/30/2023 | 09:30 AM
10/21/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 500 | EcoFlow | EcoFlow | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. Cleaned septic tank solids filter. 12" of solids in discharge pump tank. Raked peat in both treatment units. Excellent treatment quality. Manually ran discharge pump and tested alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 07:03 PM
07/25/2023 | Alternative | Routine/Scheduled | 04-163-0208 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. BioFilter - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | Dec 30 1899 7:45AM
10/12/2023 | Alternative | RoutineScheduled | SD-06-22 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches |  | 43.750000 | ["SludgeScum Accumulation"] | ["Attached Growth Medium","Effluent Screens","Dispersal System Operation"] | YES | Septic | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/14/2023 | 08:30 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | UV light is not functioning | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
05/11/2023 |  | RoutineScheduled | 17-118-0005 | Charles City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | EZ Treat |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","Control Operation","Recirculation Pump","Distribution Pump Operation","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/11/2023 | 12:00 AM
02/09/2023 |  | RoutineScheduled | 099-STS-91700 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [5 empty] | 02/09/2023 |  | 15.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. 14" of broken down paper in septic tank, will check again next visit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/18/2023 | Alternative | RoutineScheduled |  | Culpeper | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Pending Review | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1500 | septic | Multi-flo | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | YES | Septic | Discolored | [14 empty] | Pumped Out |  | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 12/11/2023 | 07:50 AM
03/30/2023 |  | RoutineScheduled | 175-16-0065 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
03/08/2023 |  | RoutineScheduled | 95-186-095 | Smyth | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 2 Chlorine 3 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/08/2023 | 12:00 AM
04/27/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Gravity | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | Jan 1 1900 12:48PM
04/27/2023 | Alternative |  | 150-18-0099 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Multi Flo | [6 empty] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","BlowerCompressorAerator Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 12:00 AM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2024 | 12:23 PM
04/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | This is a 5 pod purflo septic system. The pods are draining but peat is very broken down and sandy. A sample will be taken | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
08/08/2023 | Alternative | Initial Visit | 023-STS-43502 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | EcoFlow |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | First annual inspection. 22" of accumulated solids in septic tank. Homeowner indicated that it has never been pumped. Based on settling characteristics, the septic tank will be re-evaluated next year to determine if pumping is needed. Septic tank solids filter was very clogged and was resulting in the water level in the septic tank to be slightly elevated. Cleaned septic tank solids filter and replaced. removed tipping tray and flow diverters from EcoFlow unit. tipping tray working as designed. Peat was raked to breakup and level. Condition of peat was good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/17/2023 | Jan 1 1900 7:03PM
10/03/2023 | Alternative | RoutineScheduled | 1999-143-0279 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 6.000000 |  | Puraflo |  | Pump | Gravity | Pad |  |  | [] | ["Attached Growth Medium","Control Operation","Level Sensor Operation"] |  | None | Cloudy | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/03/2023 | 12:00 AM
10/19/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/19/2023 | Dec 30 1899 12:40PM
07/17/2023 | Alternative | Routine/Scheduled | 093-12-0164 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Delta Environmental Products, UC Series |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration tank - noraml level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - concrete - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/18/2023 | Dec 30 1899 8:00AM
06/23/2023 | Alternative | RoutineScheduled | 181-06-0309 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 2.000000 | 2000 | Ecoflo |  | Pump | Pressure | Trenches |  |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | Filters checked and cleaned. Cleaned tipping bucket and trays. Peat moss raked and in good condition. System did not need to be pumped. No apparent leaks in system or drain field area. Control panel functioning properly. Lids properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 11:25 AM
04/06/2023 |  | RoutineScheduled | 175-19-0166 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter"] | ["Auxiliary Filter"] | NO | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
01/10/2023 | Alternative | Reportable Incident | 103-STS-101800 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 |  |  | Pump | Gravity | Trenches | Not Applicable | 300.000000 | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | COSS - Repair - VDH Permit 151-22-0196 - GMP2018-02 Original septic tank pumped empty and abandoned. Installed new 1500 gallon top seam STEP Tank Installed new 2" PVC forcemain. Installed new 8 port concrete distribution box. Installed new absorption laterals. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/11/2023 | 11:45 AM
01/16/2023 |  | RoutineScheduled | 179-15-0247-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment is cloudy due to customer using medication. Water level was a little above normal pumped it down to see media and appears to be clean. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
11/27/2023 | Alternative | RoutineScheduled Component Maintenance | 177-07-0017-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium" ,"Control Operation"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | There are roots growing in at the base of the riser on the septic tank. If you get alarms during periods of heavy rain we recommend excavating and resealing this riser. The contractor in the control panel is louder than normal and may be failing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
04/10/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Micro fast | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [18 empty] | Needs to install four new float sensors and a new pump pit lid. Also needs to add Lye to micro fast system and pump the tank and add fresh water. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12:00 AM
09/15/2023 | Alternative | Reportable Incident Component Maintenance | 179-08-0001-SWP | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to hung toliet. While onsite video inspected header lines and roots have gotten worse. updated proposal to be sent. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/02/2023 | 05:18 AM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend replacing discharge pump chamber lid. Peat is showing signs of its age. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/27/2023 | Alternative | Routine/Scheduled | 228-05-0905 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/27/2023 | Dec 30 1899 11:50AM
02/10/2023 | Alternative | RoutineScheduled | 154-06-0514 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for rountine inspection and a aerator alarm. Aerator was not running due to a panel failure. installed new panel and reprogramed new panel. All tanks need to be pumped out due to sludge increasing drasiticlly due to the use of scent beads and fabric softner. Made homeowner aware and pump out has been scheduled | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
06/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/11/2023 |  | Routine/Scheduled |  | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 |  |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Processing Tank - recirc - recirc pump, media drapes & spray grid serviced. Processing Tank - discharge - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | Jan 1 1900 7:45AM
03/27/2023 |  | Pump-Out Only |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Aquarobic Mini Plant | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 01:06 PM
05/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/10/2023 | Alternative | Follow-Up | SD-07-364 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Dug up distribution box and inspected for blockage. Added PVC to lowest header to get even distribution out of distribution box. Dug up part of line 1 and removed bulk of roots. Added root kill to all lines. Added 6? male adaptor to replace difficult end cap removal. Marked drain line with flags for reference of future concrete pad build. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/15/2023 | Alternative | RoutineScheduled | 10-100-0172 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | BIOCOIR |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | [] | [] | YES | [17 empty] | EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | 02:00 PM
09/15/2023 | Alternative | Initial Visit Component Maintenance | 177-STS-92272 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NO | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
03/02/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
09/13/2023 | Alternative | Initial Visit | 085-STS-33704 | Hanover | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 2.300000 |  | 2.000000 | [5 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the wire nuts on the pump and pump float. The splice box needs to be repaired (need to dig up by tank) and replace other wire nuts with silicone ones. The UV needs two screws. Took initial BOD and Fecal samples. The timer is set to 2.5 minutes every 4.5 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/13/2023 | Dec 30 1899 12:00PM
03/30/2023 |  | RoutineScheduled | 179-16-0140-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 3.000000 | 1500 | 2-6 0-12 | 0-3 | Pump | Pressure | Drip | UV |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","Disinfection"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","Disinfection"] |  | None | Clear |  |  | 16.000000 | [11 empty] | Inspected | soft spot in Field looks better | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 04:00 PM
05/25/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-90121 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NO | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
05/03/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Mound | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Drip loop was repaired. System is functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/07/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1875 | Septic | pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 03/07/2023 | Sample Chamber | 4.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/18/2023 |  |  | 107-14-0047 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  |  | Trenches |  |  | ["SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | 12:00 AM
07/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
08/07/2023 | Alternative | Routine/Scheduled |  | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [17 empty] | System Repair / Upgrade Installed new riser access on septic tank. Installed new riser access on pump tank. Installed new air compressor and controller - aeration now operating. Installed new discharge pump and float sensors. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/07/2023 | 06:45 AM
09/29/2023 | Alternative | Routine/Scheduled | 041-STS-257837 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/29/2023 | Dec 30 1899 9:32AM
09/13/2023 | Alternative | RoutineScheduled Component Maintenance | 175-02-0463 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Gravity | Gravity |  | Not Applicable |  | ["Dispersal System Operation" ,"Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Force main prior to modules needs repair. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | 12:58 PM
04/19/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-4"sludge 2"scum/ Microfast ATU-4"sludge 1"scum ( Requires Chemical Cleaning and pump out due to bacteria issues) Pump Tank-2"sludge 0"scum/ Blower air filter cleaned and working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-4236 ETM-804h 42m On-12m Off-2h 28m Peak Off-2h/ Peak-13 ETM-46h 27m/ High-19/ Watermeter-0,358,475.2/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
01/31/2023 |  | Follow-Up | 179-14-0008-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Assisted pumper with proper pump out of ATU. Replaced alarm buzzer in control panel. Sealed ATU riser. Replaced lids on ARV boxes. Refilled ATU with water. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 08:57 AM
08/07/2023 | Alternative | Routine/Scheduled | 234-16-221 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | Dec 30 1899 11:40AM
07/18/2023 | Alternative | RoutineScheduled Component Maintenance | 179-10-0226-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump" ,"Effluent Screens"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
03/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
01/13/2023 |  | RoutineScheduled | 179-09-0162-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium"] | ["Control Operation" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Media is ponding pretty bad, augered and got it draining. Media needs to be replaced. Will send proposal as soon as possible. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
06/21/2023 | Alternative | Reportable Incident |  | Loudoun | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Multiflo FTB | [6 empty] | Distribution Pump Operation | Distribution Pump Operation | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/03/2023 | 09:59 AM
05/22/2023 | Alternative | RoutineScheduled | 171-13-0180 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Aquaklear |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [16 empty] | Inspected | Sludge level-under 1" scum layer on top-5" sludge trace on bottom in Septic tank - Treatment Unit 6" slduge and has clear effluent on top- Good aeration. Pump tank was moist pump on a block,above the water- Aerator is running but aged, cleaned airfilter- Alarm is good but aged and new owner will have us replace this summer.. Pump tank looks good, total Pump run time 28:58:42 Hours about - Doses 1327 cycles - low pump run time/cycles indicate a sllight leak somewhere in these 3 tanks. The other tanks are at normal levels. Owner wants estimate to replace aram box, dog house cover and blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
11/11/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20 |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 14" of accumulated solids in septic tank. 4" of solids in discharge pump tank. Flushed treatment unit spray manifold. Cleaned recirculation pump solids basket filter. Tested floats, pumps and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/05/2024 | 07:03 PM
02/09/2023 |  | Follow-Up | 228-16-0357 A | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Control Operation","Disinfection"] | ["Control Operation","Disinfection"] | N/A | [17 empty] | Replaced UV bulb, cord and ballast. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/09/2023 | Jan 1 1900 3:00PM
04/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim |  |  |  |  | Pump | Pressure | Drip | UV |  | ["SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Auxiliary Filter","BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [17 empty] | septic/microfast tank needs pumped | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/23/2023 | Dec 30 1899 5:00PM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1500 |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 11/02/2023 | Sample Chamber | 31.000000 |  |  | 45.500000 |  |  |  | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/11/2023 | Dec 30 1899 3:20PM
01/03/2023 |  | RoutineScheduled | 179-STS-90520 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NO | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend replacing the broken junction box lid on the Pump Tank and installing a union on the EZ Treat pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
02/09/2023 |  | Reportable Incident | 94-163-0053 | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Pump | Pressure | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Reportable Incident - Found distal end of one absorption lateral damaged where "contractors" had buried 4" line for storm gutters. Excavated and repaired LPP lateral. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/13/2023 | Jan 1 1900 7:15AM
07/19/2023 | Alternative | RoutineScheduled | 05-100-0550 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 2.000000 | 1250 | ECOFLO |  | Pump | Gravity | Mound | Not Applicable | 600.000000 | [] | [] | YES | [17 empty] | SLUDGE JUDGE 4" FROM BOTTOM EVERYTHING WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | 10:50 AM
09/18/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/20/2023 | 01:45 PM
06/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping ATU. Recommend mowing drainfield area to keep larger vegetation down. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/23/2023 |  | Routine/Scheduled | 16-142-0340 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 3.000000 | [7 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The septic tank needs to be pumped out and when doing so pump the sludge out of the Clearstream tank. The timer is set to 8 minutes every 2 hours. Took 5 year BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/23/2023 | Jan 1 1900 1:00PM
07/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
09/01/2023 | Alternative | Pump-Out Only Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank Pumped | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 2.000000 | [8 empty] | ["Other"] | [] | YES | [17 empty] | Pumping Only | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | 12:00 AM
01/02/2023 |  |  | 15-113-095 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/02/2023 |  | 4.360000 | [5 empty] | Will be sent separately |  | BOD: 4.36 TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/02/2023 | 12:00 AM
08/22/2023 | Alternative | Routine/Scheduled | 2017-143-0072 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 550.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | [17 empty] | Septic tank should be pumped in the next year. The treatment sheets need to be scraped when the tank is pumped out. Also, the treatment tank will need to be pumped out and refilled when the sheets are scraped. The recirculation pumped had 374 overrides in the past 30 days. The recirculation pump on time was changed from 0.8 minutes to 0.7 minutes. The off time was changed from 15 minutes to 11.4 minutes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/22/2023 | 01:56 PM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/27/2023 | Alternative | RoutineScheduled | VAG408388 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 1.000000 |  | FAST | Constructed Wetlands | Gravity | Gravity | Discharge |  |  | [] | [] | NA | [17 empty] | Not discharging at time of inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/12/2023 | 09:45 AM
08/29/2023 | Alternative | Initial Visit | 800-STS-14919 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 8.000000 | [7 empty] | Owner called due to the alarm going off all the time. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Fixed the alarm - re-wired the wires in the panel - were not stripped back enough. The mute button was labeled wrong. The timer was set at 45 seconds every 2 hours changed it to 2 minutes every 2 hours. Took initial BOD sample. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/29/2023 | Dec 30 1899 11:45AM
04/10/2023 | Alternative |  | 17-100-0507 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-12"sludge 1"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-105,073 ETM-1,086,923/ Pump2-131,461 ETM-1,651,089/ Turned Puraflo peat in all modules, may need replacement next year/ All support bars in the modules may need replacement next year as well | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/22/2023 | Alternative | RoutineScheduled | 115-07-0522 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 12000 | Dual Biomicrobics Fast 2.5 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Level Sensor Operation","Control Operation","Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Effluent Screens","Level Sensor Operation","Control Operation","Auxiliary Filter","BlowerCompressorAerator Operation"] | YES |  |  | 7.300000 | 8.800000 |  |  | 15 | 02/23/2023 | Pump Chamber | [7 empty] | Inspected | Septic Tank #1 Sludge levels- 1-2" scum and 16" light sludge trace ( tanks were pumped in august), septic tank #2 minimal scum and 10-12" light sludge trace- Fast treatment unit has good Aeration Fast #1 6" sludge trace and Fast #2 trace-" sludge. The system tanks were pumped 6 months ago. Cleaned blower airfilters, Good Aeration observed from both Blowers, cleaned all the probes. One probe TSS in for replacment. Took Ph and Do Readings. Cleaned both Effluent screens. Treatment unit #1 9.2 DO and 6.4 pH. Treatment unit #2 8.5 DO, pH 7.6. pH . In pump tank Ph was 7.3 @ 15.0c - Effluent meter reading 6672663 previous 6541110 . Over 100 days, The current flow 131.553 Gallons or 1,316 Gallons per day on average. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/23/2023 | 09:30 AM
05/22/2023 | Alternative | RoutineScheduled | 171-06-0632 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | [17 empty] | Inspected | Sludge level-1-2" scum layer on top-14" sludge on bottom in Septic tank -pump tank had 6" sludge. Pump ct 16066 cycles vs 15805 last year or 261 pump cycles since last year- Pump run time 6079:17 Hrs vs 6069.95Hrs Last year or about 10 hours Total pumping this year., Pump runs good, Alarm test ok, Float switch tested ok. Peat moss in pods is older but still good.- Turned peat in all four pods. Peat Condition is ok for age. System is fully functional. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
04/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/07/2023 |  | RoutineScheduled | 175-16-0281 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/17/2023 | 10:44 AM
04/10/2023 |  | RoutineScheduled | 13-197-A3 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/10/2023 | 12:00 AM
03/28/2023 |  | RoutineScheduled | 153-STS-20369 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Disinfection","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Disinfection","Level Sensor Operation"] | NA | [7 empty] | 03/28/2023 | Sample Chamber | 65.000000 |  | 1600.000000 |  |  |  | Attached to this report |  | Septic Tank-3"sludge 2"scum/ Microfast-2"sludge / Pump Tank-0"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ UV-Light sleeve cleaned and light is working/Found On and Off Floats were faulty and were replaced during inspection / Controls, pump, floats and alarms are now functioning properly/ Counts: Pump-852 ETM-151h 48m/ High-16/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Mound | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/01/2023 | Alternative |  | 04-125-055 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 08/01/2023 |  | 6.350000 |  |  | 3.330000 |  |  | Will be sent separately |  | BOD: 6.35 TSS: 3.33 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/01/2023 | 12:00 AM
03/27/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
08/07/2023 | Alternative | Follow-Up Component Maintenance | SP-05-307 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Assisted pumper with pump out of Recirc tank. Inspected tank for cracks; repaired 6 small cracks, 5 at mid-seam and 1 in the roof. Reattached lid to pod. Dug up RSV line from tank and inspected for breaks; OK. Will brings struts during next service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
05/02/2023 |  | RoutineScheduled | 101-05-0740 | Albemarle | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Blue Ridge | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation"] | ["Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | filter clog cleaned to repair pump flow | This AOSS should now return to normal function after having provided the above state routine maintenance | 06/21/2023 | 03:35 PM
08/30/2023 | Alternative | Routine/Scheduled | 234-15-153 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | Dec 30 1899 2:20PM
07/27/2023 | Alternative |  | 09-113-182 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/27/2023 |  | 3.170000 |  |  | 4.530000 |  |  | Will be sent separately |  | BOD: 3.17 TSS: 4.53 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/27/2023 | 12:00 AM
06/06/2023 | Alternative | RoutineScheduled | 154-11-0153 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | biomicrobics |  | Pump | Pressure | Drip | Not Applicable | 150.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Blower was replaced on 07/25/2023. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | 11:50 AM
03/13/2023 |  | RoutineScheduled | SP-05-269 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | Annual inspection. Only 3 small pockets of ponding water in the pods, but peat is wet and a bit mushy when squeezed. System was installed in 2006 so peat may be nearing the end of its useful life. Will evaluate next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
03/31/2023 |  | RoutineScheduled | 05-192-278 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation","Septic Tank Baffles"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/31/2023 | 12:00 AM
07/31/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | Dec 30 1899 1:44PM
11/03/2023 | Alternative | RoutineScheduled Component Maintenance | 177-10-0156-SP | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | UV |  | ["Disinfection" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | As noted previously, the blower and the UV light are not working. We recommend installing a new blower and a new Norweco AT1500 UV Unit in place of the existing Salcon unit | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/01/2023 | 08:44 AM
03/16/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
06/20/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1060 | Multiflo FTB |  | Gravity | Gravity | Trenches |  | 450.000000 | Control Operation |  | N/A | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/12/2023 | 12:59 PM
09/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  | 1500 |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 3:10PM
06/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["SludgeScum Accumulation","Attached Growth Medium","Dispersal System Operation"] | [] | NA | [17 empty] | Septic Tank-4"sludge 0"scum/ Microfast-18" sludge / Pump Tank-1"sludge/ Septic- Microfast Tank requires pump out/ Blower air filter cleaned and working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-5295 ETM-1150h 29m/ Peak-61 ETM-43h 14m/ Watermeter-406,306.14/ Zones 1 & @ are dosing at the same time due to faulty check valves and requires replacement. Replacement to be scheduled soon/ No breakout or spongy areas on the drip field. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
08/07/2023 | Alternative | Reportable Incident Component Maintenance | SWP-03-412 | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for patio and pool being installed on top of drip field. Drip tubing was cut homeowner thought it was a old sprinkler system. Drip field can not be repaired. Told homeowner to contact Aose to locate a new drainfield. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 09/01/2023 | 05:07 AM
02/03/2023 |  | RoutineScheduled | SWP-05-142 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 1-1 | 0-0 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [17 empty] | Inspected | pump tank may have infiltration | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | 02:00 PM
09/22/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and pumping | 1942001330 | Michelle | McKim | 2.000000 |  | 1500 |  | Pump | Pressure | Drip | UV |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 2:45PM
03/20/2023 |  | Routine/Scheduled | 145-STS-259910 | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/20/2023 | Jan 1 1900 12:09PM
03/07/2023 | Alternative | Reportable Incident | 073-STS-101493 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | COSS - Repair Install - VDH Permit 136-22-0245 - GMP2018-02 Existing septic tank pumped empty and abandoned in place. Installed new 1000 gallon concrete, mid-seam septic tank with riser access to grade and cannister style effluent screen. Installed new 8 port concrete distribution box. Excavated and installed 4 laterals as per permit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/08/2023 | 10:00 AM
08/10/2023 | Alternative | RoutineScheduled Component Maintenance | 179-15-0173-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Inlet wedge lid and outlet riser have small roots growing in and they both leak. Proposal to be sent to correct infiltration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
09/25/2023 | Alternative | Routine/Scheduled | 157-06-0355 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level Less than 1" of solids with 4" of sludge Pulled and cleaned filter Filter is intact but is original -Discharge/Pump Tank: At normal level Alarm float was no longer mounted to the pole so I installed a new bracket. Both floats are aged but working Pump is working -Peat Moss: Tipping bucket functioning Peat is root matted and unable to rake it out -Control Panel: Working properly Visual and audible alarms working Panel is original Pump pulling 9.73amps | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | 10:31 AM
12/09/2023 | Alternative | Reportable Incident |  | Loudoun | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Multiflo FTB | [6 empty] | Distribution Pump Operation | Distribution Pump Operation | N/A | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/25/2024 | 02:37 PM
05/16/2023 |  |  | 124-STS-2379 | Charles City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Ecoflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [18 empty] | -Replaced STEP 20 pump -Replaced ORENCO control panel -Replaced Aquarium air pump -Replaced alarm float -Replace chlorine & de-chlor tablets | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/05/2023 | 12:00 AM
08/11/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Rejected | EHD - Blue Ridge | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
09/18/2023 | Alternative | RoutineScheduled | 107-15-0235 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
04/19/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | Jan 1 1900 12:48PM
10/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Bio Barrier | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 10/24/2023 |  | 8.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample Normal Repaired air supply | This AOSS should now return to normal function after having provided the above state routine maintenance | 11/22/2023 | 09:18 AM
02/14/2023 | Alternative | Reportable Incident | 103-STS-101824 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | COSS - Repair - VDH Permit 151-22-0204 Pumped empty and removed existing septic tank. Installed new 1000g concrete mid-seam septic tank w/ effluent screen. Installed new 1000g concrete mid-seam pump tank. Installed new 2" pvc forcemain / conveyance line Installed new 8 port concrete distribution box. Installed 6 - 60' x 3' absorption laterals @ 18". | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/15/2023 | 10:30 AM
04/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/22/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-94 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 2.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation" ,"Septic Tank Baffles"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Everything looks good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
08/10/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired air line & diffuser. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
04/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/27/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/28/2023 |  | RoutineScheduled | 2010-143-0011 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 |  |  | 3.000000 |  | Biomicrobics Microfast |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/28/2023 | 12:00 AM
04/04/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 2705051738 | Joshua | Hott | 1.000000 | 1250 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/28/2023 |  | Routine/Scheduled | 234-14-430 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | Jan 1 1900 1:45PM
05/16/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic Tank |  | Gravity | Gravity | Discharge | UV |  | ["Disinfection"] | ["Disinfection"] | YES | [6 empty] | Ecoli 1MPN/100mL |  | Sample Chamber | 2.000000 |  | 1.800000 | 6.000000 |  |  | Attached to this report |  | Septic Tank-4"sludge 0"scum/ No pump out needed at this time/ Sample box clear/ UV-Light and bubbler functioning properly/ Discharge point clear. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
04/20/2023 |  | Routine/Scheduled | {FIPSCode}-STS-1656 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Hoot |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [13 empty] | UV is not working. Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/20/2023 | Jan 1 1900 8:45AM
09/05/2023 | Alternative | RoutineScheduled | 06-197-A2 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 0.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.500000 | 7.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
06/19/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | Dec 30 1899 8:05AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | EcoPod | EcoPod | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Drip panel audible alarm is intermittent. Recommend replacing it. Visual is still functional. Blower motor sounds odd but is functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/14/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 12:00 AM
06/27/2023 | Alternative |  | 10-125-170 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 06/27/2023 |  | 2.190000 |  |  | 1.000000 |  |  | Will be sent separately |  | BOD: 2.19 TSS: 1.00 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/27/2023 | 12:00 AM
11/02/2023 | Alternative | RoutineScheduled | 08-192-039 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | WHITEWATER |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation","Dispersal System Operation","Control Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 1 - Blue Crystal tablet installed 2 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/02/2023 | 12:00 AM
09/05/2023 | Alternative | RoutineScheduled | 175-06-0747 | Manassas | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Elite Onsite | 1942001726 | Drew | Saunders | 2.000000 | 1500 | 750 | 750 | Gravity | Gravity | Trenches | UV | 350.000000 | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | 03:40 PM
08/17/2023 | Alternative | RoutineScheduled | 10-173-015 | Prince Edward | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 |  | Norweco |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["SludgeScum Accumulation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Cloudy | [14 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/17/2023 | 12:00 AM
05/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon |  |  | Septic Tank/ EZ- Treat Recirc. Tank | Pump Tank | Pump | Pressure | Drip | UV |  | ["Disinfection","Recirculation Pump"] | ["Disinfection","Recirculation Pump"] | YES | [17 empty] | Septic Tank-5"sludge 1"scum/ EZ-Treat Recirc. Tank-4"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Recirc. pump and UV-Light bulbs require replacement/ Recirc. Sta-Rite Step-20 pump replaced and UV-Light Bulbs replaced. Controls, pumps, floats , UV-Light and alarms now functioning properly/ Counts: Discharge pump- Ec1-0045934 ETM-0138820/ Pump cycles-314/ Pump Run Time-77h 37m/ High level- 11/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
12/05/2023 | Alternative | Routine/Scheduled | 166-07-533 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 07:01 PM
08/19/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-11298 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | ATU | Polishing Sand Filter | Pump | Gravity | Discharge | Chlorination | 500.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] | NA | Musty | Clear | 7.700000 |  |  | 1.800000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/21/2023 | 12:00 AM
06/08/2023 | Alternative | RoutineScheduled | 087-STS-6213 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
11/17/2023 | Alternative | RoutineScheduled Component Maintenance | 177-14-0283-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
12/08/2023 | Alternative | RoutineScheduled Component Maintenance | SR-05-503 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
05/12/2023 | Alternative | RoutineScheduled | 10-173-046 | Prince Edward | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1300 | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/12/2023 | Dec 30 1899 12:00PM
05/23/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
12/13/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | Replaced UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 2:20PM
06/05/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jesssica | Young | 1.000000 | 1500 | septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The breaker for the blower had tripped and it was reset at time of inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/06/2023 | Alternative | RoutineScheduled | 15-100-0049 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 500 | AQUA SAFE |  | Gravity | Pressure | Mound |  | 450.000000 | [] | [] | YES | [17 empty] | SLUDGE JUDGE REVEALED 4-5" FROM BOTTOM AND AQUASAFE LESS THAN 1/3 SOLIDS-REPLACED MUSHROOM VENT, PUMP STATION LID, HIGH PRESSURE SWEEP ON DRAIN LINE EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/25/2023 | 11:15 AM
11/28/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-195 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | The peat is settling below the spray grid. This is likely a sign that the pet is starting to deteriorate. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
11/07/2023 | Alternative | Follow-Up | 166-14-158 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | replaced blower, system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/05/2023 | Alternative | RoutineScheduled Component Maintenance | 175-04-0279 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Distribution Pump Operation" ,"Control Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Peat still working okay. Septic tank should be pumped out by end of summer. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
10/10/2023 | Alternative | RoutineScheduled | 107-08-0423 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The blower and spin filters were both cleaned. The effluent screen was sprayed off. The controls were operating as designed. There were no visible leaks in the drip field. There was return effluent returning to the pump tank from the drip field. The drip field was operating as designed. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/09/2023 | 12:15 PM
07/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
09/05/2023 | Alternative | Reportable Incident | {FIPSCode}-STS-63692 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | [7 empty] | [] | [] | [17 empty] | Inspected | resealed pump tank riser and replaced textile sheets | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | 10:00 AM
12/01/2023 | Alternative |  | 177-07-0293-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/04/2023 | Alternative | Reportable Incident | 151-04-545 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | COSS - Maintenance - Repair - VDH Permit 151-23-0069 - GMP2018-02 Pumped septic tank empty for replacement as per Permit. Installed new 1000g concrete mid-seam septic tank - riser access to grade - cannister style effluent screen in outlet baffle. Found DBox to be degraded - replaced - found 2 additional laterals - replaced degraded header lines with new. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | 07:45 AM
03/06/2023 |  | RoutineScheduled | 11-125-158 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/06/2023 | 12:00 AM
04/27/2023 |  | Routine/Scheduled | {FIPSCode}-STS-3741 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | [15 empty] | Pumped Out | Replaced pump | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/27/2023 | Jan 1 1900 9:00AM
10/10/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:00 AM
06/01/2023 | Alternative | Pump-Out Only | 02-142-0326 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Supervised pumpout of primary septic tank and processing tank by Commonwealth Waste Solutions ... refilled processing tank with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/07/2023 | Dec 30 1899 11:30AM
09/25/2023 | Alternative | Reportable Incident | 093-15-0175 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Customer stated alarm light was on for honey house pump tank Opened system and found at normal level Tested floats and found Alarm float is faulty Quoted replacing both floats or just alarm float and customer approved both floats Replaced both float while on site. All components functioning properly Also checked system at main house and all components are functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | Dec 30 1899 10:09AM
11/21/2023 | Alternative | Routine/Scheduled | 800-08-0118 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Ecoflo |  | Pump |  |  |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Replaced peat moss | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/21/2023 | Dec 30 1899 9:00AM
09/19/2023 | Alternative | RoutineScheduled | 13-197-A2 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/19/2023 | 12:00 AM
04/24/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | Dec 30 1899 12:48PM
12/29/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [14 empty] | Replaced aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/29/2023 | Dec 30 1899 8:00AM
03/27/2023 |  | RoutineScheduled | {FIPSCode}-STS-4052 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/27/2023 | 12:00 AM
01/13/2023 |  | Routine/Scheduled | 147-18-0036 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash tank - normal level - wipes present in trash tank. Aeration Tank - normal level - mixing present - compressor serviced. Pump tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | Jan 1 1900 12:00PM
09/21/2023 | Alternative | RoutineScheduled Component Maintenance | 015-STS-333422 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
12/21/2023 | Alternative | Reportable Incident | 095-STS-5741 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Found surfacing and found that a loop end has slipped and causing water to surface. Quoted repairs customer approved onsite. Repair failed multiple times. Finally got the repair to hold properly. Once done tested no leaks there was none. Reset pressures for drainfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | Dec 30 1899 8:49AM
02/17/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 | Eco Flo Drip |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | 12:00 AM
12/20/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | Control Operation | Control Operation | N/A | [17 empty] | Replaced Timer | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/20/2023 | Dec 30 1899 10:30AM
03/01/2023 |  | RoutineScheduled | 163-STS-333750 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | AdvantexAX20RT | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The Recirculating and Discharge pumps were both pulled and cleaned. The spin filter was cleaned. The textile sheets were sprayed off. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | 09:30 AM
03/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
01/06/2023 |  | RoutineScheduled | 181-12-0021 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 5.000000 | 7000 | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","Effluent Screens","SludgeScum Accumulation"] | ["Auxiliary Filter","Effluent Screens","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Checked and cleaned filters and effluent screens. Three septic tanks pumped and cleaned. Control panels, floats and pumps all functioning properly. NO apparent leaks in system or drain field area. Lids were properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/14/2023 | 11:10 AM
05/11/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 12:00 AM
03/02/2023 |  | RoutineScheduled | 175-14-0093 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
08/23/2023 | Alternative | RoutineScheduled | 10-197-A2 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/23/2023 | 12:00 AM
04/28/2023 | Alternative | RoutineScheduled | 031-STS-27575 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 15000 | Advantex AX MAX |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [7 empty] | 12/21/2022 | Pump Chamber | 5.600000 |  |  | 2.900000 | 5.400000 |  | Will be sent separately | Inspected | Quarterly Inspection on AX MAX - Sludge levels- Septic tank 2-5" scum layer and 6" trace of sludge on bottom. Setic tank 2, Trace of sludge, Surge tank, trace of sludge, Anoxic tank trace of sludge Looks most impact from FOG, Keep the grease traps pumped frequently, to reduce scum and oil buildup, Make sure no sanitizers, sanitizer soaps from bathrooms or other chemicals are dumped into the drains- Grease traps- need pumped. Checked aeration fan - running good - mild Odor - a lot of flies- Rinsed off spray nozzels, lidsand some media in recirculation zone- good spray. Ran pumps and checks for operation-all good. Checked chemical feed and both are dripping, DO reading 1.0 on Effluent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
01/12/2023 |  | Routine/Scheduled | 02-142-0528 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid servied. PUmp Tank - float sensors, pump and controls operating. LPP field has broken / fractured lateral - repaired. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/16/2023 | Jan 1 1900 7:15AM
03/09/2023 |  | RoutineScheduled | 147-06-0009 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Parsley Septic Tank , Inc. | 1942001106 | James | Parsley | 1.000000 | 1000 |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | None | Clear | [14 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/09/2023 | 12:00 AM
09/15/2023 | Alternative | RoutineScheduled | 175-10-0305 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | Chlorination | 500.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles"] | YES | Musty | Clear | 7.600000 |  |  | 2.200000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/16/2023 | 12:00 AM
05/16/2023 | Alternative | Routine/Scheduled | 136-06-0104 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | AOSS - Initial Visit Primary septic tank - pumped empty for Chesapeake Bay - replaced effluent screen with new. Pump Basin - float sensors, pump and controls operating. Biofilter - fiberglass - peatmoss ponding - in extreme poor condition - raked / turned best able. Recommend biofilter changeout. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 08:30 AM
12/04/2023 | Alternative | Reportable Incident Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Installed Norewco UV unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 09:34 AM
07/17/2023 | Alternative | Routine/Scheduled | Legacy | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Biofilter - four modules - peatmoss in good condition - 6" effluent in inspection port | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/18/2023 | Dec 30 1899 7:30AM
03/16/2023 | Alternative | Routine/Scheduled | 150-05-190 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. bulging present. BioFilter - peatmoss in poor condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/20/2023 | 08:00 AM
06/28/2023 | Alternative | Routine/Scheduled | 147-15-0088 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/28/2023 | Dec 30 1899 12:38PM
08/10/2023 | Alternative | Routine/Scheduled | 234-15-302 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | Dec 30 1899 9:35AM
08/07/2023 | Alternative | Routine/Scheduled | 07-174-0153 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump |  | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/07/2023 | Dec 30 1899 9:57AM
11/27/2023 | Alternative | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Orenco Advantex | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2024 | 01:02 PM
10/07/2023 | Alternative | Initial Visit | 019-STS-27735 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AXRT20 |  | Pump | Gravity | Trenches |  |  | ["Control Operation"] | ["Control Operation"] | NA | [17 empty] | Initial start-up visit. Set recirculation pump flow rate. Programmed pump timers based on indicated occupancy. Verified correct installation. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/23/2023 | 07:03 PM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/14/2023 | Alternative | RoutineScheduled | 2017-143-0062 | Henrico | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Henrico | Revised Environmental, LLC | 1942001508 | Danna | Revis | 1.000000 | 1250 | Multi-Flo |  | Pump | Pressure | Drip | Not Applicable | 600.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 11/15/2023 | 01:40 PM
04/13/2023 |  | RoutineScheduled | 175-11-0300 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 04:23 AM
02/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
09/25/2023 | Alternative | RoutineScheduled Component Maintenance | 179-17-0444-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
02/07/2023 | Alternative | Routine/Scheduled | 136-13-0059 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Delta Environmental Products, UC Series |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash tank - normal level Aeration Tank - mixing present - compressor serviced. PUmp Tank - transducer, pump and controls operating. DBox - unknown - heavy vegetation present on absorption field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/09/2023 | 07:45 AM
11/10/2023 | Alternative | RoutineScheduled | 2005-143-0325 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/17/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | Dec 30 1899 11:08AM
04/21/2023 | Alternative | RoutineScheduled | 115-17-0064 | Campbell | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Biomicrobics Fast |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | Musty | [15 empty] | Inspected | Sludge levels--2-4" scum and 12" sludge Septic tank zone. Fast Side port 20", No aeration upon arrival and blower was tripped via breaker in off- reset breaker and blower began to work fine. Sampling port has clear water flow. Reccomened to pump and FOUTZ septic returned and pumped the system after my visit. Pump operational, both alarms operational. cleaned blower filter, System has returned to full operation. Pump rest 3 hours and pumps 1 min on. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/30/2023 | 09:30 AM
07/10/2023 | Alternative | RoutineScheduled | 133 06 0436 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Western Virginia Water Authority | 1942001145 | Michael | Doss |  |  |  |  | Gravity | Pressure | Drip | UV |  | ["None"] | ["None"] | NA | None | Clear | [5 empty] | 07/10/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 06:15 AM
05/17/2023 |  | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | DeHaven's Backhoe Service Inc. | 1942001541 | Wayne | Edmonson | 2.000000 | 2500 | Microfast |  | Pump | Pressure | Drip | Not Applicable | 125.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Distribution Pump Operation","Level Sensor Operation"] | NA | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/22/2023 | 10:00 PM
01/01/2023 |  | RoutineScheduled | 06-137-0039 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/28/2023 | Alternative | Initial Visit | 136-10-0064 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Delta Environmental Products, UC Series |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Distribution Pump Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | AOSS - Initial Visit 03/27/2023 - Pump truck called for a flooded septic system - found to be an AOSS - pumped Pump tank empty and trash tank empty for storage due to a discharge pump failure. 03/28/2023 - AOSS inspection conducted. Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - replaced failed discharge pump - added water to tank for test. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/29/2023 | 10:33 AM
03/29/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | An inspection of a conventional gravity septic system. There is a pvc cleanout near the house. The sewer line was camera snaked to the tank and was clear. There is a tree planted on the sewer line. We would recommend removing so as not to crush the pipe in the future. The concrete septic tank is 7 feet from the driveway and is 12" under the ground. When the outlet lid was hand dug up a large crack was found that runs from the top of the tank to down the side of the tank. Unsure how much further the crack goes. At this time we feel the tank is structurally compromised. The conveyance line was camera snaked and was clear. The 9-port plastic d-box was dug up it was 9" under the ground. All 6 corrugated header lines were camera snaked and clear. Drain field was probed and dry. Drain field is in a horse pasture. At this time the septic system is not in working condition due to the septic tank being cracked. An AOSE will need to be contacted to issue a permit and design for new tank. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
12/21/2023 | Alternative | RoutineScheduled | 12-118-0019 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Clearstream |  | Pump | Pressure | Drip |  |  | [] | ["BlowerCompressorAerator Operation","Effluent Screens","Control Operation","Distribution Pump Operation","Dispersal System Operation","Level Sensor Operation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | 12:00 AM
01/23/2023 | Alternative | Routine/Scheduled | 166-16-149 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2023 | 06:54 PM
10/05/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-03-783 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Top lip on septic tank inlet riser was broken, removed and used second lip to screw lid on if mowers break that lip new riser will need to be installed. Root inside 2nd pod, removed. Septic tank has wipes and tampons inside advised customer not to flush unbreakable materials. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
10/18/2023 | Alternative | RoutineScheduled | 182-10-0079 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | 12:00 AM
04/13/2023 |  | Routine/Scheduled | 133 15 0107 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 12:30 PM
02/21/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Advantex sheets and the bottom cleaned. Septic system is in working condition | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
11/09/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Sand |  |  | Pressure | Trenches | Not Applicable |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Septic pumped at tenant house | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/08/2023 | 12:00 AM
05/04/2023 | Alternative | Routine/Scheduled | 18-160-0110 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Advanced Septic |  | Pump | Pressure | Drip | Not Applicable |  | SludgeScum Accumulation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/04/2023 | 12:30 PM
08/14/2023 | Alternative | Routine/Scheduled |  | Frederick | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Sandfilter, Recirculating |  | Pump | Pressure | Discharge |  | 450.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation"] | ["Attached Growth Medium","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation"] | N/A | [18 empty] | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 11/27/2023 | 03:52 PM
06/19/2023 | Alternative | Reportable Incident | 175-11-0081 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Control Operation"] | ["Control Operation"] | [18 empty] | System in alarm: Controls completely off/ Requires pump out/ Found wires damaged from the house to the junction box on the pump tank. Wires replaced and system tested, functioning properly at this time. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/24/2023 |  | Routine/Scheduled | {FIPSCode}-STS-2922 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | Jan 1 1900 7:30AM
07/10/2023 | Alternative | RoutineScheduled Component Maintenance | 179-14-0212-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Third line still not taking water. Roots can be felt just inside header at d-box. Owner has been provided a repair proposal to remove the roots and video inspection of all lines. Waiting on approval to proceed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
12/01/2023 | Alternative | RoutineScheduled Component Maintenance | 107-01-0537 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | needs to clean et bed and drainfield area | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
08/14/2023 | Alternative | RoutineScheduled | 151-03-310 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
03/21/2023 |  | RoutineScheduled | 16-137-0045 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 2.000000 | 2500 | Multiflo |  | Pump | Pressure | Trenches |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/27/2023 | 12:00 AM
01/13/2023 |  | RoutineScheduled | 18-197-A2 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 Chlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/13/2023 | 12:00 AM
06/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 12:00 AM
02/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 2.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/08/2023 |  | Reportable Incident | 234-13-463 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aeratro | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/08/2023 | Jan 1 1900 7:30AM
01/03/2023 | Alternative | Reportable Incident | SD-96-436 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed new American 1 Zone hydraulic unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
04/07/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
08/07/2023 | Alternative | RoutineScheduled | 04-192-109 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 10 - Blue Crystal tablets installed 10 - Bio max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/07/2023 | 12:00 AM
04/14/2023 |  | RoutineScheduled | 132-18-0030 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | ANUA PuraFlow |  | Gravity | Gravity | Trenches | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/16/2023 | 12:00 AM
03/30/2023 | Alternative | Routine/Scheduled | 05-174-0162 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 3.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/30/2023 | Dec 30 1899 3:22PM
10/13/2023 | Alternative | RoutineScheduled | 109-12-0276 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Multiflo ATU |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge levels in septic tank-2" Scum layer and 12" sludge on bottom of tank. Treatment tank has 2" scum on the deck of multiflo with about 5" sludge on bottom. No living roots in tanks noted, Owner will remove soil buid up around treatment lid. Good aeration in multi flo | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/17/2023 | 09:30 AM
06/02/2023 | Alternative | Routine/Scheduled | 166-14-059 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - plastic - deformed - roots present. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/07/2023 | 12:00 PM
05/15/2023 |  | Routine/Scheduled | 550-STS-6588 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | Jan 1 1900 11:50AM
02/20/2023 |  | RoutineScheduled | 179-16-0238-SWP | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"SludgeScum Accumulation" ,"Auxiliary Filter"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Auxiliary Filter"] | NA | Pungent | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend replacing the Orenco riser lids on the inlet & outlet side of the Advantex, along with the Advantex vent cap. We recommend pumping the Pump Tank due to sludge accumulation in the tank. There are signs that effluent may be surfacing along the drip mound. We plan to follow up in drier weather to be sure this was not due to recent rains. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/03/2023 | 08:19 AM
09/26/2023 | Alternative |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | J&G Septic Service |  | James | Kleindl | 2.000000 | 3000 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/27/2023 | Dec 30 1899 8:00AM
09/20/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
01/24/2023 |  | Routine/Scheduled |  | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/24/2023 | Jan 1 1900 11:46AM
11/29/2023 | Alternative | Routine/Scheduled | 228-17-0162 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/29/2023 | Dec 30 1899 11:25AM
09/01/2023 | Alternative | Reportable Incident | 06-118-0117 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Advanced Septic |  | Gravity | Gravity | Trenches | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Install - VDH Permit 22-118-0099 Installed AOSS in accordance with permit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | Dec 30 1899 8:15AM
06/28/2023 | Alternative | RoutineScheduled | 12-120-0140R | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 1600 | 1000 | 750 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Recirculation Pump"] | YES | Musty | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 12:00 AM